## Background
Background
As stipulated by the 3rd Energy Package, ENTSO-E is mandated to publish the biennial Ten-Year Network Development Plan (TYNDP) - “ENTSO-E shall adopt a non-binding Community-wide 10 year network development plan, including a European generation adequacy outlook, every two years” . For the 2014 plan, ENTSO-E has created a package of reports (eight in total) which cover not only the pan-European view but also the regional perspectives: - the Community-wide TYNDP report 2014; - the six Regional Investment Plans 2014; and - the Scenario Outlook and Adequacy Forecast 2014. ENTSO-E strongly encourages and factors stakeholder involvement into the TYNDP process. During the two-year development period, ENTSO-E both provided information to, and sought input from stakeholders during several phases of the process via 17 European and regional public workshops , six public web consultations, numerous requests for contributions and bilateral meetings. In addition, ENTSO-E formed a stakeholder group to regularly and proactively discuss and provide input on topics regarding long-term network development. This group meets 3-4 times a year, in addition to related dedicated task forces meetings, and is attended by European organisations who have an interest in system development. Finally, the TYNDP 2014 package was open for public consultation from 10 July to 20 September 2014. During the 10-week consultation, ENTSO-E received more than 400 comments from 30 stakeholders. The present excel incorporates all the received commnets and the ENTSO-E to each of them. This document is acompagne by the report on the stakeholders' comments , report proposes a synthetic typology of all feedback received during this last consultation.
Next steps:
end October 2014 - ENTSO-E delivers the TYNDP 2014 package to ACER for their official opinion
end December 2014 - ENTSO-E publishes on its website the final TYNDp 2014

## TYNDP 2014
Respondent Organization | Initial | Proposed | Comment | ENTSO-E answer
Nordenergi |  |  | The cohesion of Nordic and Baltic Sea markets suffers from various bottlenecks in the area. Although many important investments have been carried out as scheduled, other important investments have either been cancelled or delayed in to the future. Nordenergi encourages TSOs to further improve their cooperation in order to strive for a common and more coherent market. | ENTSO-E, and especially its Baltic Sea Regional Group, have investigated the influence of the project delays and according to results it can have really huge influence for the socio economic benefit as presented in Appendix 7 on figure 107 of the Regional Investment Plan. So we support the opinion.
Europacable | “EMF exposure”. "Design cable layout to keep EMF under limits" | "MF exposure". "Design cable limit to keep MF under limits". | Cables do not emit an electric field | The initial wording is kept as EMF is a shared acronym. But the rationale is true: cable do not emit electric field... which is hence below any limit.
Element Power | Conversely, 20 to 30 GW of new nuclear capacities are expected to be brought onto the system. This is mainly in the UK but also includes Finland and Central Europe. | n/a | ENTSO-E should assess the efficiency of placing base load generation in UK/Ireland. This is not efficient for EU transmission. It is discouraged in Scotland by transmission charging because it drives high cost transmission reinforcement. The same consequence, already recognised for Scotland, applies to British isles in future. | ENTSO-E developped the scenarios in cooperation with all interested stakeholders. Having at least some scenarios relying on governmental plans appeared a must. The TYNDP appraise the impact of such plans regarding grid development, and many indicators (see RES curtailment in Vision 4 for instance), but cannot judge about their absolute "efficiency" provided the analysis must be completed in many respects of energy policy beyond the scope of the TYNDP.
Vattenfall AB | This effort represents very significant financial engagement for TSOs. However, it only represents about 1.5-2 €/MWh of power consumption in Europe, i.e. about 2% of the bulk power prices or approximately 1% of the total electricity bill. | add: Following its relatively limited share of total system costs, the realisation of the TYNDP could be perceived as an option value that would allow Europe to develop within the framework of the four visions of the TYNDP thus not risking that potential for energy transition is locked in behind insufficient grid capacities. | The cost of infrastructure investments is minor in comparison to the total cost of energy transition. Thus, the cost of underinvestment can be assumed to be significantly higher than the risk for overinvestment. The value of a strong transmission grid, that may enable all the studied scenarios and a cost efficient energy transition, must be highlighted to policy and decision makers. Otherwise, there is a risk that the significant potential for energy transition is captured behind bottlenecks. | The cost of transmission infrastructure is indeed only a fraction of the cost of the total system. This is a fact, and it is reflected in the quoted figures. These figures however do not measure nor limit the risk or opportunity of "overinvestment". Not to mention the pre-requisite of a fair burden sharing regarding stranded costs, overinvestment can prove difficult to afford in a period of economic downturn and cost savings; and counterproductive (if a transmission project proves a waste of money, it can cast doubts on useful projects).
Nordenergi |  |  | Our main point number 1: Many of the proposed projects are already delayed for several different reasons. We suggest that a simple list of the delayed projects is compiled and presented in the beginning of each regional plan with reasons for non-implementation/delay, as well as the actions which need to be taken. Main point 1. is elaborated as follows: It is commendable to have a planning to 2030. However, Nordenergi thinks that the plan should include more comments on the midpoint, 2023−2024. This should be made in connection with a simple list naming the delayed projects, the estimated change in finalization date and reason for the delay (e.g. permitting, technical problems, etc). | The full list of the projects and the status information is given in the table in Appendix 1, section 11.1.2. The table includes the project evolution information since TYNDP 2010 and also gives additional information of current status.
Europacable | "Restrict works to avoid sensitive breeding seasonseasons for protected species" | "Restrict works to avoid sensitive breeding seasons for protected species". | Typo | Appendix 7 has been amended in this sense.
Element Power | Figure 4-2 Map of main bottlenecks in the ENTSO-E perimeter | n/a | It is not clear direction of bottlenecks. | The location of the bottleneck is the most important information alerting where action is required. The basic motivation appears also essential. The map is hence limited to displaying the above information. More is provided later in the report, with the magnitude of the flows to begin with. With more volatile flows in the coming decades, both directions are usually at stake, with few exceptions (esp. major plant connection issues). The regional investment plans describes more deeply the main bottlenecks and the projects assessments sheets provide the details about GTC magnitude and direction.
Vattenfall AB | This lack of acceptance, in addition to lengthy permit granting procedures regularly result in commissioning delays. Most of the projects featured in the TYNDP 2014 that have entered the permitting process have thus experienced delays. | add: Figure 0-X presents the status of the investments of pan-European significance contained in the Community wide TYNDP 2012 Table of Projects | The issue of public acceptance must be thoroughly emphasised also in the executive summary, therefore we propose to include the illustrative figure 9-1 in the executive summary. | The executive summary has been amended in this sense.
Nordenergi |  |  | Our main point number 2: The scenarios and their impact still need to be improved. In addition, the current scenarios give a false impression of precision, e.g. energy policy changes such as capacity markets will have a strong impact on merit orders and spot prices. Main point 2. is elaborated as follows: The scenarios hardly consider the macro-economic implications. For example, the energy intensive industry can only remain in Europe if the costs are comparable to the rest of the world. As the current discussions on the consequences of Energiewende shows (e.g. IHS 2014) a future with high cost choices for the European power system will have more far reaching impact on the demand side, than are foreseen in the current scenarios. The European electricity market is in a flux, and depending on decisions on continuing renewable energy supports systems, the introduction of capacity markets in some countries, balancing responsibility for all generation in the system or not and progress in the intraday and balancing markets integration or not, the value of cross border capacity between countries and investment in transmission capacity can be highly affected. Nordenergi thus encourages ENTSO-E to also include some political cases that lead to changes in the electricity market, prices and trade patterns in further scenarios and assess how that impacts on investment incentives. | Scenario building is a difficult science where ENTSO-E asked their stakeholders' for support during the whole process of preparing the TYNDP scenarios, from Spring 2012 to Autumn 2014. The selection and appraisal of macroeconomic parameters in all scenarios have been discussed. The process restarts this Autumn until next Summer for the TYNDP 2016 scenarios. Most interested stakeholders can join the works of the Long term network stakeholders groups for a more active involvement and contribution.
IFIEC |  |  | The Executive summary of the report remarks that Grid development is a vital instrument in achieving European energy objectives, such as security of supply across Europe, sustainable development of the energy system with renewable energy source (RES) integration and affordable energy for European consumers through market integration. In this document you can find the comments from IFIEC Europe (IE) to the TYNDP 2014 public consultation. | -
Element Power | Figure 4-2 Map of main bottlenecks in the ENTSO-E perimeter | n/a | Why are some bottlenecks markedas lines and some as ovals? | The boundary is either closed or open: the connection of a specific power plant or the supply of a specific area at risk is usually marked as a closed line, as connection or transmission support can be imagined a priori from all directions. Bottlenecks in the market usually do not isolate completely (360°) a region but solely prevent power flows to cross a certain section.
Vattenfall AB | this assessment shall lead to a ranking of projects for internal use of the Group. Neither the regional list nor the Union list shall contain any ranking, nor shall the ranking be used for any subsequent purpose | Delete this section | The quote from the Regulation 347/2013 refers to projects of common interests only, since the TYNDP does not only include PCI listed projects, the legal reference does not rule out a ranking in the context of the TYNDP plan. We propose to add to the final TYNDP edition a CBA ratio between monetised benefits and estimated costs and include that as a separate column for each project. | Although also applied to non-PCI projects, the CBA methodology has been developped to support Regulation 347, and the quotation of Art. 4.2.4 which is referred to here is valid: ranking is expected within every group, based on their own weighting of the multicriteria analysis provided here, and prior public ranking is excluded. Monetisation of non-monetised criteria involves valuation choices that prove complex, many times with no single valuation parameters and are no consensus in Europe nowadays. Hence they cannot be implemented in the end release of the TYNDP 2014.
NorthConnect KS | (Only Ch.1 can be selected above. This General Comment relates to statements made in Chapter 0.7.3 and Chapter 5.3.1) | N/A | The TYNDP 2014 highlights that interconnection capacity throughout Europe will need to double in the years to come. However, only 10% of the TYNDP 2012 investments planned are completed, and many others have fallen substantially behind programme. The next TYNDP (2016) should include a variance analysis (current plan versus previous plan) and address possible reasons why investments are lagging behind, and also suggest solutions. This should include solutions on how to attract more 3rd party interconnectors and private capital to contribute to the €150 billion grid expansion needed. | Explanations for delayed investments are provided in §6 (as an overview), and specifically to every project in the assessment sheets. Two main reasons stand out, both depending on decision making outside TSOs' hands: longer than expected permitting procedures; and delayed generation projects post-poning the need to build the related transmission assets.
Nordenergi |  |  | Our main point number 3: Stakeholder representation in both the European and regional planning works needs to be improved. Main point 3. is elaborated as follows: The idea of a Stakeholder development group is very good. The strengthening of the future group to represent all generation interests is a step into the right direction. Additionally, it is important that the stakeholders also can represent the different European regions, in our view, as there is currently regional divergence in regulation and design of markets through for example the introduction of national capacity markets in some but not all regions. In addition we suggest that similar stakeholder groups are installed at the level of the regional investment plan, since that would allow a better access to the regional expertise and detailed knowledge of more local/regional actors. Finally, we propose that the groups can invite in experts from the universities or other countries such as the New York ISO to draw on their expertise when needed. | Stakeholders' involvement can certainly be improved. The next move is ensuring an active participation in the framework of the Long term network development stakeholders group. Participation can be arranged from a distance. Most important is actual contribution from the stakeholders with respect to scenario inputs or modelling pieces and acknowledgement for our joint works. Outsider experts such as universities can already now be invited to present issues on their expertise to the LTND SG meeting. ENTSO-E needs others' expertise but has not identified all possible interested parties, nor can force anybody. Beyond the LTND SG, regional workshops and consultation will still be regularly organised during the process, where stakeholders can give input and take part in the process.
IFIEC |  |  | The plan should include more details on how demand response potential is considered necessary to avoid a negative impact in the European industrial consumers (competiveness and security of supply. Measures must be taken in that respect at EU level, inter alia through the development of framework guidelines (FG) on tariff harmonization announced by ACER. Grid investments should be based on socio-economic criteria, with demand response, market design and power flow management etc. taken into consideration. | DSR is considered in the methodology but however it fails, unfortunately, to address grid development issues of pan-European significance. The major concern is conveying large amount of RES to load centers, especially when the generating output of RES facilities is close to their capacity. Higher load at the same moment, especially when close to the generating RES sources, is welcome.
Element Power | Figure 4-2 Map of main bottlenecks in the ENTSO-E perimeter | n/a | Doesn't show severity or significance of constraints. | (see answer above)
Vattenfall AB | generation cost |  | Clarification. The use of change in generation cost as proxy for socioeconomic impact of transmission disregards demand side response and may thus yield incorrect estimates. Since the activity on the demand side is likely to increase over time, the impact of this simplification is insufficiently transparent as it is not summarised anywhere to what extent the generation cost approach vs the total cost approach is applied in the different regions. | Demand side response has been modelled in the scenarios, the methodology been shared publicly and consulted upon; and the modelling can be improved for the TYNDP 2016. ENTSO-E believes DSR can bring great benefits to system operation. The major concern for grid investment is however conveying large amount of RES to load centers, especially when the generating output of RES facilities is close to their capacity.
NorthConnect KS | (Only Ch.1 can be selected above. This General Comment relates to statements made in Chapter 0.8.2 and Chapter 10.2) | N/A | In the 2014 TYNDP Entso-E acknowledges that the current methodology needs improvement to capture “capacity” value of assets. This is important to address within the next TYNDP (2016). | ENTSO-E improved the TYNDP greatly from one release to another in the past and will go on this way in order to meet stakehdolders' expectations.
Nordenergi |  |  | Our main point number 4: Nordenergi thinks a ranking of the projects following a transparent methodology would be helpful. In addition Nordenergi thinks it needs to be clarified how and why projects are clustered. Clustering decreases the transparency. Main point 4. is elaborated as follows: Clustering of projects obstructs transparency in selection criteria. The CBA methodology should be based on individual assessments where the cost of each individual transmission project is valued against the assessed benefit of that given project. Such an assessment is needed to secure a transparent build-out of the grid. Clustering should only be valid in cases where a ‘sub-project’ is a clear precondition for a ‘mother-project’. The current CBA clustering rules are too superficial. Additionally, it should be possible to rank the projects with respect to the value achieved and the cost for the project. | ENTSO-E strived to give enough information based on the CBA methodology for the stakeholders to make their ranking, as everyone would weight criteria differently. Clustering rules were tightened in the CBA methodology compared to the TYNDP 2012 based on stakeholders' feedback. Clustering rule is now that the investments are supporting same grid transfer capacity and that the effect should be at least 20% of the total capacity increase. In addition the investments should be not futher apart than 5 years. Typically a cross-border interconnector is clustered with the needed internal reinforcements needed to achieve the wanted interconnection capacity.
IFIEC |  |  | For getting market integration on track, it is necessary - To develop interconnection capacity between systems fixed by the European Commission in a minimum value of 10% of the total installed generation capacity for 2020. - The economic impact of the TYNDP 2014 must consider the present situation of the European industrial energy consumers, avoiding the risk of carbon leakage. Increasing and unpredictable grid tariffs is of high concern. Energy intensive industry's ability and contribution to stabilizing grids and power production need to be fully recognized. | The target capacities computed in the TYNDP eventually match the EU's "10% criterion". (Projects presently foreseen at the North border of Spain multiply by 4 the present capacity, but must however be completed to meet the objective and further studies are launched in the framework of the TYNDP 2016 to cope with the identified gap.) The economic impact of the TYNDP 2014 has been appraised, with total investments costs of all projects of pan-European significance (equivalent to 1.5-2 €/MWh) lower than the total generation cost savings they bring (equivalent to 2 to 5 €/MWh savings).
Element Power | Figure 4-2 Map of main bottlenecks in the ENTSO-E perimeter | n/a | Security of supply affects an area and is not a line. | In the Dublin area, north south flows threaten the security of supply. Hence a line has been drawn.
Vattenfall AB | Table 2-2) was done using the TOOT (Take One Out at a Time) | Change to: Table 2-2) was done using both the TOOT (Take One Out at a Time) and the PINT (Put One In at a Time) method, described in detail in the CBA. | We do not support this clear focus on only the TOOT method. As proposed by the THINK report, it should be possible to evaluate against a TOOT and a PINT baseline, both results should be presented and in the case of significant differences, further analysis for the respective project shall be initiated. | Section 2.4.1 of the TYNDP report is clarified.
Nordenergi |  |  | Our main point number 5: In-depth reporting on the bottlenecks is missing. Main point 5. is elaborated as follows: The section on bottleneck locations and typology is too superficial. The bottlenecks are the fundamental issue that is being addressed by the TYNDP, and Nordenergi encourages the TYNDP to portray a detailed description of individual key bottlenecks and furthermore be much more specific in the report in regards to assessing to what extent the suggested TYNDP investments will mitigate the given bottlenecks and on which timescale. This way a much needed transparency on the individual key bottlenecks is secured and ACER and the NRAs would have a better understanding of which bottlenecks are addressed to what extent and on which time scale, leaving the NRAs a better basis for assessing when further action in form of changing the congestion management regime is needed. | The TYNDP is trade off between a synthetic overview and detailed information. Bottlenecks are located on boundaries; and the analysis of the bulk power flows through the boundaries compared to the boundary capacity enable a characterisation (frequency, magnitude) of the bottleneck. Mostly, such results are displayed in the Regional Investment Plans as monotonous (or not) hourly load curve (see for instance Regional Investment Plan Baltic Sea, § 4.5)
IFIEC |  |  | The TYNDP points out that the 150 billion EUR grid investments only represents about 1.5-2 €/MWh of power consumed in Europe, i.e. about 2% of the commodity power prices or approximately 1% of the total electricity bill. For some customers however, the increase may be much higher. Uncertainty about future grid costs for industry is increasing. To keep a competitive industry, European and national authorities should not add on to already high electricity prices and regulatory costs in Europe. Companies need competitive and predictable framework conditions to be able to invest for future sustainable long term industry production. | (Complementing other answers) Benefits of the TYNDP are higher than costs; otherwise, additional support to industry depends on the regulatory framework.
Element Power | 2. Direct connection of generation: both thermal and renewable facilities. | n/a | why is connection of thermal an issue? It can be sited in many places, with the development of transmission for renewables thermal bottleneck should not exist. | One of the main drivers for grid development in 2030 is the connection of generation. Thermal, as any other type of generation (e.g. RES) requires grids development and therefore is considered at in the transimission planning for 2030. Some of the connection projects are large enough to be projects of pan-European significance.
Vattenfall AB | The year 2030 is used as a bridge between the European energy targets for 2020 and 2050 |  | See previous general comment: a socio-economic assessment of long term investments based on analysis results of only 2030 is too limited. At least 2020 (but preferably also 2025) for all scenarios and stages should be included in the modelling results. | (see answer to comment row 114)
Tractebel |  |  | Tractebel Engineering. Some information about transfer capacities between countries are provided in the TYNDP 2014: • Figure 4-1 shows the aggregated levels of Net Transfer Capacities (NTC) in ENTSO-E perimeter in 2013; • Chapter 6 describes the target border capacities displayed as ranges for the different visions (from the Scenario Outlook and Adequacy Forecast 2014-2030) by 2030 and the corresponding transmission adequacy; • Grid transfer capability increase associated to the described projects (for both directions of the boundary) is given but there is no guarantee on the additivity of these increases of NTC. However, this information is not sufficient and does not provide an accurate picture of the present situation nor a comprehensive view on the evolution of the net transfer capacities. Day-, week-, month- and year-ahead NTC values are available on the ENTSO-E transparency platform only for past and present values. A figure or a table with these figures for every boundary and for every direction is not included in the report and must be added. In any case, no forecast for these NTC values is provided. The evolution of the net transfer capacities (even if subjects to caveats) with the proposed project portfolio must be made available to the stakeholders of the European transmission system. | The TYNDP 2014 provides target capacities values for all relevant boundaries. These boundaries may correspond to present international borders or merge some of them, in order to give the most accurate description of congestion, more respectful of network meshing and kirschhoff laws' than an arbitrary allotment between borders would be. The displayed information is as accurate as the uncertainties behind the scenarios allow for. At this long term horizon, pretending to display a more accurate information would be just misleading.
Nordenergi |  |  | Modelling: As is shown in the tables in Appendix 3, Baltic Sea region TYNDP, all countries will more or less install a huge overcapacity. Alas, the numbers are not easily comparable as the generation is reported in MW and consumption in TWh. This can easily be resolved though as figure 26 clearly indicates that there are energy numbers available per region, and per technology. With regards to supply and demand balance, the numbers reported do indicate that ENTSO-E foresees that the current German conundrum will remain unsolved. This brings us to an extremely serious and potentially devastating modelling issue. For example, figure 28 compares the different average marginal costs between the regions. As a long run trading projection this only works if the marginal costs include the full costs, in so far that the capital costs are included, i.e. the long run marginal costs. Now, if some areas decide to remunerate capital through regulated mechanisms such as capacity mechanisms, the energy prices will be depressed in these areas and the flows may go counter to what real long run marginal costs would demand. This can create serious issues for cost efficiency and long run investment in transmission capacity and generation capacity in neighbouring countries, which are similar to the consequences of price dumping cases. The chapter in price differences and trade flows therefore only makes sense in regions where a continuing energy-only market is probable. Nordenergi regrets that these questions are not addressed for example in an additional sensitivity case or test to the main scenario. | The production capacities presented in the Appendix 3 are presenting the installed capacity. The produced energy is then a result of the market model runs based on the visions assumptions, and the balance can be seen on the cross-border energy flows as presented on Appendix 4. There are restrictions on using the market models, as stated they assume energy-only market, perfect competition, they only take into account marginal costs, not captial costs. It is worth to note that these presented average marginal costs do not represent a full cost, nor do they try to represent a true market price.
IFIEC |  |  | Possible FG on tariff harmonization must be considered in relation to grid expansion plans, and need to take into consideration the power intensive industry’s role in stabilizing the grid and reducing investments and need for competitive grid tariff level. | (see answer to comment row 37)
Element Power | 2. Direct connection of generation: both thermal and renewable facilities. | n/a | Thermal bottlenecks should be shown seperately to renewables. | All generation means must be considered when appraising the need to develop the grid.
Vattenfall AB |  |  | Readability of figures 3-5, 3-9, 3-13 and 3-17 should be improved with figures rather than shades of grey and or linked to high resolution maps on the ENTSO-e web page. The average marginal cost data should be provided both in a table and in the format of duration curves for hourly price differences between bidding zones. | Shades of grey have been implemented and no figure provided as they could be misleading: on average over the year, absolute prices in every country may be close one to another; although hourly price differentials may be high (in one direction at some moments, and in the other direction at other moments). The maps hence display the information that serves the demonstration, highlighting mainly the average absolute price differentials; and giving additionnally with the shades of grey the feeling about which countries are major importers/exporters. The text completes the information indicating the average cost all over Europe.
IFIEC |  |  | Meanwhile, through the implementation of projects of pan-European significance, the increased market integration should lead to an overall leveling of electricity prices in Europe, mitigating electricity prices on average from 2 (in Vision 1) to 5 €/MWh (in Vision 4). We appreciate initiatives reducing power cost, but emphasize that large investments costs must not result in increased grid costs for the power intensive industry, which it´s exposed to global competition. | The TYNDP identifies the basic extra high voltage investment needs to ensure functionning systems or markets. The organisation of the system and market is subject to subsidiarity: based on the planned infrastructure, the relevant authorities are in charge of designing the operation and market procedures, in particular organising the cost recovery among all stakeholders. Tariff structures are the responsibility of National Regulatory Authorities.
Vattenfall AB |  |  | Section on “Present Situation”. The evaluation of the present situation should include a reference to the current bottlenecks in the transmission system, supported by the findings of the technical report according to the CACM guideline. The future TYNDP package should include a review of current costs related to insufficient grid capacity and how this cost is mitigated for each 5-year period as the TYDNP package is gradually commissioned. That would require that the future TYNDPs study comprises several points in time. | Only an overview of the present situation is displayed in chapter 5 as more detailed information is available on the ENTSO-E web site (www.entsoe.net), from detailed data to synthetic reports.
Nordenergi |  |  | CBA methodology: The CBA methodology and the subsequent possibility to conduct a cross border cost allocation are the key enablers for the development of a European grid infrastructure. Nordenergi would like to emphasize the importance of the work on and the timely finalization on the CBA methodology. The cost-benefit calculations are also sensitive to several assumptions. Currently it is not obvious whether the SEW calculation is based on national or European methodology i.e. whether the numbers are comparable at all. The cost-benefit calculations are also sensitive to several assumptions, none the least, the choice of what is the relevant area that the calculations cover. TSOs look at different areas, with some looking primarily at national benefit and costs for TSOs, while others also look at a wider regional or European perspective. When stated that the TSOs in the TYNDP 2014 are looking at “optimum solutions”, these solutions must be firmly put in the context of assumptions and national restrictions. Given that the infrastructure packages recognize the need to facilitate the realization of projects with benefits in third countries, Nordenergi would encourage ENTSO-E to publish the CBA results of analyzed projects including cross border distributional effects to facilitate a more open discussion on the realization of affected projects. Nordenergi would also encourage a more open discussion on how the diversity of organizational structures of the TSOs, and the owners instructions, affect the decision to go ahead, or as it were, cancel decisions. Nordenergi would like to point out that a transparent decision making process and access to the assumptions and data that lead to a decision are especially important the more uncertain the future is. In our view the major benefit of a scenario approach chosen by the TSOs is therefore the discussion they stimulate, i.e. what kind of development is reasonable under different assumptions about the future. Given that grid building and planning is also affected by highly specific local conditions, some of the discussion should be even more decentralized, as in for example the work with Svenska Kraftnät’s grid plan for 2025 where Swedish actors could give a more detailed view on a line-by-line, project-by-project basis. Transparency would also ensure certain coherence between national and European grid scenarios. The table of cost/benefit results for each project gives a fairly rough estimate of the costs but is hard to find the aggregate estimates of the benefits. This is clearly difficult in the case of infrastructure. However, a cost and benefit analysis should clearly include both. For example, one of the projects in the Nordics discussed since 1989, the strengthening of the Hasle cut was surprisingly (for the market participants) cancelled or delayed indeterminably with reference to unclear benefits. There could be some improvement of the reporting, for example by given the best and the worst sums per project. Several projects operate with large differences in possible/anticipated investment costs, e.g. NSI and NorthConnect etc. This creates a large uncertainty regarding potential future costs and SEW. The reason for these rather large uncertainties should be explained and if possible reduced. In addition, a search for the discount rate used in the calculations yields no result. Discount rates are one of the key factors in modern cost benefit analysis and thus can play a key role for the overall profitability of a project. Loss variations are deemed as a benefit. However, we believe that the benefits regarding losses are in reducing them and not in the variations. Developing new generation far away from load may create new bottlenecks on the way to the consumer, long transmission lines and power transport hence, increasing losses. In what way does the TYNDP take into consideration pricing signals in the market and through tariffs in order to facilitate new generation is located in order to reduce bottlenecks, network investment needs and losses? | Regional Groups of ENTSO-E have performed the CBA assessement of the projects based on the common CBA methodology. It has been recognized already some improvement needs for the methodology. The assessment has also been performed against the common pan-european visions, so the results are comparable. The tools used are not the same on each region. The results reported are either the pan-european benefits/effects or regional benefits/effects, where it has been deemed that the effect of the project is neglible in the other regions. The national benefis have not been assessed during the TYNDP and Regional investment plan process. ENTSO-E has assessed all the projects in four visions just to cover some of the uncertainties of the future system evolution. All the CBA indicators are shown in the cost/benefit tables. For losses, projects can either increase or diminish losses, this is the reason why the indicator is called losses variation.
IFIEC |  |  | TYNDP 2014 recognizes that the most critical area of concern is the stronger market integration of the four main “electric peninsulas” into mainland Europe. The proposed projects must be enough for reaching a minimum level of interconnection capacity between systems fixed by the European Commission of 10% of installed capacity, without increasing costs for power intensive industry. This minimum value is very hard to reach in 2020 for some regions. The appropriate level of interconnection capacity compared to the installed capacity will vary due to power system capacities and characteristics in the connected countries. Without a minimum of interconnection capacity it is impossible to come to full market integration in Europe. It is necessary to eliminate the present bottlenecks and to develop interconnections where it is socio-economically profitable. Industrial energy consumers from these electric peninsulas are and will be deprived of the benefits of Market integration, suffering the effect of isolated systems. | ENTSO-E sympathises with the raised concern. IFIEC, as well as other bodies or persons can help efficiently by supporting specific interconnection projects during local public debate, with neighbouring population and authorities.
Vattenfall AB |  |  | Information in figure 4-1 should be given in a table and/or in a format that allows direct comparison to what is (a) regarded as socioeconomic sound by the TYNDP-plan and (b) what is included in the TYNDP plan 2014. | Figure 4-1 displays the present transmission capacity at every border. It is an excerpt from the ENTSO-E data portal, which provides a whole range of detailed statistics, especially regarding the use of that capacity. No socio-economic appraisal is performed in the TYNDP regarding this factual information.
Tractebel |  |  | Tractebel Engineering. Additional information regarding the modelling of load management and demand side response has to be provided. This includes the DSR level considered in the models as well as the followed methodology. | Demand side response has been modelled in the scenarios, the methodology been shared publicly and consulted upon; and the modelling can be improved for the TYNDP 2016. ENTSO-E believes DSR can bring great benefits to system operation. The major concern for grid investment is however conveying large amount of RES to load centers, especially when the generating output of RES facilities is close to their capacity.
Nordenergi |  |  | Benefits of RES integration, CO2 reduction and Security of supply: In the CBA evaluation, integration of RES seems to be one of several benefits that are taken into account. Even though reaching RES targets is important, we cannot see that introduction of specific production technologies gives a social economic benefit in itself. Especially if these technologies trigger other expensive investments in order to secure Security of Supply and a stable grid. Thus the measure must to some extent be coupled to some target achievement decided on beforehand. In addition, it is somewhat difficult to see how increased infrastructure can change the overall CO2-emissions if not a direct link is made to EU’s CO2-cap. Transmission may lower the cost of using for example nuclear or wind power by enhancing the trade of electricity by these sources. However, that trade in itself does not affect the CO2-cap which is set by a regulatory decision by the EU Commission. Security of supply (SoS) is one of the most important issues in the TYNDP and one of the main drivers for European network development. However, in our opinion the TYNDP does not in a sufficient way address and analyze the SoS issues. Differences between countries regarding production technology and access to flexibility and reserves, and how these different technologies are interconnected and utilized in Europe is of imperative importance when addressing SoS. In our view it is therefore important that ENTSO-E addresses these issues vigilantly and improves the TYNDP to this regard. A lot of the projects (disregarding the subsea projects) are still planned as overhead lines. However, the environmental disturbance of overhead lines as compared to underground cabling is large, which can lead to delayed permitting procedures. Thus, even if cabling may be more expensive it may gain time, and advance the benefits of a project time-wise. Hence Nordenergi proposes that projects that are delayed due to environmental resistance traceable to overhead lines, some comment to the effect on how much benefits that are lost for every year of delay would be an improvement in the TYNDP. In addition the TSO should give an assessment of how much more mitigating actions such as cabling would cost. Armed with this it could be possible to discuss whether the more expensive alternative of cabling is worth investigating. A fair amount of projects in the Baltic Sea Region has been delayed or in the worst cases cancelled. To increase political pressure on the national/local authorities, Nordenergi thus proposes that relevant local/regional/national authorities are invited to the respective stakeholder groups. A final comment is on the decision to move the PCIs to the appendixes and annexes. For the less initiated reader it may appear as those projects have less socioeconomic value than those supported by ENTSO-E. This is of course not so. Thus Nordenergi proposes that these projects are given a more prominent place in the report. | ENTSO-E has already noted that the CBA methodology has some needs for improvement especially concerning SoS assessment. RES has been taken in as one CBA indicator due to the European goals as well as the CO2 indicator. CO2-cap has not been included on the assessment, rather the actual CO2 emissions in the various visions.
IFIEC |  |  | In order to finance the investments of €150 billion, it is necessary to avoid negative impacts on the European industrial consumers. The EU must take some measures for it, included a competitive, and predictable tariff policy. | ENTSO-E aims at identifying the main long term pan-European transmission needs and report their potential economic impacts. However the tariff structures are the responsibility of National Regulatory Authorities.
Vattenfall AB | Grid reinforcements increase the social and economic welfare of Europe | Change to: Grid reinforcements increase the social and economic welfare of Europe through a positive net benefit contribution. | Giving the socioeconomic contribution in size of M€ without including the cost does not provide the necessary information to state that this project is socioeconomically sound. Rather, the average cost-benefit ratio of the TYNDP project should be shown. | The TYNDP cost benefit analysis as a whole can be summarised comparing the 1.5-2 €/MWh of additional costs required by the investments and the 2 to 5 €/MWh of generation costs savings.
Tractebel |  |  | New clustering rules to define projects of pan-European significance have been used in the TYNDP 2014. This clustering aims at bringing together investment items with the same purpose. Although the purposes of the projects are explained in the detailed descriptions, these must be made explicit in the summary table. Furthermore, the projects must also be sorted with new macro categories such as interconnections, internal reinforcements, connection of offshore wind farms, etc. Next, the value brought by each investment item of a project can significantly vary in a same cluster. Thereby, the TYNDP has to provide disaggregated information about the estimated cost of the projects and include single investment grid transfer capacity increases. Finally, the assumptions taken to estimate the cost of the different projects must be provided (e.g average cost per km of AC overhead line, of AC underground cable, of DC OH lines and cables…). These assumptions have to be listed and consolidated in the report to ensure transparency. | The project assessments are performed according to the CBA clustering and valuation rules. The disagregation of the project GTC per investment is provided in the investment table and costs figures are tuned in the final release of the TYNDP 2014. Cost figures derive from specific estimate for each project, submitted to ENTSO-E by the project promoters and hence, there are no standard assumptions behind cost figures.
Gaelectric Energy Storage Ltd |  | 1 | The current Cost Benefit Analysis methodology for TYNDP 2014 does not fully capture the benefits of bulk energy storage, mainly because system operational constraints within each power system are not included in the any of the modelling platforms used. In the All-Island power system in Ireland, some key operational constraints were not included in the TYNDP 2014 analysis: 1. System Non-Synchronous Penetration (SNSP) Limit: This is a limitation on the amount of wind energy and interconnector imports that can serve demand at any one time. Generation from non-synchronous sources above the SNSP limit will be curtailed. The limit is currently set at 50%, however a programme is in place to incentivise increased system services (DS3 programme) to enable this limit to be increased up to 75%. 2. Operating Reserve: The TSOs must hold a certain amount of dispatchable load in reserve to ensure that sufficient spinning and non-spinning reserves are available in times of frequency deviations and tripping of large generators. Generators are often constrained towards their minimum generation operation level to provide reserves, which is sub-optimal from an efficiency perspective given the nature of the heat rate curves of thermal generators. 3. Minimum Number of Units Online: On the island of Ireland, a total of 8 large generators must be on-load at times to ensure sufficient inertia on the system. At times of low demand, this constraint very frequently results in wind curtailment due to there being “less room” for wind to meet demand. The Larne CAES (compressed air energy storage) facility (Project Index # 221) provides the following benefits which are not captured in the TYNDP 2014 analysis: 1. (a) Increase of dispatchable demand to increase the amount of non-synchronous generation that can remain online. (b) Provision of system services to enable SNSP limit to be increased above current level of 50%. 2. Increased levels of reserve compared to conventional generation units and reserve is provided at lower cost. 3. (a) Demand side is synchronous so can provide inertia while consuming energy. (b) Increase of dispatchable demand to increase the “room for wind” on the system. Without including key constraints such as the above, the full value of storage cannot be captured. Useful link: http://www.eirgrid.com/media/OperationalConstraintsUpdateVersion1_16_August2014.pdf | ENTSO-E acknowledges all benefits of storage projects are not captured: the implementation of the CBA only captures the 'energy' part of the benefits, ie. only the ability to buy at cheap hours and sell at peaks and none of the operating benefits. A caveat is provided in the CBA methodology and the introductory page of the Appendix 1.3 (storage assessment) of the TYNDP report provides an explicit caveat in this respect, insisting the valuation is still to be completed with respect to 'capacity' and 'flexibility' parts of the benefits. A clarification that this comes from the simulation limited to a 60 minutes-quantum will be added.
IFIEC | B2. Socio-economic welfare (SEW) or market integration is characterised by the ability of a power system to reduce congestion and thus provide an adequate GTC so that electricity markets can trade power in an economically efficient manner. |  | It is necessary that industrial consumers get advantage of this SEW Benefit. In next editions of the TYNDP the CBA must be reviewed to consider some aspects in favor of European industry and to avoid carbon leakage. | The TYNDP methodology (the so-called "CBA" methodology, co-developped with the stakeholders) appraises the overall benefits for Europe as a whole. Benefits specific to industrial consumers depend additionnaly to the market and tariff structure in every country, falling beyond the scope of the TYNDP.
Vattenfall AB | A limited impact on protected and urbanised areas | Most projects pass protected and urbanised areas but generally this is only the case for a minor part of the route. | 15 km is still not an insignificant distance and might cause long delays in permitting. If possible, add a group showing projects that has zero or close to zero distance through environmentally protected or densely populated areas. It is important to highlight for decision makers that public acceptance is key for most projects, even though the absolute distance may vary. | The indicator gives a feeling of the share of the project that may be challenged by crossing protected or urbanised areas. The thresholds in the breakdown have been chosen to split the portfolio into main categories, and less than 15 km means "to be appraised at the level of a local community". At this level, the length at stake is less important than the type of area, or other background information.
TIWAG-Tiroler Wasserkraft AG |  | General Comment and atatched TIWAG Response "ENTO-E TYNDP 2014 Consultation, Pumped Hydr Storage Assessment | We consider TYNDP 2014 as one of the best start up strategy papers to give energy transition of the electricity system a well-organized and structured technical framework. We are aware of the relevance of this paper not only for experts of the energy sector, but also for policy makers and other persons interested in that topic. TIWAG welcomes the inclusion of Hydro Power Storage as 3rd party projects to the TYNDP 2014. | -
Diamond transmission corporation |  |  | If the intent of the document is not only to announce where projects are required but to facilitate investment, then the document could provide more information about the relative parties supporting the projects. | The purpose of the TYNDP is to display the required grid reinforcements, for all stakeholders. Project promoters are the concerned TSOs, members of ENTSO-E, except for the few projects promoted by consortia not members of ENTSO-E.
IFIEC |  |  | In the past TYNDP, IE proposed Market Studies to present the hypotheses on the generators cost considered in the analysis. We have not found references on this in this report. We consider necessary to make public all relevant market information and assumptions including generator costs. The results of the market studies depend on these hypotheses and directly affect the decisions about grid extensions. | Fuel and CO2 costs have been published and they are recalled in the TYNDP itself. Resulting price curves stacking all generation means are also provided (see 3rd 2030 Visions workshop on ENTSO-E website for instance).
Vattenfall AB | Choosing the route and the technology – AC or DC, cable or overhead, etc. – are the two key decisions in order to avoid or mitigate any undesirable effect on the environment, with no a priori ‘better solution’. | add at the end: It is crucial that this is accompanied by a regulatory framework that recognizes the benefits of and creates incentives for the use of technologies that facilitate public acceptance. | ENTSO-E should make clear to regulators and decision makers that the regulatory framework must provide incentives, for example to use different technologies in order to avoid public resistance towards individual projects. | A regulatory framework incentivising grid investment is necessary, but it is independent from the technology issue. With respect to public acceptance, the active support of authorities and stakeholders is the most important, whatever the technology.
TIWAG-Tiroler Wasserkraft AG |  |  | In general TIWAG is affected by this paper as a market player and in particular as one of the most important Austrian (cross-border-) ancillary and flexibility service providers operating hydro storage and hydro-pumped storage power plants during the last 70 years. We welcome that the alpine region and its potential of hydro storages is addressed as an important factor to promote the RES integration at an European scale. | -
TIWAG-Tiroler Wasserkraft AG |  |  | With respect also to the latest German Grid development plan we may assume, that until 2030 HPS will play a key role for system stability and security of supply focusing on (market based) ancillary service products at low costs, high flexibility, best efficiency (economical as well as energetical) and CO2 neutrality. Additionally, from 2030 on they will expand their role in short, medium and long term storage for energy shifting purposes. | -
Diamond transmission corporation |  |  | It would be useful to have more detailed explantion of why the price differences occur between the countries in the various scenarios. The information provided is general and at a high level | (see answer to comment row 119)
IFIEC | This is a markedly different concept from that taken for the scenarios up to 2020 used in the TYNDP 2012; these aimed to estimate the evolution of parameters under different assumptions, while the 2030 Visions are designed to estimate the extreme values between which the evolution of parameters is expected to occur. |  | The demand response potential is considered in the different scenarios. There are no details of how it is calculated. | DSR has been addressed when building the scenarios, and modelled in the market studies and network studies. What DSR? which potential? - this has been decided during the scenario building process with an important involvement of stakeholders. However DSR fails, unfortunately, to address grid development issues of pan-European significance. The major concern is conveying large amount of RES to load centers, especially when the generating output of RES facilities is close to their capacity. Higher load at the same moment, especially when close to the generating RES sources, is welcome.
Vattenfall AB | Confirming the trend of the “2013 monitoring update of the TYNDP 2012” published in June 2013, more than one third of investments are delayed compared to the initial schedule, mostly because of social resistance and longer than initially expected permitting procedures, possibly leading to project reengineering. This phenomenon is not specific to certain countries or regions. | add at the end: Applying the CBA methodology, ENTSO-E calculated an estimate of socioeconomic cost of this delay, results are shown in table 9.X below. | With support from the CBA methodology and its results, the cost of a delayed delivery of socioeconomic surplus may be calculated. That would allow ENTSO-E to put a figure on the value of enhanced permitting procedures, etc. | A valuation of the yearly benefits of every project is provided. Although it is performed for 2030, it is often a good estimate of the project benefit for the commissioning year and the costs of delaying the project can hence be derived. A better answer will be provided for the next edition, where an intermediary horizon will also be valuated.
TIWAG-Tiroler Wasserkraft AG |  |  | TIWAG intends to expand these services inter alia by extending the existing power stations Sellrain-Silz/Kühtai and Kaunertal Power Station resulting in enormous investments for the benefit of the region and the European industry. | -
Diamond transmission corporation |  |  | Figures 3-5, 3-9, 3-13 and 3-17 would benefit from a key to explain the yearly average cost, if only to mark the low and high shading. | (see answer to comment row 123)
IFIEC |  |  | Visions 1 and 2: Compared to the 1990 level, the emissions are reduced by 40% in the ENTSO-E perimeter. Why is it necessary to consider an increment of the RES participation with Visions 3 and 4? | The TYNDP 2014 aims at a large exploration of the 2030 horizon, a bridge between 2020 and 2050. The construction of the four Visions has relied on stakeholders feedback. In this respect, the aim at higher CO2 mitigation and RES penetration has been desired, resulting in Vision 3 and 4.
Vattenfall AB | 5% of the investments have been cancelled | 5% of the investments have been cancelled. The cancelled projects together with CBA results and motivation of cancellation are to be found in annex X | Note there is a section in the regional plan showing all cancelled investments, but no CBA data included. Part of this list should be an explanatory motivation for cancelling a particular investment. | The relevant appendix of each regional plans shows cancelled investments with some explanation on the reason why the investment was canceled. Non profitable CBA is a particular reason falling into this scope.
TIWAG-Tiroler Wasserkraft AG |  |  | The “Extension of the Pump Storage Powerplant Kaunertal” is part of the 1rst EU-wide PCI-list (project index 222) and is affected by the CBA assessment for 3rd party projects within TYNDP 2014 (see page 296 of the regional investment plan 2014, Continental Central South Region). Within this extension Kaunertal Power Station not only will provide ancillary services and flexibility products but also produce additional renewable energy (in total 622 GWh/a) by additional natural inflow. Thus, we assume its aditional CO2-avoidance potential by approx. more than 500 kt/a. | The information of natural inflows was not available to ENTSO-E when making the assessment but is relevant. The CO2 avoided thanks to natural inflows will be added to the figure presently in the report.
Diamond transmission corporation |  |  | There is limited information on energy storage and the need for grid services (reactive power and frequency response), both of which will be esential components of the future European grid. Therefore further information would be welcomed | (see answer to comment row 127)
IFIEC |  |  | In Vision 3 "green transition", the valuation of interconnection projects often shows less value than in other Visions, as all countries are equipped with similar facilities – wind power, gas units – in large, and sufficient volumes. Other aspect is: Compared to the 1990 level, the emissions are reduced by 64% in the ENTSO-E perimeter. This means that with this Vision the minimum of interconnection capacity in some regions will not be reached and it will be impossible to come to full market integration in Europe. We would, however, get a green scenario, but with a residual spillage of RES being the highest in all Visions: it amounts to 48 TWh!! | Eventually, Vision 3 show a limited consistency, illustrating that merely compiling national non-cooperative energy policies together is not optimum.
Vattenfall AB | For future TYNDPs and assessments, ENTSO-E and all interested stakeholders plan to evolve the CBA as far as needed to better match the needs of decision makers. | Add: Table X summarises the already planned developments of the TYNDP methodology in the 2016 edition. | Proposed improvment of transparency of planned methodological improvements | The plan for CBA methodology improvements is still being drafted, with dedicated workshops and Long Term Network Development Stakeholders Group meetings.
TIWAG-Tiroler Wasserkraft AG |  | Add at 10 Annex 6 (as well at 11.5., Page 295, Regional Investment Plan 2014, CCS): Pumped Hydro Storages have played a significant role and will do so for highly efficient RES-integration, system stabilization and security of supply within a time frame less than 60 minutes.. Respecting the enormous complexity of a wide area simulation, as a convention for TYNDP 2014, the assessment is done at a 60 minutes’ time frame and these basic benefits are out of scope. However, it is expected to be part of future versions. Therefore not all benefits of PHS are part of this assessment. For efficiency reasons the assessment scheme mainly was developed for transmission line projects, where more aspects for KPI declarations are needed. Accordingly, storage projects systematically may not get the full points of some KPI’s. | (Pumped) Hydro Storage power plants have played a significant role for a highly efficient system stabilization and security of supply and thus have played a significant role for a cost effective big scale RES-integration during the past years. The German Grid Development Plan 2014 (NEP 2014) estimates an additional PHS-demand with of approx. 6 GW (!) for load frequency control reserves solely for this area within the coming 15 years. These services are mainly driven by power demand and are operated within a time frame less than 60 minutes. TYNDP 2014 and other recently published highly qualified strategy papers underline clearly, that the increasing divergency of RES-generation and demand will lead to a significant additional amount of energy driven storage capacity with medium and long term (seasonal) energy shifting. Hydro pumped storage power plants mainly in the Alps will play a basic role to meet this challenge (s. page 8, investment plan, CCS-Region). This demand is expected approx. from the year 2025 on. ENTSO-E clearly stated at the stakeholder workshops, that all assessment calculations are done at a 60 minutes time frame. Therefore all results reflect on steady state conditions and discuss more or less energy balancing aspects. This means, that power relevant aspects being relevant for PHS-LFC-services – as a con-vention – have not been assessed. While it is clear for experts that within this well defined scope only a part of PHS-benefits are assessable, the latest discussions point out, that it may be unclear for a number of stakeholders in particular for policy decision makers. To avoid any misunderstanding and other negative effects, we suggest to add the requested commentary (here at collum "E" - Proposed version) to chapter 11.5, storage projects (p. 295, Regional Investment Plan 2014, CCS): | ENTSO-E acknowledges all benefits of storage projects are not captured: the implementation of the CBA only captures the 'energy' part of the benefits, ie. only the ability to buy at cheap hours and sell at peaks and none of the operating benefits. A caveat is provided in the CBA methodology and the introductory page of the Appendix 1.3 (storage assessment) of the TYNDP report provides an explicit caveat in this respect, insisting the valuation is still to be completed with respect to 'capacity' and 'flexibility' parts of the benefits. A clarification that this comes from the simulation limited to a 60 minutes-quantum will be added.
CZ Ministry of Industry and Trade | This effort represents very significant financial engagement for TSOs. However, it only represents about 1.5-2 €/MWh of power consumption in Europe, i.e. about 2% of the bulk power prices or approximately 1% of the total electricity bill. | This effort represents very significant financial engagement for TSOs. It represents about 2,98 - 3,47 EUR/MWh of power consumption in Europe, i.e. increase based on investment to transmission projects of the European significance. The amount of investments needs for all projects, including national projects on transmission level, distribution at high and low voltage level, will be multiply higher. Subsequently all investments will have direct impact on increase of the total electricity bill. | The calculation is not in accordance with the information given to other points in the text. Electricity consumption (including pumping) is the highest for Vision 4, i.e. 4327 TWh. The repayment of investment equalled to 150 billion EUR by increasing the price of electricity for 10 years represents the price increase by 3.47 EUR/MWh. For the Vision 1 and the consumption of electricity (including pumping) 3 610 TWh, the calculation for the lowest level of investment by the Tab. 5-1 (107.5 billion EUR), represents the increase of price by 2.98 EUR/MWh. Therefore increase of prices listed in the Conclusions according to the data in the document, is 2.98 - 3.47 EUR/MWh at minimum. This information applies only to investments in projects of the European significance and does not take into account additional investments in infrastructure, that are needed for other projects of regional and national significance - see also text in section 5.4: “The portfolio of projects of pan-European significance must however be completed at the regional or national level to achieve an overall consistent development of the whole energy system. Some additional infrastructure may also be required to completely support the Vision 4 environment.“ Total investments and the increase of electricity prices as a result of investment in transmission networks and other investments induced by vision 4 will therefore be significantly higher. TYNDP does not deal with the distribution infrastructure. That is why the necessary investments in distribution networks are completely omitted, which also affects the possibility to achieve objectives that are the basis for the TYNDP 2014 creation. To avoid misinterpretation of the data in the presented document, it is necessary to provide correct and complete information. | The goal was to give an order of magnitude, hence the rounded figures. The standard duration used for the computation is 20 years but could be even longer: the amortisation of extra high voltage investments can vary but is about 40 years and 100 year old assets can here or there still prove useful; besides and the investment effort is progressive.
IFIEC |  |  | The fourth scenario is Vision 4, “green revolution”. Vision 4 reflects an ambitious path towards the 2050 European energy goals, with 60% of load supplied by RES in 2030. Compared to the 1990 level, the emissions are reduced by 78% in the ENTSO-E perimeter. These targets must be accompanied by clear recommendations on how to avoid carbon leakage for the European industry. Here apply the same comment made above (in Vision 3) with reference to the completion of market integration. | Vision 4 was built without specific recommendation about leakage of European industry (one option being: the rest of the world is aligned on the same goals, avoiding leakage).
Vattenfall AB |  |  | A general request for change to the report is that the monetised benefits and cost estimates should be used to calculate a simple but yet illustrative cost-benefit ratio that is presented for every project. | All benefits from projects cannot be monetised: monetisation of non-monetised criteria involves valuation choices that prove complex, many times with no single valuation parameters and are no consensus in Europe nowadays. The TYNDP report includes all relevant information for every reader to make his/her specific assessment of the cost/benefit ratio according to his/her parameters for monetization and/or prioritization of indicators
Europacable | "AC – with about 21000 km of new lines planned – is expected to remain the prominent technology. Around 10% of the investments actually consist of upgrades or refurbishments of existing AC assets. Most new overhead lines planned will be built using AC technology, which is still the easiest to implement for inland applications". | "AC – with about 21000 km of new lines planned – is expected to remain the prominent technology. Around 10% of the investments actually consist of upgrades or refurbishments od existing AC assets. Most new overhead lines planned will be built using AC technology, which is still the easiest to implement for inland applications. Partial undergrounding of sensitive areas will increasingly complement overhead lines". | Quoted from Deliverable D3.1. - Technology Assessment: Report on Passive Transmission Technologies (Cables) eHighways2050 project | Section 5.2.2 of the TYNDP report is amended accordingly.
CZ Ministry of Industry and Trade | , i.e. about 2% of the bulk power prices or approximately 1% of the total electricity bill. | It represents about .. % of the bulk power prices. The calculation is based on the expected price of electricity on the wholesale market in the range between XX EUR/MWh and YYY EUR/MWh. | It is appropriate to indicate the prices used by authors of the document at calculation, because the level of the wholesale electricity prices 75 or 100 EUR/MWh means difference is a significant. In addition, we are missing any notice regarding potential capacity payment - see "capacity" component, mentioned in chapter "3.6 Comparison of the Visions". | In order to give the order of magnitude of 2% and 1%, the investment annuity has been compared to the average system prices in Europe expected for 2030: basically around 50 and 100 €/MWh depending on the set of fuel and CO2 prices considered. The average end-user's bill is augmented with network costs, customer support costs and taxes and is supposed to end up twice as much as the bulk flow prices, as observed today.
IFIEC | By 2030, the main driver for power system evolution and grid development is generation. When a boundary can be flagged with more than one concern, market integration prevails over generation connection and security of supply. 60% of the boundaries are primarily related to this issue with 40% cross-border and 20% internal. Boundaries associated to market integration issues may correspond to bilateral borders between countries, but actual interconnection concerns often have to be addressed at a larger scale. |  | Here apply the same comments made in the item "Market integration and industrial energy consumers. General remarks": IE considers necessary: - To develop interconnection capacity between systems fixed by the European Commission in a minimum value of 10% of the total installed generation capacity for 2020. - The economic impact of the TYNDP 2014 must consider the present situation of the European industrial energy consumers, avoiding the risk of carbon leakage. | As previously noted, the TYNDP methodology appraises the overall benefits for Europe as a whole, based on the CBA. Benefits specific to industrial consumers depend additionnaly to the market and tariff structure in every country, falling beyond the scope of the TYNDP.
Vattenfall AB |  |  | In many cases, the estimated cost range is very large which makes it hard to assess the socioeconomic contribution for the respective project. | ENTSOE will reduce the margins on the cost of projects in the final release of TYNDP package 2014. ENTSOE would like to point out that there will always be some uncertainty in the cost of projects, especially for long term projects which detailed scope is not yet defined.
Europacable | "More than 75% of the total amount of HVDC lines will be built using cables. Submarine cables will represent the greatest length planned, with fewer kilometres onshore". | "More than 75% of the total amount of HVDC lines will be built using cables. Submarine cables will represent the greatest length planned, although over 4,600 km of cables are planned onshore". | Actual fact from TYNDP | Section 5.2.2 of the TYNDP report is amended accordingly, after checking the figures.
CZ Ministry of Industry and Trade | The consistency of the generation mix development strategy: Visions 1 and 3 build from the bottom-up on each country's energy policy; Visions 2 and 4 assume a top-down approach, with a more harmonised European integration. | The consistency of the generation mix development strategy: Visions 1 and 3 build from the bottom-up on each country's energy policy; Visions 2 and 4 assume a top-down approach, with a more harmonised European integration. The right of each Member State to determine the source mix for electricity generation is not undermined. | It should be noted at the same time, there is no doubt about the right of a Member State to determine the source mix for electricity generation. | ENTSO-E cannot express any opinion on Member States' prerogatives. Scenarios are built with the involvement of stakeholders and try to embrace all reasonnable expectations.
IFIEC |  |  | It is recommended to consider the necessary projects to complete the market integration as PCI. | PCI selection process is ruled by (EU) 347/2013 and every PCI (candidate) is assessed in the TYNDP.The TYNDP identifies the main transmission needs and comes up with a corresponding projects portfolio.
Vattenfall AB | In practice there would have been price-differences between England and Scotland, making the values different for the two projects. Additional NorthConnect is planned realized after NSN, which will make this project NorthConnect less valuable. | Change to: It is a fact that NorthConnect is approximately 10% shorter, implying lower investment costs. Furthermore, IF there will be price-differences between England and Scotland that would also make the values different for the two projects. In addition, NorthConnect is according to current plans to be realized after NSN. | A detailed comparison is not possible given the available data in the TYNDP. The formulation should be more neutral. | Comments in that section of the report only concern indicators one by one. TYNDP and RgIP reports 2014 will be amended as follows: comment on the SEW (…) one node. If there are price-differences between England and Scotland, this would make the values different for the two projects. In addition, according to current plans, northConnect is to be realized after NSN.
Europacable | "Adequate track design based on environmental criteria improves the social acceptance of new projects". | "Adequate track design based on environmental criteria as well as considering available technology options may improve the social acceptance of new projects". | Improved wording | Section 7.6 of the TYNDP report is amended accordingly.
CZ Ministry of Industry and Trade |  |  | It is not clear whether top-down vision (Vision 2 and 4) are developed on the basis of an official European or national strategic documents (e.g. NREAP for 2020). | Vision 2 and Vision 4 are built according to the methodology developped with stakeholders and eventually consulted. They derive from Vision 1 and 3 (which match the NREAP) but their overall consistency has been improved. Additional information can be found in SOAF report pp 128-133
IFIEC |  |  | The challenge for the coming decades is to facilitate larger and more power flows across Europe. For doing that we need to eliminate the bottlenecks and to increase the NTC between regions, in particular with the four main “electric peninsulas” in Europe. | Indeed, this is a major concern highlighted in the TYNDP.
North Sea Commission |  |  | These are the comments of the North Sea commission on the Ten-Year Network Development Plan 2014, its Executive Summary and the Regional Investment Plan 2014 for the North Sea Region | -
Europacable | "The situation always needs to be analysed on a case-by-case basis as environmental impacts are vastly different between overhead lines and underground cables technology". | "The situation always needs to be analysed on a case-by-case basis as environmental impacts are vastly different between overhead lines and underground cables technology. Partial undergrounding complementing overhead lines in sensitive areas may in some cases be a cost efficient compromise and an acceleration of the permitting procedure". | Quoted from Deliverable D3.1. - Technology Assessment: Report on Passive Transmission Technologies (Cables) eHighways2050 project | Section 7.6 of the TYNDP report is amended accordingly.
CZ Ministry of Industry and Trade |  |  | Visions are characterized as extreme cases. They are however used throughout the document as scenarios and are treated as scenarios also in assessing the options. It is necessary to add a description of the mechanisms that will be used, if the conclusion will be that we are heading to the extreme point specified for instance by 4 vision, i.e. to the highest costs of the system and not to the optimum from the competitiveness of European industry and end consumers of electricity point of view. | The TYNDP so-called "Visions" are indeed the scenarios, the set of assumptions that are used to identify and assess bottlenecks and then investments. The Vision 4 is indeed ambitious, but although investments costs for additional transmission capacity are high to meet this scenario, they are only a small part of the overall cost of the scenario (i.e. including generation investments).
IFIEC | Social and Economic Welfare (SEW) is characterized by the ability of a power system to reduce congestion and thus provide an adequate transmission capacity so that electricity markets can trade power in an economically efficient manner. A project that increases transmission capacity between two bidding areas allows more power in the lower-priced area to be exported to the higher-priced area. The new transmission capacity reduces the total cost of electricity supply. Therefore, a transmission project in general will increase social and economic welfare if the benefit exceeds the costs of the project. |  | The new transmission capacity will have an estimated cost of €150 billion, with a direct impact on the transmission fees of over 1.5-2 €/MWh of power consumption in Europe. However the reduction forecast due to the enhanced market integration, that would reduce bulk power prices by 2 to 5 €/MWh is not clear, in particular in regions where the market integration will be a wish more than a reality… | The reduction of bulk power prices from 2 to 5 €/MWh corresponds to the generation costs savings that the projects of pan-European significance, jointly, enable: more interconnection capacity enables more exchanges, i.e. cheap generation means can evict more expensive generation means.
North Sea Commission | The proposed projects reflect most of the investment needs. Conversely, some additional reinforcements to cover investment needs specific to the most ambitious scenarios of RES development by 2030 are yet to be designed. | The proposed projects reflect most of the investment needs. Conversely, some additional reinforcements to cover investment needs specific to the most ambitious scenarios of RES development by 2030 are yet to be designed. Although part of the financing is indicated to be potentially covered by congestion rents and grid-tariffs, proposals have to be developed how financial coverage for the remainder can be secured. | 0.7.7, page 13, after 4th paragraph Additional text | The proposed amendment is actually covered later (see last § of the executive summary)
Europacable | "AC 220kV or 400kV cables can be appropriate in densely urbanised areas where a large amount of power must be supplied over a relatively short route crossing a particularly cramped area". | "HVAC underground cable transmission technology up to 400kV finds its applications in urban and suburban densely populated areas, in submarine connections and increasingly in rural areas of outstanding natural beauty, where the implementation of overhead lines is difficult or impossible. Rather than undergrounding full projects, HVAC underground cables may be deployed in selected sensitive areas sections of a line complementing overhead line technology". | Improved wording | Section 7.6 of the TYNDP report is amended accordingly.
CZ Ministry of Industry and Trade |  |  | It is not clear which values were used in the CBA analysis. The SEW and other parameters are reported in the list of projects for individual Visions. Is the methodology described in the "Appendix 3 - Cost Benefit Analysis Methodology" fully used? | The TYNDP compute the CBA indicators for every scenario as described in the Appendix 3.
IFIEC |  |  | ENTSOE should take into account: The whole TYNDP 2014 results fully depend on the Generation considered in the 2030 visions • Any Transmission Project Proposal evaluation depends on it • Each country needs to have enough Conventional Generation to supply its load and all CCGTs have the same costs all over Europe. Therefore: RES Generation in 2030 visions have a relevant influence on the Grid Plan | Indeed, assumptions about generation mix and location are key to the TYNDP: the location, frequency and magnitude of congestions and hence the investments needs directly depend on them.
North Sea Commission | New dynamic operating concerns will thus require specific studies to anticipate potential risks. | New dynamic operating concerns will thus require specific studies to anticipate potential risks. Furthermore, more attention will be paid to the potential integration of the power grid with the grid for other energy carriers, such as gases and heat. As interest in energy conversion has grown rapidly, serious research has started up to analyse the contribution to the overall energy system of chemical conversion of energy and energy storage. Examples of technologies that could well seriously develop further are power-to-gas and liquids (electrolysis, methanation, production of biomethanol etc.) as well as various applications of hydrogen in transportation, chemical applications and otherwise. | 0.8.2, page 15, after 3rd paragraph Additional text | The comment relates to the scenario building, and can be investigated for the TYNDP 2016. Power to heat and power to gas are options comparable to power storage for the power system. ENTSO-E and ENTSO-G are working on a common methodology to articulate gas and power issues. Such development are complementary (but not a pre-requisite) to the development of means required to further investigate dynamic phenomena addressed here.
Europacable | "On the other hand, overhead technology may be more suitable than cabling when two 400kV circuits must cross a forest; compared to large trench cabling, this would require taller towers 500m apart and would enable small trees to grow behine the line, causing minimum disturbance to the biotypes (with anchorage every 500m) and be fairly invisible to anybody in the forest or admiring it from a distance". | Delete | Do not think that "admiration" of the forest is something to be included in the TYNDP. Agree that overhead technology should be used in the majority of lines to be built in Europe, not limited to forests. Also cable trench would likely to be narrower than overhead line right of way. | The TYNDP depicts an actual situation where overhead technology was preferred by local communities compared to cables.
CZ Ministry of Industry and Trade |  |  | The vision and the associated calculations are used to confirm the eligibility of each project, respectively linked projects. The procedure should be the opposite, i.e. to identify projects necessary for specific future values in scenarios (see e.g. scenarios in “Scenario Outlook & Adequacy Forecast 2014-2030“), or for limit values in Visions. | In essence, ENTSO-E first identifies bottlenecks (= where grid fails to support power exchanges triggered by market forces) in every Vision; then test what investments could fill in the gap, and last finalise the comprehensive assessment of promising projects candidates. It may happen of course that a bottleneck and projects have been identified in earlier studies and that they are merely rechecked and quantified.
IFIEC |  |  | In TYNDP 2014 the RES Generation in each country in all 2030 visions are “forecasts” • Each “forecast” has been made by each national TSO • No Government Plan in most countries (for 2030) • No Market signals considered (new capacity power asking for access) • No RES capacity costs have been considered • No long term exports/imports contracts possibilities have been considered • RES “forecasts and forecasting methodology” in TYNDP 2014 are unclear and must be reviewed for TYNDP 2016 | The TYNDP scenarios are possible futures but none is strictly speaking a "forecast". RES development (as well as other assumptions) in Vision 1 and 3 stem from national sources, brought in by TSOs complying with a common methodology, but mostly matching national scenarios stemming from governments or national authorities. These assumptions as well as the methodology to build Vision 2 and Vision 4 have been shared and consulted by ENTSO-E: they could be improved, in the framework of the public scenario building process for the next release.
North Sea Commission | New dynamic operating concerns will thus require specific studies to anticipatepotential risks. | New dynamic operating concerns will thus require specific studies to anticipatepotential risks. Also, more extensive attention will been given to the development of (quasi) decentralized energy systems, as there seems to be a clear trend towards decentralized power production and energy conversion within Europe, and also to local grid connections with local balancing and storage. This trend will clearly have a serious potential impact on future grid requirement both nationally and in terms of interconnectors. | 0.8.2, page 15, after 3rd paragraph Additional text | The comment relates to the scenario building, and can be investigated for the TYNDP 2016: types and location of generation is a key for the TYNDP studies (and decentralised generation is already considered in the TYNDP 2014, although not highlighted). Such development are complementary (but not a pre-requisite) to the development of means required to further investigate dynamic phenomena addressed here.
Europacable | New introduction | When considering the role of any future transmission technology, the aspect of security of electricity supply is predominant. Given today's dependence of society on electricity, security of supply in the transmission and distribution networks needs to be at the centre of our attention. Transmission system operators and When considering the role of any futrure tranmsission technology, the aspect of security of supply is predominant, Given today's dependence of our society on electricity, security of supply in the transmission and distribution networks needs to be at the centre of our attention. Transmission system operators and manufacturers are fully committed to this objective. Other objectives, such as environmental impacts or cost implications resulting from the choice of deploying certain techologies are highly relevant, but are under the constraint to ensure security of supply". | Quoted from Deliverable D3.1. - Technology Assessment: Report on Passive Transmission Technologies (Cables) eHighways2050 project | Security of supply is an important concern. It appears however already taken cared about in the TYNDP report; the challenges ahead being predominantly the integration of RES. Hence the tone of the TYNDP report.
CZ Ministry of Industry and Trade |  |  | Due to the high importance of comments above, we leave aside less important issues of the document, e.g. as follows: - Inaccuracies in the text (including non-compliance sum and figures listed in some tables), - Using terms without explaining their content (e.g. "Strong European Framework") , - The lack of terminology coordination between documents in the package, etc. | Inaccuracies in the text or confusing terminology is to be corrected, and we'll screen the TYNDP package to improve it. Apologies meanwhile for the inconvenience. In particular, the reference to a "stronger" or "weaker" European framework is not a strict definition, but express the differentiation between Visions 2, 4 on the one hand and Visions 1, 3.
IFIEC |  |  | EC and stakeholders required ENTSO-E to develop scenarios Top-Down (2 and 4), with a European vision – The scenarios 2 and 4 (Top-down) don´t show this European vision – In a Top-Down vision, the new European generation must follow a central criteria, not the 27 national criteria, in order to get the maximum general profit. | Scenarios were built regularly asking stakehdolders' feedback for improvement from Spring 2012 to Autumn 2014. In particular, the methodology to derive the "top-down" Vision 2 and 4 has been consulted. The TYNDP reflects the outcome of this process.
North Sea Commission | In this respect, ENTSO-E welcomes Regulation 347/2013, which features many positive elements regarding the permitting process, which will facilitate the fast tracking of transmission infrastructure projects, including proposals on onestop-shops and defined timelines. | In this respect, ENTSO-E welcomes Regulation 347/2013, which features many positive elements regarding the permitting process, which will facilitate the fast tracking of transmission infrastructure projects, including proposals on onestop-shops and defined timelines. In the light of the importance of smooth procedures and swift realization processes, a more extensive estimate of the potential costs and timeline for delivery of grid infrastructure, the major barriers to implementation as well as the risks of delay has to be made, including ideas how to deal with that. The fast tracking procedure foreseen in Regulation 347/2009 is a first step in the right direction, but is limited to PCIs only. | 0.9, page 15, after 2nd paragraph Additional text | The concern is adressed in general in §9 of the TYNDP report (with the present summary in the executive summary); and specifically to every investment in the assessment sheets.
Europacable | New introduction continued | "This need to ensure secure electricty supply has a direct consequence for technologies deployed for transmission grids and their technical evolution: 1. Technologies need to be mature and highly reliable 2. Any new technology to be deployed will have to be thoroughly tested and may only be introduced into the system in a repsonsible manner in order to ensure system stability". | Quoted from Deliverable D3.1. - Technology Assessment: Report on Passive Transmission Technolggies (Cables) eHighways2050 project | (see earlier answer to comment row 96)
Element Power | Variations in electrical losses are an indicator of the energy efficiency of a power system. | Variations in electrical losses are an indicator of the electrical energy transmission efficiency of a transmission network. Transmitting renewable energy sources from remote renewable sources will often tend to increase transmission losses, but with an overall benefits of decarbonisation and cost optimisation. | The rewording is to help improve the terminology and explanation and avoid misunderstadning from use of this measure. | Section 5.3.6 of the TYNDP report is completed in this sense. (see also answer to comment row 105)
IFIEC |  |  | As a consequence, IFIEC recommends ENTSOE for the next exercise (TYNDP 2016): - To define the RES forecast for 2030 following an optimization process (generation + transmission) considering the most efficient generation solution for Europe. - The future TYNDP scenarios should take into account de-industrialization and the resulting loss of energy consumption in Europe on account of European Regulatory costs. (see IFIEC manifesto attached for more details.) | The TYNDP 2016 is similar to the TYNDP 2014 regarding the process of scenario development: stakeholders can join in the Long Term Network Development Stakeholders Group, public workshops and consultation... before scenarios are finalised by Summer 2015.
North Sea Commission | It is also important to note that the supporting schemes are limited to the Projects of Common Interest, while there are many significant national transmission projects, which are equally crucial to the achievement of Europe’s targets for climate change, renewable energy and market integration. | It is also important to note that the supporting schemes are limited to the Projects of Common Interest, while there are many significant national transmission projects, which are equally crucial to the achievement of Europe’s targets for climate change, renewable energy and market integration. Crucial is also in what way the realization and costs of the grid infrastructure are to be ‘sold’ and promoted to the general public who will end up having to pay for it. The benefits of a grid networks to customers need to be promoted to address potential societal resistance. | 0.9, page 16, after 1st paragraph Additional text | ENTSO-E shares the concern, and addresses it in the TYNDP report. The executive summary will however not be amended in this sense as it needs to be kept short and balanced.
Europacable | New introduction continued | "Consequently, unlike in other technology sectors where 40 years may be considered a long period, allowing for substantial technology advancement, it is expected that electricity power transmission technologies will undergo only gradual developments. Having said this, cable transmission technolgies have and will continue to evolve, especially in terms of voltage ratings and distances that can be covered. Notably, 1, the introduction of solid dielectric transmission cable featuring XLPE (Cross Linked Polyethylene) insulation marked a significant step in the past years; 2, in HVAC applications, XLPE has enabled the development and increasing deployment of the concept of "partial undergrounding" where underground cables complement overhead lines; 3, the emergence of HVDC application on land and subsea marks a relevant technology innovation for Europe's future grid". | Quoted from Deliverable D3.1. - Technology Assessment: Report on Passive Transmission Technologies (Cables) eHighways2050 project | (see earlier answer to comment row 96)
Element Power | However, the main driver for transmission projects is currently the higher need for transit over long distances, often leading to increased losses | To summarise, the main driver for transmission projects is currently the higher need for transit over long distances, often leading to increased transmission losses but necessary for an overall reduction in CO2 emissions and to bring more cost effective renewable energy sources to customers. | See comment above | Section 5.3.6 has been completed in this sense. (see also answer to comment row 101)
Vattenfall AB |  |  | Please note that when uploding the template all comments were set to general and it was not possible to change to anything else than "chapter 1". In order to provide you with a back up on the actual text references to our comments we attach the filled out excel template to this comment. Br | The uploading of comments can indeed be improved and ENTSO-E will work on it. Apologies for the inconvenience.
Agder Energi | N/A | N/A | The TYNDP 2014 highlights that interconnection capacity throughout Europe will need to double in the years to come. However, one third of the TYNDP 2012 investments are delayed. The next TYNDP (2016) should include a variance analysis (current plan versus previous plan) and address possible reasons why investments are lagging behind, and also suggest solutions. This should include solutions for how this high number of projects should be financed. | Explanations for delayed investments are provided in §6 (as an overview), and specifically to every project in the assessment sheets. Two main reasons stand out, both depending on decision making outside TSOs' hands: longer than expected permitting procedures; and delayed generation projects post-poning the need to build the related transmission assets.
Europacable | "Underground and submarine HVDC XLPE (Cross Linked Poly-Ethylene) cables: some of the above mentioned HVDC projects consider the use of XLPE cables. XLPE cables are modern, the operational experience if limited to less than one decade. The supply market appears to be limited, although deliveries from Korean and Japanese suppliers could be expected in the future. However, major European suppliers have announced extensions of their production capacity". | Underground and submarine HVDC XLPE (Cross Linked Poly-Ethylene) cables: some of the above mentioned HVDC projects consider the use of XLPE cables. XLPE DC cables are state of the art up to +/- 200kV with a capacity of 500MW with some projects having reached voltages of +/- 320kV with a capacity of 800-1000 MW. Operational experience is limited to less than one decade. The technology has so far mainly been used in submarine applications, either connecting offshore wind farms to land or transmitting high electrical power over long distance through the sea where overhead lines cannot be used. Increasingly, HVDC cables are beginning to be used also for large on-shore transmission projects or power highways. At the same time HVDC Mass Impregnated (MI) cable technology continues to remain a reliable power transmission cable technology up to 525kV as it has been for the past 25 years. | Quoted from Deliverable D3.1. - Technology Assessment: Report on Passive Transmission Technologies (Cables) eHighways2050 project "Appearances" of market supply are not relevant in this context. Production capacities will follow demand. | Section 8.3 of the TYNDP report is amended accordingly.
Element Power | Figure 6-1 Target capacities by 2030 in Vision 1 (left) and in Vision 4 | n/a | It is not clear if these are additional capacities required or whether they include existing capacities. | The target capacities do include presently existing capacities. They represent total figures.
Vattenfall AB |  |  | Vattenfall welcomes the strong improvements of the TYNDP reporting and methodology achieved since the TYNDP 2012, especially increased transparency on the results, and the improved CBA method. | -
Swedenergy |  |  | See attached document | -
Europacable | "Underground and submarine HVAC XLPE (Cross Linked Poly-Ethylene) cables have been deemed as an appropriate technology selection for special applications. Mostly, cabling will be found in densely populated areas as a limited length of an overhead line. There is worldwide experience of their use offshore to connect synchronous networks and remote load centres such as island communties. AC cabling has so far been the preferred technology for the connection of offshore wind farms located close to land; a key limitation of all types of AC cables is their high electrical capacitance, which means that for longer lengths of cable the capacitive charging current becomes significant and results in a reduction in their ability to transmit real power. On land, this is mitigated by the installation of reactive compensation plants in the form of shunt reactors". | "Underground and submarine HVAC XLPE (Cross Linked Poly-Ethylene) cables have been deemed an appropriate technology selection for special applications for more than 20 years. On land, cabling will mostly be found in densely populated areas and sensitive rural areas with outstanding natural or environment heritageas a limited length of an overhead line. Looking ahead,the major technical evolution expected for XLPE HVAC cables is an increase in transmission capacity beyond today's 500kV technology. Furthermore, there is worldwide experience of their use offshore to connect synchronous networks and remote load centres such as island communties. AC cabling has so far been the preferred technology for the connection of numerous offshore wind farms located close to land." | Quoted from Deliverable D3.1. - Technology Assessment: Report on Passive Transmission Technologies (Cables) eHighways2050 project. References to shunt reactors not necessary in the context of most partial undergrounding solutions | Section 8.3 of the TYNDP report is amended accordingly. Reference to the high electrical capacitance is kept, but in a more neutral tone.
Element Power | Together with this report, the 6 Regional Investment Plans and the Scenario Outlook and Adequacy Forecast 2014-2030 outline, in more granular detail, the various investment needs for pan-European grid development | n/a | Please provide data in report in a spreadsheet so that stakeholders can see details of GW installed, GWh produced and flows on assets. | The spreadsheet with the GW installed is already available on the ENTSO-E website. The number of simulation done and the amount of data make it impossible in practice to share flows on assets. GWh are available in spreadsheets.
Vattenfall AB |  |  | The TYNDP 2014 explores a large spectrum of possible 2030 outcomes. We recognize that ENTSO-E has been working hard with short deadlines to finalize the TYNDP in line with the energy infrastructure's requirements. However, we think that a socio-economic assessment of long term investments based on analysis results of only 2030 is too limited. Modelling results for at least 2020 (but preferably also 2025) for all scenarios and stages of grid development would improve transparency of TSO priorities over time. | Resources constraints compelled ENTSO-E to limit the investigations, and stakeholders feedback put priority on 4 visions at longer horizon, rather than exploring a second, intermediate horizon. TYNDP 2016 will provide a more complete picture in this respect.
Diamon Tranmsisison Corp |  |  | If the intent of the document is not only to announce where projects are required but to facilitate investment, then the document could provide more information about the relative parties supporting the projects. | The purpose of the TYNDP is to display the required grid reinforcements, for all stakeholders. Project promoters are the concerned TSOs, members of ENTSO-E, except for the few projects promoted by consortia not members of ENTSO-E.
Europacable | "Gas Insulated Lines (GIL) is mature and exhibits a high degree of reliability. The technology is derived from the Gas Insulated Switchgear (GIS) technology, which has been in use for more than four decades. Many projects have been realised worldwide and the latest GIL project as part of European transmission grid was commissioned in 2011 (1.9km, Kelsterbach, Germany)". | "Gas Insulated Lines (GIL) is mature and exhibits a high degree of reliability. The technology is derived from the Gas Insulated Switchgear (GIS) technology, which has been in use for more than four decades. Many projects have been realised worldwide and the latest GIL project as part of European transmission grid was commissioned in 2011 (1.9km, Kelsterbach, Germany). However, GIL is only expected to offer a very limited contribution to the network by 2030". | Quoted from Deliverable D3.1. - Technology Assessment: Report on Passive Transmission Technologies (Cables) eHighways2050 project | Section 8.3 of the TYNDP report is amended accordingly.
Element Power | The increase of RES is large, all over Europe. Solar power jumps from 69 GW today to 224 GW, while wind power increases from 105 GW to 361 GW. | n/a | Vision 3 has only 224GW of PV and Vision 4 only 339GW. The EPIA market outlook 2014-28 has a high case of 500GW in 2030. This expert organisation's view should be used in Vision 3 and exceeded in Vision 4 | The methodology for building the scenarios has been publicly shared and consulted from Spring 2012 to Autumn 2014. Experts organisation, EPIA in particular, have been kindly required to contribute, especially in the framework of the Long term network development stakeholders group. The TYNDP reflects the outcome of this process.
Vattenfall AB |  |  | The future TYNDP must be clear on how the actual grid is affected and go beyond the ENTSO-E Technical Report prepared for the pilot bidding zone review project. The TYNDP should at least include details on current bottlenecks, how they are managed currently and over time. The analysis should show the location, frequency and amount of congestions realised in the European transmission grid. Congestions should preferably be analysed in stages 2015, 2020, 2025, 2030. | The TYNDP package is already heavy. Information regarding present and mid-term situation are available and updated on the ENTSO-E web site, from detailed data to synthetic reports. Regarding investments though, the assessment of projects at an intermediate horizon is foreseen in the TYNDP 2016.
Diamon Tranmsisison Corp |  |  | It would be useful to have more detailed explantion of why the price differences occur between the countries in the various scenarios. The information provided is general and at a high level | ENTSO-E experts are available to provide more detailed information. The report can in this respect only display a synthetic overview.
Europacable | "HVDC technology has proven its reliability and attractiveness for long distance power transmission, long submarine cable links and the interconnection of asynchronous systems. Converters to convert from AC to DC and DC to AC are critical.” | "HVDC technology has proven its reliability and attractiveness for long distance power transmission, long submarine cable links and the interconnection of asynchronous systems. HVDC cables are also beginning to be used for large on-shore transmission projects or power highways". | Unclear why reference to current converters needed in this paragraph | Appendix 4 of the TYNDP report is amended accordingly.
Element Power | For instance, solar jumps from 69 GW today to 339 GW, while wind power increases from 105 GW to 431 GW. | n/a | Vision 3 has only 361GW of Wind and Vision 4 only 431GW. The EWEA Pure Power forecast in 2011 has a forecast of 400MW in 2030. This expert organisation's view should be used in Vision 3 and significantly exceeded in Vision 4 | The methodology for building the scenarios has been publicly shared and consulted from Spring 2012 to Autumn 2014. Experts organisation, EWEA in particular, have been kindly required to contribute, especially in the framework of the Long term network development stakeholders group. The TYNDP reflects the outcome of this process.
Vattenfall AB |  |  | The challenge to reach an agreement on methodologies and regulatory mechanisms for cost allocation across borders is not mentioned in any part of the report. The report should at least indicate which projects depend on cross-border cost allocation between more than two member states. | The TYNDP aims at determining where investments are required in Europe and this evaluation considers the overall European welfare as a whole. CBCA issues comes next. They are however adressed in further, project specific and complex analyses. The TYNDP is a demanding exercise already, that cannot address efficienty CBCA issues additionnally.
Diamon Tranmsisison Corp |  |  | Figures 3-5, 3-9, 3-13 and 3-17 would benefit from a key to explain the yearly average cost, if only to mark the low and high shading. | The legend of the maps in chapter 3 is improved in the last edition. (+ see answer to comment row 34)
Europacable | "Meshed DC systems could appear with the advent of commercial DC breakers". | "Voltage levels of DC underground and subsea cables will continue to increase considerably. By doing so and with circuit breakers and switchgear equipment gaining market experience, meshed HVDC networks will become possible, thus creating the meshed HVDC overlay networks that Europe will need and the capacities enabling market integration and security of supply across Europe". | Reference from Deliverable D3.1. - Technology Assessment: Report on Passive Transmission Technologies (Cables) eHighways2050 project | Appendix 4.2.1 of the TYNDP report is amended accordingly.
Element Power | The increase of RES is large, all over Europe. Solar power jumps from 69 GW today to 224 GW, while wind power increases from 105 GW to 361 GW. | n/a | Vision 3 has only 361GW of Wind and Vision 4 only 431GW. The EWEA Pure Power forecast in 2011 has a forecast of 400MW in 2030. This expert organisation's view should be used in Vision 3 and significantly exceeded in Vision 4 | (see answer to comment row n°121)
Vattenfall AB |  |  | Third party projects are included in the TYNDP for the first time – this is an important improvement to the first TYNDP. We look forward to the further development of the procedures for inclusion of 3rd party projects. All transmission projects should be treated equally and have the same status in the TYNDP. Thus, all maps, tables, etc. should include TSO projects and 3rd party projects. | ENTSO-E and non-ENTSO-E project promoters have been treated equally in the TYNDP 2014, with a non-discriminatory application process. TSOs and TSOs projects are displayed the same way. The implementation of the process proved difficult (advertising, completion of application, assessment finalisation deadlines...) and can certainly be improved... on both sides.
Diamon Tranmsisison Corp |  |  | There is limited information on energy storage and the need for grid services (reactive power and frequency response), both of which will be esential components of the future European grid. Therefore further information would be welcomed | Indeed, as stressed in the report, investigating dynamic phenomena on top of the presently performed steady states analyses would definitely improve the findings, showing more benefits for grid and storage projects. This is all the more critical for the latter, that the ancillary services they can offer represent more benefits than the presently assessed business of pumping at cheap hours and generating at peak prices.
Europacable | "For HVAC cables, however, no withstanding the reecnt technological progress, the further deployment and consequent cost reduction, the cost barrier (when compared to conventional solutions) is still high and is expected to remain so due to the intrinsic higher complexity and installation constraints of this technology". | "For HVAC cables, however, not withstanding the recent technological progress, the further deployment and consequent cost reduction, the cost barrier (when compared to conventional solutions) for fully undergrounded projects is still high and is expected to remain so due to the intrinsic higher complexity and installation constraints of this technology". | Cost barrier not such an issue for partial underground solutions | Partial undergrounding induces specific costs at the transition between overhead conductors and undergound cables and they may not be negligible.
Element Power | For instance, solar jumps from 69 GW today to 339 GW, while wind power increases from 105 GW to 431 GW. | n/a | Vision 3 has only 224GW of PV and Vision 4 only 339GW. The EPIA market outlook 2014-28 has a high case of 500GW in 2030. This expert organisation's view should be used in Vision 3 and exceeded in Vision 4 | (see answer to comment row n°117
Vattenfall AB |  |  | We urge ENTSO-E to further increase transparency on the results. Instead of using colours and price intervals between bidding zones, we propose that the TYNDP presents actual results in terms of money. In addition, we suggest that ENTSO-E presents the hourly results (flows and prices). We suggest the results are presented both in a table summarizing the results and in the form of duration curves covering the whole period which is being examined. The hourly values should be presented, the reason for not presenting them is not clear. In the report it is e.g. stated on p 40: “Yearly averages are not sufficient indicators to make decisions regarding grid extensions (hourly values are more useful in this respect)”. The simulations are made with hourly resolution. It is, thus, strange why not the hourly values are included in the report. | Hourly values are displayed in the TYNDP when details are provided on a specific bottleneck or project: mostly, they are displayed as monotonous (or not) hourly load curve. The bulk power flows and hence target capacities also derive from thresholds appraised at hourly level. Should ENTSO-E publish more material? 1 sole run of a probabilistic tool can be 8970 h time x about 1000 draws time about 40-100 nodes/boundaries time about 100-200 possible outputs (marginal price, but also power generated by every single generation means, etc.) so about 10 billion values. For about 100 projects to assess one by one, about 100 runs are needed, time 4 scenarios (not accounting for calibration nor variants), so that market studies basic results solely amount to more than 1 trillion values (not to mention cross-checking between tools). 1 load flow with a network models of 3000 nodes/6000 branches, is about 100 000 to 1 million output values; considering systematic N-1 analyses, and not mentioning topology adaptations, testing of reinforcement options, network studies' outputs can represent about 1 trillion values as well, from which only part is actually useful.
Nordenergi |  |  | Nordenergi, the joint collaboration between the Nordic associations for electricity producers, suppliers and distributors, welcomes the opportunity to comment upon the draft Ten-Year Network Development Plan for 2014. The work has been aspiring and the reports from the different regions are ambitious. Some of the reporting has clearly improved since the pilot TYNDP 2010, and Nordenergi’s comments should be seen in the light that we recognize the complexity of the issues involved, and we do see that the TYNDP 2014 is a further step in the direction of a transparent process for developing the regulated infrastructure of the European electricity market. Our comments concern the general documents, the Baltic and Nordic Sea regions of the TYNDP 2014. | -
Europacable | "Nevertheless, these underground assets represent a specific risk for operation that has to be carefully analysed; on the one hand this technology is less exposed to external events, but on the other hand it causes long outages when damaged". | Delete | There is no similar reference to outage times of overhead lines, which when more than one pylon is concerned (e.g. snowstorms) may well equal outage times for underground cables. | The sentence highlights both the risk of meteorological events for overhead lines; and the length of default localisation and repair for cables. On average, these are factual discrepancies between the two technologies.
Element Power | Figure 3-21 | n/a | Please show current (2013/4) capacity for comparison and solar and wind seperately. | Wind and solar are merged on the figure in order to show that they represent jointly the major increase in generation capacity from Vision 1 to Vision 4. As a rule of thumb you can compute the amount of power generated by wind (resp. solar) by multiplying the generating capacity by 25% (resp. 10%) time 8760 h.
Vattenfall AB |  |  | Gaining public acceptance is a major challenge to realise the TYNDP and the investment needed to transform European energy supply. Vattenfall suggests that ENTSO-E and/or ACER forms an ad-hoc group, with a balanced group of stakeholders participating, to discuss and analyse common difficulties with the permitting process and with the explicit task to publish concrete ideas on how to speed up the permitting process. | ENTSO-E launched the long term network development stakeholders' group in 2012. The group started addressing the issue and devised refined indicators to replace the old social and environmental indicators with an objective measurement of the km of grid assets crossing protected (resp. urbanised) areas. The next steps is to have grid supporters expressing themselves publicly in local debates: in a local public debate, non-TSOs supporters are much more convincing than TSOs when advocating grid assets.
Nordenergi |  |  | Infrastructure creates options. Compared to the vast sums expected to be invested in electricity generation, the infrastructure investments, however large, are small in comparison. But as long as the European power systems are fundamentally different, the option values created by building new infrastructure must be accounted for. In the Baltic and Nordic Sea regions, all bidding areas have their own characteristics. This fundamental truth makes it more likely that there will be too little infrastructure built than too much. | Different technical and regulatory backgrounds always complexify the set up of new projects. Yet, the TYNDP, with its focus on technical issues, leaving aside organisation and regulatory concerns, is efficient in identifying appropriate options for grid reinforcements. It is then up to authorities and operators locally to make them happen.
Tractebel |  |  | Important improvements have been made from the TYNDP 2012 process in order to analyse the system as a whole and to determine transmission needs from a European perspective. However, investment planning in the TYNDP still mainly relies on national perspectives. For example, the TYNDP analysis shows important price differences between the Nordic countries and Continental Europe for all the different visions (even considering planned interconnection projects). This suggests that further increases of interconnection capacity between these areas could significantly increase the European social welfare. The TYNDP must in the end demonstrate that the proposed projects actually give the highest social-economic welfare for Europe and that no other/alternative projects would provide a higher social-economic welfare. Otherwise the project portfolio has to be adapted. ENTSO-E must play an important analytical and advisory role using the top-down approach in order to ensure consistency between the national plans and even more importantly point out projects of European interest; even those with limited national interests or even negative national interests. | The TYNDP role is to increase the trasnparency on the necessary pan-European infrastructure in order to reach the European targets. It also indentifies the main bottlenacks in the system and the issues assocaited to tehir mitigation. In this sense the TYNDP had defiend clear criteria for indentifying the proejecst of Euroepan relevance, projects are are further assessed( agains 4 contrasting visions) and therefore demonstrated to bring possitive benefits to Europe. The TYNDP is updated every 2 years process which allows an in time adaptation of the plan based on the latest anaysis and conditions. The TYNDP is a middle step towards the 2050 targets. Looking at 2030 TYNDP allows a more indepth view on teh necessary infrastructure ( concrete projects) conpared to the 2050 perspective. They are working weel together since tehy tacke different resolution for the grid development.
Tractebel |  |  | The e-Highway2050 project (funded by the European Commission), in which ENTSO-E participates, plants to develop such top-down planning methodology. Interactions between the two projects, TYNDP 2014 and e-Highway2050, must be clearly addressed and discussed. | The to projects are complementary one to another, TYNDP looking from now into the future; e-Highway2050 looking at 2050 and then backwards to 2030. The TYNDP 2014 has been projected to 2030 in order to build the bridge: in 2015, ENTSO-E plans to complete the analyses of the 2030 horizon for the Regional investment plans considering with the (or, at least, one) same scenario as eHighway for the 2030 horizon.
Tractebel |  |  | Tractebel Engineering. The Cost Benefits Analysis (CBA) results in the TYNDP 2014 are based on a wide set of data and models. Many of these may be commercially sensitive information or subject to confidentially rules. However, for the transmission projects in the design & permitting phase, more detailed technical information must be provided. Additional information indicating the type of investment items such as overhead line, substation, etc. must be included in the tables. This would improve the overall quality and transparency of the TYNDP release. The TYNDP 2014 also now includes some storage projects of common interests (PCIs) that are equally assessed according to the CBA methodology. The description of these storage projects suffers even more from a lack of technical details. While storage project have to be third party investment projects (from deregulated players), it is of prime importance to allocate sufficient time and effort in the TYNDP process to monitor and analyse possible interaction with these projects. | Technical details for every investment is provided in the assessment sheet of every project, with the level of details that are available from the project promoter(s).
Tractebel |  |  | According to the report, more than one third of the investments are delayed compared to the initial schedule. This has already been observed in the previous release and no change in this trend is observed. The reasons for these delays must be explicitly reported and in-depth analysed. An action plan to overcome this problem must be proposed in the next TYNDP. Without clear changes in the trends of delays in the projects, it means that the schedule of the projects of the TYNDP is not realistic and must be changed. The baseline vision of the TYNDP must be a realistic one and no wishful thinking. | Project delays are displayed for every investment, with the reason for the delay. Such case by case issue, that can only be very briefly summarised in the TYNDP tables, inviting the reader to contact the project promoters for more details. Overview of the concern in the main body of the report merely issue a generic warning.
Tractebel |  |  | Finally, it is needed to make available a database of the project portfolio, like it was the case in the previous release of the TYNDP, with an Excel file. | The projects/investments list shall be displayed in a spreadsheet but the information to display is quite large and complex and would be require a database. ENTSO-E is still working on the format to make it as easy as possible to manage by stakeholders.
Tractebel |  |  | Multiple alternatives exist for addressing adequacy concerns. These different solutions may in some cases be complementary and in other cases be alternatives to each other. They include network reinforcements but also generation or storage investments. The methodology of the TYNDP 2014 has to present how the competition/complementarity or interaction between the regulated solutions (network reinforcements) and the deregulated solutions (e.g. generation or storage investments) is assessed. | The TYNDP (CBA) methodology considers load, generation and storage as input data, in order to appraise transmission concerns. In other words, storage, DSR and generation mix assumptions are exogenous. The rationale is the relatively high cost of generation and storage means compared to transmission. Later on, when assessing every project, be it transmission or storage, the valuation compares the situation with and without the project.
Tractebel |  |  | Security of Supply (SoS) is one of the main drivers for European network development. However, SoS issues do not seem to be addressed and analysed in a sufficient way. Further details on the methodology followed to assess the security of supply of the system have to be provided in the TYNDP. | Security of supply is an important concern, but securing the supply of load centers appears to be a more local than pan-European issue as far as transmission is concerned. One exception is the supply of southern Germany. The explanation for this paradox relies in the fact that all 4 "Visions" assume a generation mix in Europe that overall matches load. (Conversely, if investments in the generation means are missing, then SoS will become an issue of pan-European significance.)
Tractebel |  |  | Concerning loss variations, it must be noted that the main driver for transmission projects is currently the higher need for power transfer over long distances, which increases losses. Thereby, the socio-economic welfare of the entire system can be increased even with higher thermal losses. Variation in losses is therefore not a relevant benefit indicator per se. Furthermore, the monetisation of these variations in thermal losses is already accounted in the total cost of generation. | The variation of losses is a relevant indicator per se: first of all this focus has been required by some stakeholders and furthermore, it is not accounted for in the computed in the total cost of generation in the market studies nor in the SEW, when projects are assessed.
T&D Europe | Some are even though they might not be largely implemented, i.e. they have already proved their general applicability, have been fully developed, tested, their operation within the existing meshed grid has proved reliable and introducing new items is not a technological challenge. DC connections between synchronous and asynchronous areas and Phase Shifting Transformers (PSTs) are examples of such mature technologies. | Some are mature, even though they might not be largely implemented, i.e. they have already proved their general applicability, have been fully developed, tested, their operation within the existing meshed grid has proved reliable and introducing new items is not a technological challenge. DC connections between synchronous and asynchronous areas, Phase Shifting Transformers (PSTs), Static Var Compensators (SVC, STATCOM) and Series Capacitors (SC) are examples of such mature technologies. | FACTS devices can be categorized as being mature, because:  The first installation of an SC by an ENTSO-E member was made in 1950. There are now at least 20 SC installations currently in operation in the European transmission grids, and more than 400 installations world-wide.  The first installation of an SVC by an ENTSO-E member was made in 1982. There are at least 50 SVCs currently in operation in the European transmission grids, and further installations are currently under construction and procurement. World- wide, there are well over 300 SVCs owned and operated by transmission system operators.  At least 10 of the actual ENTSO-E member companies have SCs, SVCs or both technologies installed in their transmission grids. The acronym FACTS refers to many different technologies: SVC, STATCOM, SC, TCSC, SSSC, TSSC, TSSR, TCSR etcetera. It is correct that the latter four technologies exist only as pilot installations or even conceptual designs that have never actually been built in full scale. | This introductory text in section 4.2 of the TYNDP report is aimed at illustrating the different level of maturity for technologies and only a few examples are provided. A comprehensive list of technologies ios displayed in the rest of the section.
T&D Europe | Some are in the development phase, i.e. no feasibility questions remain, but some resources are needed to engineer some still missing elements (e.g. some operating IT, some forms of Flexible AC Transmission System – FACTS). | Some are in the development phase, i.e. no feasibility questions remain, but some resources are needed to engineer some still missing elements (e.g. some operating IT, some forms of Flexible AC Transmission System like SSSC, TSSC, TSSR, TCSR). | SSSC, TSSC, TSSR, TCSR exist only as pilot installations or even conceptual designs that have never actually been built in full scale. | This introductory text in section 4.2 of the TYNDP report is aimed at illustrating the different level of maturity for technologies and only a few examples are provided. A comprehensive list of technologies ios displayed in the rest of the section.
T&D Europe | Flexible Alternating Current Transmission System (FACTS) equipment is a family of power electronicsbased devices able to enhance AC system controllability and stability and increase power transfer capability. FACTS are naturally compared by TSOs with mechanical driven equipment providing controllability features, such as Phase Shifting Transformers (a simpler, more robust, reliable and generally less costly solution, but with limited dynamic capabilities). | Flexible Alternating Current Transmission System (FACTS) equipment is a family of power electronics based devices able to enhance AC system controllability and stability and increase power transfer capability. When voltage stability is limiting the transfer capacity of a power line, SVC or STATCOM may be an economically attractive solution compared to upgrading the power line, or construction of a new line. They also have the added benefit of a significantly shorter implementation time. SC is used for long transmission distances to improve the transfer capacity by reducing the impedance, to reduce transmission losses and to improve system stability. | A very common reason to install dynamic shunt compensation (SVCs or STATCOMs) is that the transfer capacity is limited by voltage stability. By installing an SVC or a STATCOM, the TSO can avoid or postpone new lines or upgrades of existing lines. It is not straightforward to compare SVCs/STATCOMs and phase-shifting transformers since they solve different problems in the transmission grids. | ENTSO-E acknolwedges the benefits of statcom and svc. Voltage stability is a very rare issue in the European dense network, and the potential for statcom, svc is rather low. The comparison with the PSTs can be removed and Appendix 4.2.2 of the TYNDP report is amended accordingly.
T&D Europe | Costs, complexity and reliability issues nowadays represent the main barriers to the integration of these promising technologies from the TSOs’ perspective. Up to the present, shunt devices (like the SVC, Static VAR Compensator) have been the most widespread and mature FACTS technologies. Further FACTS penetration will depend on the technology providers’ ability to overcome these barriers thanks to more standardisation, interoperability and economies of scale. | SC technology is a cost efficient way to reduce losses, improve stability and increase the transfer capacity of long transmission lines. FACTS devices operate completely automatically and require no operator intervention. TSOs requirements on reliability and availability can normally be met. | SC technology is a cost efficient way to reduce losses, improve stability and increase the transfer capacity of long transmission lines. | ENTSO-E and ENTSO-E members welcome promising technologies, but there are only few application cases of SC technology in Europe.
T&D Europe | Key technology challenges are related to power electronic topologies and the exploration of new types of semiconductors replacing silicon. More user-friendly interfaces and proof of performance through field testing will contribute to improved confidence among TSOs in these new technologies. Like other active equipment (HVDC (VSC) and PST), FACTS will be crucial for the future integration of RES into the European system while also delivering full benefits when subject to a coordinated control in combination with Wide Area Measurement Systems (WAMS). | Like other active equipment (HVDC (VSC) and PST), FACTS will be crucial for the future integration of RES into the European system while also delivering full benefits when subject to a coordinated control in combination with Wide Area Measurement Systems (WAMS). | R&D efforts are continuously made for all power products and systems in order to benefit from the latest developments and ensure continuous product development. | ENTSO-E contributes to R&D efforts and in this section underlines the crucial role of FACTS. As a matter of fact, technology is evolving and field testing is required before large scale implementation.
T&D Europe | Illustration: such a technology is considered as a possible help in operations, but does not appear specifically under this name in the TYNDP list of investments. Nevertheless, some TYNDP projects involve banks of capacitors include SVC. | Illustration: The technology is considered as a possible help in operations. Some TYNDP projects involve banks of capacitors inclusively SVC. FACTS technologies therefore appear specifically under this name in the TYNDP list of investments. | FACTS technologies should appear specifically under this name in the TYNDP list of investments. | ENTSO-E will consider the suggestion of standardising the investment description for the next TYNDP and debate the options in the long term network stakeholders' group.
Ampacimon |  |  | Innovative grid technologies that allow to increase the efficient use of existing power infrastructure, for instance by maximizing the use of the capacity of the current European networks, have not yet been sufficiently deployed across Europe due to the lack of appropriate regulatory framework. ENTSOE’s TYNDP should consider these technologies as some of them are already commercially available and others will have matured over the time horizon of this plan. | ENTSO-E did consider the opportunity of HTLS conductors or DLR to increase the capacity of existing assets. Many TYNDP projects for instance rely on HTLS conductors. As far as possible, upgrade of existing assets, including the use of smart technologies such as DLR, is envisaged before new routes are proposed.
Ampacimon |  |  | There are a number of already developed and mature innovative grid technologies that can immediately help the power system to adapt to the new challenges by increasing efficiency and reducing energy costs. In this document, Ampacimon has chosen to detail the benefits that Dynamic Line Rating, as an example of one of these technologies, can bring to the European power system. | (see previous answer)
Ampacimon |  |  | During the next 10 years, a revolution, which has already started in some European regions, will occur in the power grid including o Massive deployment of renewable energy (RES) which is by nature decentralized and intermittent. o Storage of energy which is also decentralized. o Demand-side management to create flexibility at the end-user’s side | This perspective is consistent with the most ambitious Visions regarding RES penetration. Yet, RES develop mainly where the potential is highest (e.g. offshore wind); storage is mostly proposed as pump storage; and DSR shows a limited impact at pan-European level.
Ampacimon |  |  | This revolution will completely redistribute power flows in the existing power grid. Local storage will reduce flows in the transport network. Wind and solar production will create higher flow during short periods of time which will cross several countries while DSM might create unpredictable load fluctuations. There are a lot of uncertainties about the evolution of these flows. | (see previous answer)
Ampacimon |  |  | There are several strategies to manage this uncertainty. The TYNDP mainly proposes to significantly invest in new power lines or line upgrades to manage the worst case (highest excepted flows in N-1 situation). If the worst case occurs during 5% of the time, the network is used inefficiently during 95% of the time. This revolution is similar to telecommunication revolution that occurred in the 1990’s which transformed dedicated analogic phone network (low efficiency) to best-effort internet TCP/IP network (high efficiency). | ENTSO-E acknowledges and welcomes smartgrid technology breakthrough. Physics must however be complied with, and instant large surpluses of RES must either be instantly consumed on site; or stored on site; or transported where they be taken advantage of; or wasted.
Ampacimon |  |  | Another approach is to use a more Active Network Management. Active network management strategy requires monitoring and control. Monitoring includes measuring the actual state (available capacity = ampacity) of the lines in real time. It also includes short-term forecast (1h, 4h) and long term forecast (24h, 48h). Control includes the different solutions to control the production (curtailment, flexible reserve), the flow (PST, HVDC, topology changes) and demand (Demand Side Management, Smart grid). With both monitoring and control, the existing infrastructure can be managed more efficiently while providing the same (or even better) security. Using a more active network management does not mean that more new lines or line upgrades aren’t needed. A combination of both approaches is needed and would significantly change the investment picture proposed in the TYNDP | (see previous answer)
Ampacimon |  |  | In the next decade, for the first time TSO and DSO will be in competition with other alternatives. Local storage technologies are rapidly developing; several countries like Germany largely subsidies these technologies. With solar panels, local storage and flexible devices, a customer can play autonomously. In the coming years, if the price of the electricity transport is too high, customers will have the choice to disconnect from the network and use their own production. In the next decade even more than now, the electricity transport costs must be competitive with other alternatives. Moreover, as transport and distribution costs increase as a proportion of overall end-customers costs, public acceptance for new grid infrastructure such as over-head transmission line with further decrease. | Consultation on scenarios indicated different opinion on local storage perspective. Descrepancies between consumer needs and RES generation would require tens or hundreds of GW of local storage by 2030 if transmission of surpluses to deficit areas is not enabled
Ampacimon |  |  | Line monitoring can be deployed very quickly in a matter of weeks. It’s a known issue that grid reinforcements take nearly a decade in countries with dense populations. The 2014 TYNDP document refers to [30%] of delayed projects 2 years only after the previous plan (page 98 “Monitoring of the TYNDP 2012”). DLR can be a quickly deployed solution mitigating the fact that large new infrastructure projects suffer from quasi-systematic delays. Moreover, as the foreseen TYNDP calls for massive funding needs from European TSOs over the next 10 years, DLR’s considerably lower cost offers a financially affordable solution to strengthen the grid much quicker than conventional ones. | If the DLR system answer the operational need, its installation on a line can in itself be quick. But its implementation must be carefully planned in order to ensure its articulation with other grid components and ensure safe operation.
Ampacimon |  |  | DLR should not only be thought of as part of grid’s for operation, it is also relevant for planning purpose due to the high uncertainty ofnext decade’s power flow evolution. | DLR can indeed be an option for planning, yet it is not a panacea.
Ampacimon |  |  | DLR forecast 24h and 48 should also be used to avoid market decoupling due to cross-border line capacity limitations. This can considerably reduce congestion rents at a very low marginal cost per extra MW of transmission capacity offered to the market. These congestion rents could be re-distributed to end consumers through tariffs and/or re-invested in more critical new lines needing funding, therefore delivering very significant social welfare for very moderate investments. | (see previous answer)
Ampacimon |  |  | Dynamic line rating is one of the possible solutions the grid needs in order to be operated securely and optimally in the context of the energy revolution underway. DLR should be considered as a priority investment and should become an option considered as part of the ENTSOE ten-year network development plan. We recommend that DLR is considered systematically as a credible alternative to new lines on interconnections and critical branches (see Flow-based critical lines). | (see answer above)
Ampacimon | “Real-Time Thermal Rating (RTTR)-monitored cables/lines, or Dynamic Line Rating, are on their way to become a mature technology based on real-time control of the thermal rating of a line or cable. RTTR technology is rather mature, but needs further development to address integration challenges. In areas with especially high system loads, the possibility of installing modules without the need for any system outage has also been tested and validated.” |  | DLR is now a mature technology available commercially by several manufacturers since several years ([TWENTIES-REPORT], [ONCOR-DLR], [CIGRE-498]). | -
Ampacimon |  |  | - Ampacimon solution is already used routinely by ELIA and RTE to operate several lines in real-time and short term forecast. Several other TSOs (REN, National Grid, Terna, 50Hz) have also performed several pilot test installations. | -
Ampacimon |  |  | - To manage winter 2014/15 high constrains on the Belgium grid (due to the shut-down of 3 nuclear plants), ELIA will monitor transnational border lines with France and Netherlands. DLR monitors the Sag and Ampacity of each line in real-time. The ampacity | -
Ampacimon |  |  | - See [ONCOR-DLR]for a reference in US. | -
Ampacimon | Real-Time Thermal Rating (RTTR) – monitored cables/overhead lines, or Dynamic Line Rating – is on its way to become a mature technology based on the real time control of the thermal rating of an overhead line or a cable. It aims at maximising the capability of a transmission line/cable while respecting design margins, thus reducing potential congestion problems. Its further development will be facilitated by solving some practical integration challenges: integration with other tools, interoperability with protection equipment settings, coordination of RTTR monitored links, communication with SCADA and use of RTTR output values at a dispatch level. The combined use of RTTR measurements with weather forecasting might significantly increase the value of RTTR for network operations; this could become an interesting option for TSOs to achieve higher transmission capacity ratings safely and reliably for existing systems at relatively low investment costs (when compared to the investment needed for new transmission links). The challenge here consists of developing more reliable and precise wind forecasts. Illustration: Real-Time Thermal Rating Projects do not explicitly appear as such in the TYNDP list as they are not considered by TSOs as necessarily directly related to the development of the European transmission grid.” |  | As explained in the general remarks, DLR with line sensors has a wider usage than reducing potential congestions. DLR allows monitoring of the clearance of the line in real time. ([NERC-CLEARANCE]). DLR allows reduces curtailment of wind farms ([TWENTIES-REPORT]). DLR should be considered as one of tools to operate the network more efficiently. | -
Ampacimon |  |  | - Commercial solutions are available on the market to integrate with existing tools (SCADA, EMS …). At ELIA and RTE, DLR is used in daily operation since more than two years. The Ampacity (and forecast ampacity) is sent directly to the SCADA. TSOs uses th | -
Ampacimon |  |  | - DLR technology is now ready for large scale deployment on European scale. | -
Ampacimon |  |  | - commercially available. | -
Ampacimon |  |  | - Based on all the arguments above, DLR (or Real-Time Thermal Rating) must be considered as a key technology for the European transmission grid. This must become a commodity for the network operation and planning. | -
RSE |  |  | RSE believes that the four visions of ENTSO-E can define a good range of possible future scenarios, but we think that additional drivers should be considered for a further characterization of such visions. Considering the challenge of integrating more and more RES generations, the deployment of energy storage systems (both for a local and centralized use) plays a key role that should be taken into account, at least in the framework of a sensitivity analysis. At the same time, hypotheses on the technological development of power system components allow to consider different technologies in the field of generation (new RES technologies, CCS, etc), transmission (FACTS, HVDC, superconductor,…), distribution (deployment of smart grids) and operation of power system. In the future this aspect could be introduced as an additional axis for the vision identification, or anyway it should be strongly considered in the framework of sensitivity analyses. | ENTSO-E takes note of the suggestion and RSE is invited to contribute actively to the preparation of the scenarios for the TYNDP 2016.
RSE |  |  | For sake of completeness and transparency, in the chapter of TYNDP in which the four visions are presented, the general assumptions regarding the fuel and CO2 prices considered should be presented, allowing the reader a better understanding of the scenario. In addition, together with these figures, the average merit order of power technologies resulting in each country for each vision could be presented, in order to point out the main effect of the assumptions on the conventional power sources. Moreover, details on the values assumed in each country for electric vehicles, heat pumps, demand response and their effect on the resulting demand are welcome. | Details about the scenario assumptions can be found in the SOAF. But the Chapter 3 of the TYNDP report will be complemented in this respect to give a better overview.
RSE |  |  | Pag. 32: RSE welcomes the opportunity to evaluate a set of different Points in Time to be analyzed in detail by means of network studies: therefore, it is suggested to pay particular attention to the translation of market-based results as inputs for network studies in Regional Groups considering different levels of spatial detail (e.g., generation scheduling from clusters to buses, bulk power flow from neighbor countries translated in flows through interconnection lines, etc.). Moreover, different levels of time detail (8760 h/yr for pan-European/Regional Group market based simulation, a set of Points in Time for Regional Group network simulations) suggests to properly take into account storage and demand-side management, in order to maintain sufficient level of representativity for each Point in Time. | Representative hours have indeed been selected for detailed network analyses (although 8760 h systematic contingency analysis could in some Regional Groups provide a first overview of the possible congestions). ENTSO-E and TSO's are continuing the development of the methodology and are looking ways to improve the methodology.
RSE |  |  | Pag. 91-92: Concerning the Regional Groups’ studies, RSE thinks that important efforts have been made in the TYNDP 2014 in order to properly model the power system functioning in different situations. However, even if each Regional Group points out its attention on particular aspects, a consistency of the approach among the Groups should be assured, in terms of simulations (AC vs. DC model, Monte Carlo application, stochastic, …) and in terms of how much Points in Time have to be analyzed - in order to be able to interpret the results as evenly as possible. | Regional groups use different tools, which have different properties that support the regional specificities. Also most interesting points in time for network studies vary between the regions because relevant issues may occur in different circumstances. E.g. in regions such as Nordics, hydrosituation plays a huge role and also the peak load situation appears in winter; and regions such as Greece and surroundings relatively sparse grid tries to integrate a large amount of renewables and the peak load appears during the summer. ENTSO-E has given the regional groups the freedom to select the most appropriate means to check the representative and stressing grid situations.
RSE |  |  | Concerning the Pan-European market studies, RSE believes that a probabilistic assessment, instead of a deterministic approach, can provide more details to the general result of the analysis that can be also exploited in the following steps by Regional Groups. Considering that one of the main driver for the development of the network is the RES integration, probabilistic approaches become more and more relevant. It should be clarified if Pan-European studies have been conducted by means of a probabilistic or a deterministic tool. | For the pan-European studies as well, several tools have been used, some being fully probabilistic (but with a lesser detailed modelling of the system dynamics) and other better modelling system dynamics (but for deterministic/average situations). Modelling always involve trade-offs, and confronting the outputs of several model relying on different bases strenghten the results.
RSE |  |  | Concerning the network studies, RSE thinks that a probabilistic approach in the analysis (e.g. probabilistic load flow in addition to the N-1 criterion) can provide useful information on the reliability of the network. In this context, the probabilistic analysis could also help achieving a better characterization of the indicator referring to the security of supply: in fact, if market based tools are useful to identify the ENS related to the adequacy of the generation system, the application on the detailed network studies by means of a probabilistic tool allows to properly consider adequacy aspects on the detailed transmission system and then to quantify in a wider way the effect of a project on the ENS reduction. This kind of approach should became essential in the future for complete and more sound analyses, therefore we recommend a more extensive use of this kind tools in cases where they are not exploited. | For network studies also, different approaches have been confronted, including probabilistic tools. (Probabilistic tools have however a limited ability to have a refined modelling of the various remedial actions that can be resorted to in order to solve or at least mitigate congestion.) Besides, ENTSO-E has recognised a need to further develop the CBA methodology especially concerning the SoS indicator; the potential of LOLE is however limited because scenarios assume generation is adequate to supply load and pan-European scale issues are explored and appraised.
RSE |  |  | RSE thinks that more details about the models adopted in the grid studies would increase the transparency of the analysis. For example they should specify if network studies consider a full AC model with voltage and reactive power investigation (additional benefits could be extracted from here). | The tools that are used during the assessment have been listed in the Regional reports. The tools TSO's normally use are using proper ac modeling with reactive power issues covered. Quick systematic diagnoses of potential congestion over the year may resort to DC approximation.
RSE |  |  | RSE thinks that it would be important to include in the pan-European market study also Turkey, that now operates in a synchronous way with the whole Continental Europe system ENTSO-E CE. | Regional Investment Plan Continental South East accounts for the connection with Turkey, with sensitivities regarding the flow to/from Turkey. The Turkish system itself has however not been analysed. ENTSO-E is investigating the future potential to widen the scope of the studies.
RSE |  |  | Results of the CBA reported as a range of variation do not provide enough information; if they are resulting from some sensitivity or probabilistic analysis, at least the mean value and possibly the standard deviation should be presented: moreover, different level of detail considered in different Regional Groups could not allow to interpret the results as evenly as possible. | Ranges of values basically translate the uncertainty about the end-results. This uncertainty is the direct consequence of uncertainties about input data and modelling limitations. ENTSO-E has tried to give stakeholders all the information available, with a simple, manageable standard format.
RSE |  |  | Together with the losses variation introduced by the project, an estimation of their monetization should be provided, as the change in network losses represents an energy amount that someone (usually consumers) has to pay or not. In fact, even if a neutral impact on transmission losses on Europe has been found in the TYNDP (see pag. 74) in energy terms, this is not true from an economic point of view, because the energy lost on transmission system can have different monetary values depending on the time and location (according to the system marginal price). RSE suggests to provide further details on this aspects. | The losses -indicator has been assessed via network studies and most regional groups have used selected points in time to represent the most appropriate situations. When the methodology develops and there is a possibility in all regions to study all hours, it will be possible to assess the hourly losses against the hourly marginal price from the market studies.
RSE |  |  | Together with the amount of the CO2 emission avoided and the additional RES integrated, indicators with their monetization should be presented, in order to give evidence of their monetary effect on the socio-economic welfare (that already includes the effect of CO2 emissions and RES generation). | THe monetization of these two indicators is included on the SEW indicator. It has been added a separate indicator fro RES and CO2 to give actual values how much MW's and tons the projects help to integrate or save.
RSE |  |  | RSE agrees with some of the results exposed in THINK Topic 10: o overall project costs should be disaggregated in the main cost components; o clustering rule should be based also on the net benefit, not only on GTC; o even if ranking is not an output coming from the ENTSO-E CBA, particular attention should be addressed in the application of the TOOT methodology on projects that could be put in competition. In this case, possible reduction in benefits could not be detected by means the TOOT approach. | Clustering rules were developed in the CBA methodology, so that the investments that are clustered together all help enhancing the same grid transfer capacity. Individual investments must also represent at least 20% of the total GTC increase. TOOT methodology assumes that the other projects are commissioned before the assessed project. Thus the result is rather the most modest of the possible benefits that the project bring. The methodology can be improved, but ENTSO-E believes it is presently both appropriate and simple to understand/check. (E.g. investments' contribtions to the total project benefits can reliably be assessed pro-rata the GTC contributions. And if clustering rules rely on a more complex than the GTC contributions... complaints about the transparency behind the clustering rules will arise.)
RSE |  |  | Whereas RSE welcomes the adoption of a more precise range presentation of the different factors of the cost-benefit methodology, thus abandoning the color-code representation, we still remark that an extra effort should be done for better characterizing some of the analysis elements, most notably resilience and flexibility, providing a better explanation of the criteria adopted for the quantification of the indicators. | The indicators are explained on the appendix 3. Cost and benefit methodology.
Birdlife Europe | This will be achieved with only a limited percentage of the proposed projects (<8%) crossing protected and urbanised areas. |  | We understand this headline figure is being recalculated, using databases that include EU-level and international designations. However formulated in this way, the statement is misleading. In fact 8% (or the new percentage as recalculated) of the kms cross these areas, not 8% of the projects. On p. 78 it says 40% of projects cross environmentally sensitive areas. | The indicator is indeed being recomputed with more complete sources, thanks to Birdlife's alert. The figures actually relate to the length. In this respect, the TYNDP report has been checked and the formulation looks ok, at 3 locations, with "8% of the total routes" (and not "8% of the projects").
Birdlife Europe | Projects of pan-European significance are hence key to making the European energy transition possible, with a positive impact on the environment and minimum residual effect. |  | This is subjective, and a justification of the plan rather than an assessment finding. It should say the projects have a 'positive long term impact for sustainable energy and climate change mitigation'. Direct, short term impacts on the environment remain negative, even if they are minimised. | The statement is indeed subjective but it invites the reader to appraise environment as a whole; and not only focus on local impact forgetting the European-wide impact.
Birdlife Europe | Vision 4 could be used only to assess the portfolio of already identified projects. Investigation of investment needs in this Vision requires additional input and feedback from stakeholders (notably, more precise location of generation) so that a more comprehensive picture of the grid infrastructure can be supplied. |  | Vision 4 is the only one where we are on track with climate and energy goals to 2050 and also planning for an integrated EU market (which is the role of ENTSO-E). So it seems the most important scenario - yet it is only used to check plans, not as a basis for planning. This is a major shortcoming - it is planning for failure - as Fig 0-4 shows. | The statement in the report tries to explain that the vision 4 includes a large amount of renewable production which location is not known. All this production when realised, will need to be connected to the grid and most probably some internal grid reinforcements will be needed. Due to the fact that the location inside the countries are not known it was not in all cases possible to assess the needed internal grid reinforcements. Figure 0-4 shows that the presented additional capacities might not be enough in all situations.
Birdlife Europe | The TYNDP thus paves the way for the implementation of the 2050 European energy goals. |  | It paves only part of the way to achieving 2030 goals (in fact these goals would be missed with these plans in place), so in effect paves the way to fail to implement 2050 goals. | By nature, the EU 2050 goals, more ambitious than the 2030 Visions, will require investments in addition to those presented in the TYNDP for 2030. Grid assets are long-lasting however, and ENTSO-E however ensures that the investments of pan-European significance are "no regret" solutions, i.e. that they will still be useful in 2050. In this respect, the TYNDP paves the way to 2050.
Birdlife Europe | 3.1 Consistency of the four Visions for 2030 |  | Visions 1 and 2 fail to meet EU goals for 2030. Vision 3 meets the goals but on the basis of national plans rather than EU market integration. Only Vision 4 meets agreed EU goals and complies with ENTSO-E’s function to develop the internal electricity market. Yet Vision 4 is not yet used as a basis for planning. Thus we can say the TYNDP is planning for failure. | EU 2030 goals were not set when Vision 1 and Vision 2 were designed; and with 40% of load covered with RES and 42% CO2 emissions mitigations compared to 1990, the two Visions are still compatible with EU goals. Besides, the present economic downturn and the political paradigm in Europe, where energy is a competence of Member States make Vision 1, 2 and 3 plausible scenarios, even if one may not like it; and this doesn't necessarily ruin Vision 4. ENTSO-E hence believes the TYNDP browse a realistic framework for the 2030 horizon.
Birdlife Europe | New hydropower capacities are also envisaged. The present capacity of 198 GW is expected to increase by 20% to 40% depending on the Visions. The three most promising areas are the Alps, the Iberian penisula, and Norway. |  | Hydro pumped storage can cause loss of rare and important habitats through the creation of lakes, and loss of ecologically rich streams and rivers. The EU needs a plan to deliver electricity storage with minimal ecological impacts. As planned currently there is not attempt to do this, and assessment of environmental impacts of TYNPD pump storage projects is particularly weak and uninformative. | The TYNDP does not judge components of the generation mix. Figures with respect to generation assets are merely considered as inputs to the analyses. Regarding storage assessment, ENTSO-E implements the CBA and acknoledges the methodology can be improved. S1 and S2 indicators must be re-defined for storage and the final release of the TYNDP will bear for storage projects "NA" (instead of "less than 15 km"; the latter does indeed not reflect the environmental impact of storage projects). Environmental impact of hydro-storage is however not ENTSO-E's expertise and support is needed in this respect.
Birdlife Europe | Main Bottleneck locations and typologies |  | It remains non-transparent how bottlenecks are identified. Despite the large amount of information contained in the TYNDP it remains impossible for an independent assessment to be made of the real need for any of the TYNDP projects. It is disappointing that when the TYNDP development process reaches important conclusions such as this it does not go on to recommend solving the problem. | Market studies identify how power exchanges tend to occur between market nodes/countries all year round. Network studies provide a more refined view (but for fewer hourly cases), simulating how power flows from generation unists to load centers with all grid elements available (N situation) or in case of one element failure (N-1). In these simulations, the power flows are not limited by assets capacities and overflow can occur. A bottleneck is identified where the power flow violates the capacity of the grid elements and the result can be displayed as grid sections, accross which either investment is required or congestion will be experienced. And the TYNDP suggests what investments are required.
Birdlife Europe | The set of projects of pan-European significance is still to be completed in order to meet the energy revolution proposed in Vision 4; with its validation first in October 2013, Vision 4 could only be used to assess the portfolio of already identified projects. Investment needs investigation in this Vision requires additional input and feedback from stakeholders (more precise locations of generation especially) so that a more comprehensive picture of the grid infrastructure can be supplied. |  | Given meeting Europe’s targets requires more knowledge on the locations of generation, does ENTSO-E therefore support EU-wide strategic spatial planning of generation capacity, in order that necessary grid capacity can be assessed? | The TYNDP shows, at pan-European level, where adding new generation may cause congestion. Unfortunately, options for locating generation are limited by a whole range of constraints (primary energy source access, land use, etc.) and grid investments often prove more flexible, with lesser (although high) costs compared to another optimisation of the generation mix and its location.
Birdlife Europe | In Vision 1 however, coal fired units are relatively cheap, and about 36% of the projects actually help these cheap but high in CO2-emissions power plants to find new outlets. The same applies in Vision 2. |  | Visions 1 and 2 are significant failures for an environmentally sustainable energy supply in Europe. Does ENTSO-E therefore support a high CO2 price to avoid building power lines that result in failure? If you are working with scenarios that represent failure, and can see which projects contribute to that failure, then you should identify how to make the plan as a whole a success. Proposals on that would be a useful subject for consultation. | Complementing the above answer, Vision 1 and 2 may sound less appealing than Vision 3 or 4, but they sound plausible to other stakeholders and hence deserve investigation. Vision 1 and 2 are consistent with low CO2 prices or in other words still available and affordable fossil fuels which by nature are questionnable on the long run. Especially with the perspective proposed in the comment, ENTSO-E believes the TYNDP to be a success as projects of pan-European significance are "no regret" solution on the path to increased RES and decarbonation.
Birdlife Europe | The indicators 'protected areas' (S1) and 'urbanised areas' (S2) are used to show: - where potential impacts have not yet been internalised i.e. where additional expenditures may be necessary to avoid, mitigate and/or compensate for impacts but where these cannot yet be estimated with enough accuracy for the costs to be included in indicator C.1. - the residual social and environmental effects of projects, i.e. effects which may not be fully mitigated in final project design and cannot be objectively monetised. The two indicators replace the former “social and environmental indicator” from the TYNDP 2012. |  | In principle, this is a significant improvement on the heavily criticized ‘social and environmental’ indicator used in 2012. However the approach used in the draft does not match the proposal made in Annex 7 (see criticisms below). With just a number of kilometers the indicator is not comprehensible. For the indicator to be informative it either needs to be supported by a detailed map, or as a minimum the names of any protected areas must be provided and a link for further information (as suggested in Annex 7). | ENTSO-E tried to improve the indicator with stakeholder support and input. However, the information in the TYNDP is necessarily synthetic, with the provided indicators and a map for every project. The more detailed information is to be found in national development plans or in the more detailed studies accompanying every project. The latter information is simply too large to be managed in the TYNDP.
Birdlife Europe | In order to provide a meaningful yet simple and quantifiable measure for these impacts, these indicators give an estimate of the length (number of kilometres) of a new line that might have to be located in an area that is sensitive due to its nature or biodiversity (“protected areas”), or that is densely populated (“urbanised areas”). |  | ‘Sensitive due to its nature or biodiversity’ is the objective. However in the draft TYNDP the European Common Database of Designated Areas has been used so only national designations have been considered. Moreover this includes many areas with scenic or recreation value, but little ‘nature or biodiversity’ value. It excludes most areas identified on an objective basis to be the most important for Europe’s biodiversity i.e. Special Areas of Conservation and Special Protection Areas for birds (together, the Natura 2000 network and Ramsar sites). We understand this error is already being addressed in revisions to the TYNDP2014. | Indeed, the mistake is corrected in the final release of the TYNDP, thanks to Birdlife's alert.
Birdlife Europe | It is often difficult in the early stages of a project to assess its social and environmental consequences, since precise routing decisions are taken later. The quantification on these indicators is hence presented in the form of a range. For the same reason, projects under consideration or for which paths are not defined are not assessed; they are to be scored only in a successive version of the TYNDP when further studies have been done. |  | Simply looking at start and end points and a reasonable ellipse that would include reasonable routes can give an early indication. This is better than saying nothing. | Some of the project needs are more than several hundred km apart. It has been recognised that there is a transmission need, but for some of the projects even the end points and the technology is still not decided. ENTSO-E has given all information that they have for the more precise projects. While projects are more mature, more information on the effecs can be analysed.
Birdlife Europe | The two indicators have been calculated based on input from TSOs regarding the routing of projects and on data from the European Environment Agency (the Common Database for Designated Areas and Corine Land Cover Urban Morphological Zones). |  | As mentioned above and in earlier discussions with ENTSO-E, the CDDA is a database of nationally designated sites, excluding Natura 2000 areas that have been designated in addition to nationally recognised sites.This is not the appropriate data set. It has a smaller coverage area and it includes landscape designations. The differences between national and European designated areas can be seen easily in the Natura 2000 Viewer here: http://natura2000.eea.europa.eu/ | As mentioned in the comment above, this mistake is corrected in the final release of the TYNDP. Due to the lack of a sole comprehensive reference, this was achieved by checking serveral databases and merging the information extracted to compute the indicator.
Birdlife Europe | The statistics show that less than 20% (resp. less than 40%) of the projects of pan-European significance cross particularly densely populated (resp. environmentally sensitive) areas over more than 15 km. Globally, the TYNDP projects cross urbanised (resp. protected) areas for less than 2000 km (resp. 4000 km), i.e. over less than 4% (resp. 8%) of the total routes (about 46000 km); TSOs optimise the routes so as to avoid such interferences as much as possible. |  | The majority of projects are categorized as “negligible or less than 15 km” and are not presented separately from projects with no assumed impact. Also small projects cross sensitive areas: especially crossing of alignments like rivers are often of short distance but may have a very significant impact on birds. For this reason the underlying maps used to arrive at the figures should be provided, or as a minimum the names of protected areas affected should be provided. | Complementing the above answer, ENTSO-E believes it may have sounded provocative to tag projects "with negligible impact" only. A "small" project at the European scale, has a big impact at every square meter of land it uses. The TYNDP peform a standard assessment for more than 100 projects, giving the keys to, but no exhausting, all issues about every single one of them, neither on technical, nor economic nor environmental aspects. Additional documentation to the TYNDP must be resorted to.
Birdlife Europe | Environmental assessment |  | There is a difference between meaningful and purposeful environmental assessment versus setting out to demonstrate that a plan is environmentally acceptable or positive. Here it is the latter. To be a valuable exercise in terms of improving the plan, there should be an effort to find alternatives for the most environmentally-problematic projects. This would give the consultation real purpose: developers, authorities and stakeholders could advise on the potential to mitigate or avoid risks associated with specific projects. In another example, the assessment has found that under certain scenarios a large number of projects serve to undermine European climate goals. For this to be a useful assessment, that finding should then be used as the basis for changes to the plan, or proposals for other policy changes, to ensure European goals are met. | While projects mature, there is a Environmental impact assessment performed for each indivual project where deeper analysis is done and also several routes are assessed. Some of the projects in TYNDP are not mature enough that the EIA had been performed, nor the route selected. A formal Environmental assessment of the TYNDP would require the assumptions behind the plan to be less uncertain, and a consensus about the environmental impact of the energy policies in Europe.
Birdlife Europe | 10.3 The energy transition requires the grid, the grid requires everyone’s support |  | This is correct, and is a central rationale for the work of the Renewables Grid Initiative, of which BirdLife Europe is an active member. However getting public support is not about justification and more ‘acceptance’. It is about reducing impacts (and being seen to do so) i.e. improving ‘acceptability’, and developing meaningful dialogue and understanding based on openness and transparency. | ENTSO-E totally agrees, and has strived to make it possible to have this dialogue and raise understanding of the need not only to renew the production system, but that it means also changes in the main grid.
Birdlife Europe | Further analyses are however required to ensure the measure can be successfully implemented, in particular in relation to whether the timelines proposed are achievable, especially in the context of the public participation process and the potential for legal delays. |  | Is this a suggestion that there are too many opportunities for public participation and access to justice? This seems a very outdated and counter-productive position. The PCI legislation recognizes the risks of cutting corners with environmental protection, transparency and so on, and introduces additional consultation requirements and guidance to try to balance out those risks. The success of the PCI approach in reducing delays has yet to be seen. It may depend on how well provisions on environmental protection and stakeholder rights are implemented. | ENTSO-E welcomes the PCI-legislation but simultaneously notes that there are challenges on reducing delays. ENTSO-E finds it of utmost importance that proper stakeholder interaction is ensured on the process, advocating and transparently debating projects is the best way to success. Challenges are likely inconsistencies and less transparency in the authorisation process when it becomes more bureaucratic, with diluted responsibilities.
Birdlife Europe | 1.3 Storage projects |  | Assessment of storage projects using the same S1 indicator as for power lines is not informative. For example project 222 (pumped storage at Kaunertal in Austria) is given an S1 indicator ‘Negligible or less than 15 km’. Kaunertal is highly controversial as it threatens to destroy two ecologically rich rivers in the Austrian Alps. Measuring in hectares was necessary for effected environment by pumped storage sites. A way to meaningfully capture and communicate biodiversity impacts of pumped storage projects is needed. This should then be used as a basis to plan for Europe’s storage needs in a rational way. | ENTSO-E has already recognized the need to develop CBA methodology especially regarding storage projects. The computation of the S1 indicator for storage projects is indeed meaningless. On the other hand, it is also true that the methodology does not capture all potentially positive benefits of the storage projects. Regarding the assessment of the specific project HPS Kaunertal, this value was inserted by mistake and will be removed in the final version as there was no assessment of this indicator.
Birdlife Europe | the new methodology improves on this indicator by giving an estimate of the number of kilometers of a new overhead line (OHL), underground cable (UGC) or submarine cable (SMC) that might have to be located in an area that is sensitive for its nature or biodiversity (environmental impact), or its landscape or social value (social impact) |  | The data sets used in fact include landscape value under ‘environmental’ rather than ‘social’. | S1 "Protected areas" and S2 "urbanised areas" have been computed based on two distincts set of inputs indeed.
Birdlife Europe | These indicators will be presented in the TYNDP along with the other indicators as specified in ENTSO-E's CBA methodology, with a link to further information. |  | This link for further information (which should be a link to a national SEA report covering the project in question, or similar) has not been provided. It is important to provide this information, particularly if maps cannot be provided. | A map locating the project is supplied in every assessment sheet. Adding a layer with urbanised and protected areas was in practice not manageable in 2014. We wan improve in this respect for the next release of the TYNDP. Links to full SEA must be first collected by ENTSO-E before we can provide them.
Birdlife Europe | Considering that translating the project score to a colour code would make the indicator appear to be simpler and more objective than it actually is, and would undermine its main intention, which is to provide full information to decision makers and the public… |  | This is a good intention. However the information provided falls very far short of this. What is given for each project for S1 is limited to one of the following: 1. No information: where a project is at an early planning stage. 2. Negligible or 0-15 km. No information given on which or what kind of protected area might be affected. No map provided. Europe’s most important areas for biodiversity not considered. 3. 15-50 km 4. 50-100 km 5. More than 100 km This is not sufficiently informative to serve the intended purpose. It is important that the indicator should enable readers to form a view about the likely environmental challenges a project may face. This will help with planning and consideration of mitigation measures or alternatives. The additional information intended for provision in Annex 7 includes the typology of sensitivity, the name of protected areas that could be affected, and a link to a web site for interested parties to find further information. It is vital that this information should be provided for the indicator to serve its intended purpose. | ENTSO-E acknowledge that the provided information resulting from the implementation of the CBA can be complemented. More accurate information require more resources than those available for the TYNDP 2014. Improvement can be foreseen in the future in this respect, but there will always be trade-offs between the accuracy/level of detail and the available resources.
Birdlife Europe | Example (in the table): Typology of sensitivity: a. Birds Directive; b. Habitats Directive Link to further information Big Hill SPA |  | See note above. | (see answer above)
Birdlife Europe | - Sensitivity regarding biodiversity: o Land protected under the following Directives or International Laws: -Habitats Directive (92/43) -Birds Directive (2009/147) -RAMSAR site -IUCN key biodiversity areas -Other areas protected by national law -Land within national parks and areas of outstanding natural beauty - Land with cultural significance |  | The social impact indicator is also not implemented as described. It is intended to includes landscape designation, which are in fact included in S1. | The implementation of both S1 and S2 may be improved for the TYNDP 2016, in a comment to every project, designating most significant areas.
Birdlife Europe | Biodiversity... Removal/ damage to natural and semi natural habitats Disturbance of breeding and resting birds Collision with birds... Routing to avoid Natura 2000 sites and sites of high nature value |  | The TYNDP is a European plan so should serve agreed European goals. Avoiding Natura 2000 sites is indeed good practice, and a legal requirement. The TYNDP should help application of this good practice by flagging up to developers and regulators where such avoidance may be necessary. This Appendix should indicate some other important mitigation measures: 1. Undergrounding cables in particularly sensitive areas 2. Timing construction to avoid sensitive periods (nesting season). 3. Removal of inactive power lines | The text is completed in the TYNDP as follow: "*" . Item 2 is already covered ("Limit activities during breeding season"). And power lines are removed when obsolete, except if to be soon reused in a new scheme.
DII, E3G, Estela, Europacable, German Watch, Medgrid, RCREEE, RES MED, Abengoa, ACS, |  |  | However, as we point out below, it misses out the opportunity to consider more closely the great renewable resources of the MENA region and sends a discouraging signal towards the countries of that region as it neither does foresee concrete interconnection projects with North Africa, nor does it consider its attractive renewable resources. Dii would like to contribute to the further development of the TYNDP plan(s) and has the following comments on the TYNDP 2014, recognising that this plan is a draft version. Solar radiation as well as average wind speed is in many areas of the MENA (Middle East and North Africa) region significantly higher than in Europe. Additionally, land for the utilization of wind and solar energy is abundantly available thanks to a low population density. Hence, a relevant share of renewables could not only be installed to cover the rapidly growing local and regional demand in MENA but in a mid and long term perspective also for electricity exchange to meet the European renewables and climate targets in the most efficient way. In such an economically optimized, renewables based electricity system MENA and EU countries will need to be strongly interconnected to make use of balancing effects from different demand and generation profiles mainly from wind power. | The TYNDP scenarios have been developped in cooperation with all interested stakeholders but no supporter or expert encouraged ENTSO-E to develop the scenarios in this respect. The perspectives for a the developement of interconnection with North Africa mentioned in the TYNDP 2012 experienced downturns in the last 2 years but they are still being investigated. Dii is welcomed to join the LTND SG and contribute actively to complement the scenarios for the TYNDP 2016.
DII, E3G, Estela, Europacable, German Watch, Medgrid, RCREEE, RES MED, Abengoa, ACS, |  |  | The TYNDP 2012 made a first step forward towards realizing this vision and considered two projects that connect Europe and North Africa (Algeria-Italy, Tunisia-Italy, NTC 1.5GW) as projects of pan-European relevance to be executed by 2022. The draft TYNDP 2014, however, takes two steps back and only foresees a single interconnection (NTC 0.6GW), without specifying its connection points and to be realized only by 2030. Dii not only considers this as a lost opportunity from a European point of view, but also as a discouraging signal towards the North African countries who are heavily engaged in projects aiming at power market reform and regional system integration, such as MedReg, MedTSO or IMME, with the aim to integrate into the European market in the mid-term.[2] Dii recommends to, at least, consider the two projects named in the TYNDP 2012 also in the new TNYDP 2014 with an execution date latest 10 years from today on. While the TYNDP 2014 does not promote specific trans-Mediterranean interconnection projects, it also fails to integrate the MENA region in its vision for 2030, e.g. identification of strategic transmission corridors at a pan-European level to consider possible developments beyond 2020. We would therefore highly recommend including the option of a geographical expansion of today’s grid infrastructure to European neighbouring countries in the Mediterranean Sea (Turkey and MENA) even in the TYNDP and (probably) not only in the e-Highways Study 2050. | Under the framework of TSOs’ cooperation several options of new connections between Europe and North Africa have been studied. The two projects reported as "under consideration" in the TYNDP 2012, although proposed by TSOs, were basically depending on specific generation project developments in North Africa that seem now, due to changes in the envisaged scenarios, not mature enough to allow them to be considered in TYNDP 2014. Nevertheless, those (or eventually other further projects), could be considered in the next TYNDP 2016, whose preparation is now starting, if their maturity could be achieved.”
Eurelectric |  |  | EURELECTRIC welcomes the publication of the draft ENTSO-E Ten Year Network Development Plan (TYNDP) 2014 and the vast efforts put by ENTSO-E into elaborating the planning process and involving stakeholders. | -
Eurelectric |  |  | One of the main challenges is how to avoid that the TYNDP reads like a ‘wish list’ of projects, with a follow-up report that takes stock of the small number of lines actually built. According to Regulation 713/2009, ACER is obliged to monitor the progress in implementing crossborder and TYNDP investments. A reference to ACER findings in an assessment from ENTSOE’s perspective on the reasons for delays, obstacles, financial issues could be useful. The next TYNDP could provide a more thorough assessment of the previous one than is currently the case, and the reasons for large-scale non-implementation, as well as the necessary remedial actions (e.g. get policy support and regulatory support). The paper should also mention issues such as the current concern with security of supply that reverted the order of the PCIs and their impact on the grid roll-out/upgrade. | ENTSO-E stressed the reasons for delayed projects in the report. Regulation 347/2013 is a regulatory measure intending to support PCIs. However, stakeholders pleading for transmission projects in a local public debate with neighbouring population and authorities, would be more convincing than TSOs, and this is the most powerful measure to ensure timely implementation of the projects.
Eurelectric |  |  | The scenarios do not fully reflect macroeconomic consequences of the current trends. Generation capacity assumptions seem to be partly based on official plans that are often the only available indicator for TSOs to consider national capacities. However, those often do not realistically reflect the commercial profitability and feasibility for existing plants and new investments. | The scenarios have been prepared jointly with stakeholders during more than 2 years, in the long term network stakeholders group, in workshops and consulted upon. Visions 1 and 3 reflect national energy policy and there consistency at European level is indeed questionnable. Vision 2 and 4 have been built in order to provide a more consistent picture. In this respect, Eurelectric timely, valuable input is welcome for the next TYNDP 2016.
Eurelectric |  |  | The CBA methodology can be improved: the current one does not seem to provide a full estimation of costs & benefits and the transparency of selection criteria for projects is hampered by clustering of projects. Projects need to be comparable to allow for prioritisation. The TYNDP should provide disaggregated information on each investment item and include single investment grid transfer capacity increases, as proposed by ACER1. In addition, the evaluation and comparison of alternatives based on different technologies should be encouraged to increase economic efficiency. For example, most renewables are being connected to distribution networks, which also require smart network investments. The TYNDP should propose alternative solutions for specific problems in order to better evaluate the suitability of any proposal. | The CBA methodology has been developped jointly with stakeholders during more than 2 years, in the long term network stakeholders group, in workshops and consulted upon. Clustering rules have been defined following EC and ACER guidance, and disagregated information is supplied for every investment. It can certainly be improved and inputs from Eurelectric are welcome.
Eurelectric |  |  | The value of transmission development can hardly be underestimated. Thus, underinvestment is actually more ‘expensive’ than ‘overinvestment’: the energy transition has to build on infrastructure. The value of a strong transmission and indeed also distribution grid that leads to cost efficiency in all the studied scenarios should be made visible to policy and decision makers. In other case there is a risk that the significant potential of the new energy system is locked in behind grid bottlenecks- and that flexibility in regions cannot be provided. However, grids are not without alternative when it comes to providing flexibility: EURELECTRIC would thus like to see an introductory reference to technology neutrality in a broader sense, embracing interconnection, storage, demand response, and energy efficiency as alternative answers to generation adequacy concerns. | The basic equation is generation matching load; or with DSR, load matching available generation. Storage adds an additional freedom degree in the equation. If all elements in the equation are at the same place, no transmission is required at all. Only because they are not at the same location, does interconnection matter, as as a means to solve the generation adequacy equation.
Eurelectric |  |  | Stakeholder representation and regional coherence There seems to be differences in presentation forms for the ‘master plan’ and the different regional plans and seemingly in some of the methodologies used. In the future, this could be improved even though it should be recognized that there are differences between regions that might necessitate different approaches. EURELECTRIC welcomes the establishment of the long-term development stakeholders’ group and believes that the communication steps proposed by this group (on how to bring clarity at the beginning and information and feed back at the end of the drafting process) would further improve the process. The strengthening of future groups to represent all interests of all market parties is a step in the right direction. It is not possible for European associations to verify and validate input data used or the given calculation outputs due to the regional differences and the sheer amount of data for the whole of Europe. EURELECTRIC thus believes that a way forward here is further strengthening second level of stakeholder involvement at the regional level, i.e. regional consultation processes per regional investment plan. EURELECTRIC is ready to make its members aware of these regional workshops. Some sort of validation process introduced by e.g. NRAs on the final regional plans and ACER on the ‘master plan’ would strengthen the validity and acceptance of those plans. | ENTSO-E welcomes the proposal to improve stakeholders' involvement,especially regarding scenario building. Practical implementation can be discussed in the Long Term Network Development Stakeholders' group.
Eurelectric |  |  | Cost allocation Besides the CBA methodology, the subsequent possibility to conduct a cross-border cost allocation is the key enabler for the development of a European grid infrastructure. We encourage that more attention is devoted to the model for cross border cost allocation, so that the goal of reaching a cross border cost allocation is not further stalled. Thus TYNDP should include a note on the principle "beneficiary pays" with respect to regional distribution of the costs of cross border transmission. | The TYNDP aims at determining where investments are required in Europe and this evaluation considers the overall European welfare as a whole. CBCA issues comes next. They are however adressed in further, project specific and complex analyses. The TYNDP is a demanding exercise already, that cannot address efficienty CBCA issues additionnally.
Eurelectric |  |  | Main bottleneck locations and typology The section on bottleneck locations and typology should be more detailed. The bottlenecks are the fundamental issue that is being addressed by the TYNDP, and EURELECTRIC encourages the TYNDP to portray a detailed description of individual key bottlenecks and furthermore be much more specific in the report in regards to assessing to what extent the suggested TYNDP investments will mitigate the given bottlenecks and on which timescale. This way a much needed transparency on the individual key bottlenecks is secured and ACER and the NRAs have a better understanding of which bottlenecks are addressed to what extent on which time scale, leaving the NRAs a better basis for assessing when further action in form of changing the congestion management regime is needed. | The TYNDP is trade off between a synthetic overview and detailed information. Bottlenecks are located on boundaries; and the analysis of the bulk power flows through the boundaries compared to the boundary capacity enable a characterisation (frequency, magnitude) of the bottleneck. Mostly, such results are displayed in the Regional Investment Plans as monotonous (or not) hourly load curve (see for instance Regional Investment Plan Baltic Sea, § 4.5)
Eurelectric |  |  | Financing of the projects As the planned infrastructure will require major investments, a section on the how these investments are to be financed would add value. For example, the principles of cost allocation between customers (producers, industry consumers and household consumers) should be clarified. The plans do not specify which factor (SoS, RES, increased consumption etc.) would be the prime reason for each of the suggested investments. These are major issues in order to understand the need for the investments and get public acceptance. | The financing of projects is addressed in § 5.4. The CBA assessment of projects considers their social welfare for the whole European community. The cost allocation between customers is a matter of tariff structure, to be decided by NRAs.
Eurelectric |  |  | About 100 major investment needs A clarification of wording is needed in the executive summary about the TYNP approach. It says that “Through the construction of the scenarios, the four Visions assume that generation is sufficient to balance load in all countries, i.e. addressing at a macroscopic level, security of supply concerns”. It can be understood as a building of generation capacity in each country to balance the loads. Our understanding based on the complete report is that generation capacity has been built in all countries based on an estimated European demand, relying on sufficient interconnection support between all countries. This could be rephrased as “to balance load in Europe for all countries, based on sufficient interconnection support”. | Indeed, the implicit assumption behind the sentence it that scenarios are built assuming there is sufficient interconnection support. Then the TYNDP checks whether this is true and propose investments where gaps are identified.
Eurelectric |  |  | Third party projects Third party projects are included in the TYNDP for the first time. This constitutes an important step forward. EURELECTRIC welcomes this and looks forward to the further development of the procedures for inclusion of 3rd party projects as well as coordination regarding future procedures regarding infrastructural requirements and for operational issues (such as ancillary services) for enabling of cross border activities (of TSOs and market participants) for the provision of an adequate level of security of supply. Also the coordination regarding grid architecture and the inclusion of areas with huge storage potential might be optimised more efficiently | The process to associate third party projects was already opened for the TYNDP 2012, but candidates failed to meet the criteria to enter the TYNDP list.
Eurelectric |  |  | Reference to edge technologies and innovation It is very positive that the report provides a part on edge technologies (p. 95-96). But it would be also useful to refer to edge technologies and innovation in other parts of the electricity value chain beyond transmission as they also have an impact on the grids and need for grid. | There are a lot to say about the whole electricity value chain, but the TYNDP focuses on transmission and the corresponding part is developped in this respect.
Eurelectric |  |  | Four main electric peninsulas remain the same – which highlights the lack of progress. The regional concerns for interconnection in Europe have remained unchanged in the last ten years: as before the lack of interconnection of the Iberian Peninsula as well as of the Baltic region is preoccupying and further action has to be taken here. Indeed, the DC interconnection of the Baltics with the Nordic countries have progressed considerably which is to be welcomed. Yet, the Baltic interconnection with Central Europe remains negligible and Baltic internal reinforcements are still only under construction or planning. The Iberian Peninsula, central in RES capacities, sees in 2014 the opening of the Pyrenean underground interconnector. But the capacity provided is still insufficient. It is thus necessary that additional capacities are set up but, as in any other cases, in a cost-efficient way. Other insufficiently interconnected areas are the UK/Ireland as well as Italy, as the TYNDP rightly highlights (p.7 executive summary), referring to the ‘four main electric peninsulas’ in Europe. | The four 'electric peninsulas' were highlighted in the TYNDP 2012 and are still highlighted in the TYNDP 2014 as they represent real challenges by 2030. As mentioned in the report, new projects will be needed so new planning studies will continue in the framework of the TYNDP2016 framework.
Eurelectric |  |  | Also future power balance of imports and exports of Germany based on generation adequacy needs to be analyzed further. How credible is it that Germany will import in the future scenarios? Why is the load factor for wind so low in the TYNDP? The power balance in Germany should reasonably be revenues of only wind and solar power on many occasions and thus give rise to large export flows to the surrounding countries. But EURELECTRIC does not see this portrayed in the model calculations. | Assumptions for Germany as well as for other countries have been validated through the public preparation and consultation process, including load factor for wind generation. In the models, Germany exports a lot when wind and sun are available, but on average appears to be importing. In vision 3 and 4, fuel and CO2 prices assumptions make German coal fired power plant rather expensive.
Eurelectric |  |  | Regarding EU climate targets, the TYNDP shows clearly that interconnections between Nordic countries and Continental Europe are of significant importance, both regarding the facilitation of RES and reduction of CO2 emissions. In our view, regulatory steps should be taken in order to better facilitate and secure the realization of important investments in the future planning of the European power system. | -
Eurelectric |  |  | Last but not least, some information about transfer capacities between countries are provided in the TYNDP 2014. However, this information is not sufficient and does not provide a comprehensive view on the evolution of the net transfer capacities. The evolution of the net transfer capacities (even if subjects to caveats) year after year, considering the proposed project portfolio, must be made available to the stakeholders of the European transmission system. | Resources constraints compelled ENTSO-E to limit the investigations, and stakeholders feedback put priority on 4 visions at longer horizon, rather than exploring a second, intermediate horizon. TYNDP 2016 will provide a more complete picture in this respect.
Eurelectric |  |  | Broad EU wide political support is urgently needed - one stop shop and time limits in Infrastructure package are positive first steps. The TYNDP highlights that interconnection capacity will have to double on average throughout Europe (depending on the scenario used) and pinpoints about 100 major investment projects that are needed in order to remove existing or to prevent foreseen bottlenecks. According to the report, only 10% of the TYNDP 2012 investments have been completed throughout Europe. This has already been observed in previous TYNDPs and can’t be accepted as it has become a trend (“More than one third of the investments are delayed compared to the initial schedule, mostly because of social resistance and longer than initially expected permitting procedures.”). The implementation of Regulation 347 that should hopefully contribute to the improvement of this situation for the so called Projects of Common Interest is thus crucial. In addition, responsible national authorities should take further actions for supporting grid development – the transparent European TYNDP process should be used to increase acceptance. The TYNDP activities are contributing to mitigate public resistance through the promotion of a reasonable coordination of the development of the national projects as a part of our European infrastructures. Delays with respect to the implementation of transmission investments are a key-issue. It is important that ENTSO-E, ACER and stakeholders develop in common develop the necessary regulatory framework that will accelerate procedures for important projects. PCIs and the infrastructure communication are a significant first step. | ENTSO-E welcome any support to ensure a timely implementation of transmission grid projects.
Eurelectric |  |  | Infrastructure and RES development are interdependent. National climate and energy objectives could be endangered if there is not an integration of generation through sufficiently interconnected markets. Lack of sufficient interconnection capacity could be seen by stakeholders and project promoters as a barrier to the development of RES at national level. Some Member States could be reluctant to fulfil their commitments arguing that the economic burden for consumers could be unacceptable if there is not an integration of markets due to insufficient interconnection. | This comment supports the key message of the TYNDP.
Eurelectric |  |  | Furthermore, not each proposal in the TYNDP should be adopted, even if it satisfies the solution of a specific problem, since the costs will be passed on to customers. Cost efficiency must remain a prime target, including in the roll out of infrastructure. | Every CBA project assessment sheet is available to demonstrate the project costs and benefits and support the decision to build the project.
EWEA |  |  | EWEA welcomes the numerous improvements in this second ENTSO-E 10-year network development plan (TYNDP) in comparison with the TYNDP in 2012. Specifically: • Enlarging the forecast horizon of the TYNDP beyond the 10 year scope through to 2030, as a bridge between the European energy objectives for 2020 and 2050. • Improving stakeholder involvement through the creation of the Long-Term Network Development Stakeholder Group. • Quantification of every project’s benefit according to a (preliminary) Cost-benefit analysis (CBA) as foreseen by EU Regulation 347/2013. • Application of new clustering rules in line with EU Regulation 347/2013 to define projects of pan-European significance, focusing on the core investment items rather than on a plethora of minor assets. • Constant improvements and an open consultation cycle with regards to the Scenario outlook and adequacy forecast 2014-2030 (SOAF) and its accompanying target methodology for adequacy assessment. | -
EWEA |  |  | 1. Improvements of the four 2030 Visions according to the principles of plausibility and EU energy policy objectives ENTSO-E’s intention to move away from a bottom up methodology to adopt a truly European approach for grid planning and also wider and more transparent stakeholder involvement through dedicated feedback groups is understandable. However, the important concerns expressed in December 2012 and September 2013 through a joint stakeholder letter and our response to the public consultation on the 2030 visions draft have not been fully addressed. In particular the plausibility of the top-down visions and lack of an EU-wide approach on RES integration . | ENTSO-E is aware that its approach for the top down visions in TYNDP 2014 does not fully reflect a European RES optimization. As also expressed by the stakeholders - see the stakeholders paper- Recommendations on scenario building and stakeholder involvement in the TYNDP process - this is a process very hard to achieve and more active contribution from stakeholders is required to complement ENTSO-E's expertise. For the TYNDP 2016 ENTSO-E already started to seek futher stakeholder input for this task - see the material from the stakeholders' workshop on scenario developement 16 September.
EWEA |  |  | • Missing insight in ENTSO-E’s market and network modelling results. To properly assess ENTSO-E’s market and network modelling results, ENTSO-E should provide figures on electricity generated per technology including capacity factors assumed for RES and the assumed running hours for conventional generation. | The market studies run at the European and regional level are based on the hourly resolution. This information represents trillions of values and is very hard to deliver and display conveniently. However, ENTSO-E will seek to increase the data published in the TYNDP. Resulting load factors per technology are not focused on in the TYNDP report in consultation : only annual generation in TWh and installed capacity per technology, from which load factors can be appraised are displayed. ENTSO-E will however publish the source information for every pan-European market study in an XLS file along with the final version of the report.
EWEA |  |  | • Differentiate levels of fossil and nuclear power generation rather than assuming unchanged amounts of conventional power capacity throughout all four visions. It remains inconceivable that fossil and nuclear power generation capacities are maintained roughly at the same level throughout all four ENTSO-E visions. There is only a 25 GW difference between vision 1 and 4 in installed thermal capacity. | Installed generation capaciy does not entail generated power for fossil fuel units, which are the highest the merit order. Hence in Visions with higher RES penetration, load factors for fossil fuel units are reduced, entailing that their profitability is questionnable; and if profitability is not ensured, capacities will be shutdown, at least mothballed. In this respect, Vision 1 and 3 are built bottom-up with capacities as planned in every country; Vision 2 and 4 fossil-fuel based installed capacities have been optimised in this respect, according to the shared methodology, but this optimisation can be further improved.
EWEA |  |  | • Base the 2030 Visions on realistic electricity demand figures. Demand projections soar in the ENTSO-E’s “Green” visions 3 and 4: By 2030 a power consumption of 4,200 TWh is forecast, which is considerably higher than comparable 2030 demand projections by the European Commission and the IEA (between 3,000 TWh and 3,250 TWh in the EC roadmap decarbonisation scenarios and between 3,613 TWh and 3,960 TWh according to the IEA). | Although the energy efficiency is higher in the top down visions, electrical vehicles, heat pumps and other shift of end-uses from fossil fuel to electricity lead to an overall significant demand increase. The figures have been shared and consulted upon. And lastly, in the workshop ENTSO-E held on 16 September 2014 on scenario development (for TYNDP 2016) a significnat number of stakeholders considered that demand for Visions 3 and 4... shall increase.
EWEA |  |  | • Base all visions on plausible assumptions on CO2 prices, demand and technology roll-outs. The four different ENTSO-E visions select and combine different assumptions on technology roll-out for CCS, storage and new nuclear plants in a seemingly arbitrary manner. For example, in one vision large shares of RES are grouped with a high public acceptance of nuclear power and full commercial roll-out of CCS. | Vision 3 is bottom up and reflect actual energy policies of Member States, some advocating both nuclear energy and RES.
EWEA |  |  | • Develop a truly optimised RES development scenario in vision 4 “Green revolution”. To obtain meaningful results in the top-down scenarios, choices of key parameters that evidently undervalue the socio-economic potential of high shares of RES deployment must be ruled out: in particular, combining inflexible generation, large shares of RES and no or little levels of energy efficiency. In this context, we welcome that the final validation of Vision 4 should only take place in October 2014 and will give ENTSO-E further time to work on this vision. | Vision 4 indeed assumes large amount of RES, energy efficiency and thermal generation to be flexible (which entails the corresponding high investments on existing units are implemented).
EWEA |  |  | 2. Clarification of main drivers of grid development until 2030 The present TYNDP states that most of the envisaged grid reinforcements are, indeed, due to renewables without further contextualisation and seemingly contrary to other statements in the TYNDP document. For instance, on page 80 it reads: “Approximately 80% of the TYNDP 2014 projects contribute to RES integration, thus reducing CO2 emissions in Europe”. In contrast, pages 58-59 describe that market integration aspects prevail over generation connection and security of supply as 60% of the boundaries/grid sections are primarily related to this. EWEA, therefore, urges ENTSO-E to clarify this and use consistent wording: not accrue 80% of all grid bottlenecks and related projects to RES, but give a more refined picture outlining the synergy effects between RES, market integration and security of supply of grid reinforcements. This would help avoid misconceptions around the relation between achieving EU energy policy goals of RES integration, the creation of an internal energy market and security of supply with regards to the projects included in the TYNDP. | The two statements support each other: future market integration IS the transportation of RES energy surpluses to areas with generation deficit. The 80% covers both direct RES generation connection AND market integration required by RES; whereas p58-59, direct RES connection is isolated (and market integration, by nature mixing several uses, is the default option on the map). In other words: without RES developement, market integration would be basically achieved in Europe, except for the electric peninsulas.
EWEA |  |  | 3. More thorough elaboration of definition of costs and benefits estimates and their determination As in the previous version, this TYNDP draft makes important statements on cost savings through a better use of the power generation fleet enabled by the outlined grid reinforcements and the corresponding impact on power prices and the total end-users’ electricity bill. Unfortunately, there is hardly any usable background information in the TYNDP documents and annexes that would substantiate these important statements. EWEA calls for further clarification and provision of further evidence that would substantiate these crucial conclusions. To this end, more detailed explanations on methodology and modelling approach should be provided in the annexes. Importantly, to properly assess these modelling results, ENTSO-E should provide figures on electricity generated per technology including the capacity factors assumed for RES and the assumed running hours for conventional generation. In addition, ENTSO-E refers in various passages throughout the text to “avoided residual RES spillage” without any further contextualisation. On page 52, for example, where some large spillage figures are used in certain Member States when applying a particular vision. Again, without insight into the modelling it remains impossible to form an opinion whether these spillages are likely to occur. | The statement directly relates to operation generation costs savings (corresponding to the mitigation of bulk power prices in wholesale market in ENTSO-E's assumed perfect competition model): by removing congestion that prevent cheap power sources (such as RES) to reach and supply end-users instead of the otherwise available more expensive ones (such as thermal), transmission grids enable operation generation costs savings.
EWEA |  |  | 4. Develop a more integrated network planning approach to connecting offshore wind energy from the Northern Seas The concept of a co-ordinated offshore grid to facilitate, at least cost, the development of the vast offshore wind resources of the Northern Seas has existed for almost a decade. For the ENTSO-E visions 3 and 4, this project is widely anticipated and is clearly necessary. It is necessary, therefore, to include the latter as a more conceptual project in the TYNDP in terms of a regional infrastructure priority, which cannot yet be reduced to individual elements. However, the long-term nature and need for continued political support certainly qualifies it as one of the transmission projects of “pan-European significance” under paragraph 1.1.1. of the TYNDP draft. Recent research, including CBA analyses carried out by TSOs such as within working group 1 of the intergovernmental North Seas Countries Offshore Grid Initiative (NSCOGI), demonstrates that new offshore interconnection should be designed as a meshed system. This may lead to some relatively minor increase in headline costs compared to ad hoc radial designs, but in every scenario provides a tangible financial return to the electricity consumers of Europe. This return includes: • maximising Europe’s ability to exploit its vast offshore wind resources thereby contributing to the European Energy Security Strategy (EESS); • a reduced footprint on the seabed which will reduce environmental impact, Compared to ad hoc radial connections; • an enhanced ability to fully integrate electricity markets and grids which will then both lower the price of electricity and improve security of supply, compared to ad hoc radial connections. While ad hoc radial solutions for the connection of offshore grid could be justifiable in Visions 1 and 2 (Slow Progress and Money Rules), it seems clear that Visions 3 and 4 (Green Transition and Green Revolution) will require a more thought out and integrated approach such as continuously supported by NSCOGI. | The offshore grid concept is present in the TYNDP 2014 in consultation, but will be more highlighted both in the final version of the TYNDP and Regional investment plan North Sea reports.
EWEA |  |  | 5. Further improve the Scenario outlook and adequacy forecast (SOAF) and accompanying target methodology for adequacy assessment The new draft’s wording on SOAF, in particular enlarging the assessment horizon to 2030 and initiating stakeholder dialogue on the assumptions and methodologies is positive. The shift from assessing generation adequacy to broader system adequacy, including storage and demand side management in the analysis is particularly welcome. Moreover, it is positive that, in the national adequacy assessments, the term “non-usable capacity” is not used in a generalising manner, but adapted according to national expected contributions of wind power generation to system adequacy. Many TSOs still counted wind and solar generation in the so-called “non-usable capacity” category, wrongly not taking into account the amount of firm power provided. Due to the variability of wind, its capacity credit is lower than that of other technologies. Nevertheless, there is a certain amount of firm wind capacity, which increases as power systems are better integrated, and contributes to the adequacy of the power system. Despite the real technical and physical capacity value of wind power, it is not yet regularly used for capacity planning. One of the barriers is the absence of a standardised accepted method for calculating capacity credit. The ENTSO-E target methodology document, rightly, mentions the challenge of developing harmonised methodology to assess wind energy’s contribution to guaranteed capacity at peak load (the so-called “capacity credit”). Therefore, EWEA would like to express its ongoing support for ENTSO-E to develop and utilise a harmonised method for wind power capacity credit assessment in European generation adequacy forecast and the TYNDP. EWEA is keen to liaise with ENTSO-E, also bilaterally, to further refine the probabilistic methodology approaches to capture wind energy’s contribution to system adequacy. | "Non usable capacity" is a concept specifically used to assess generation adequacy in the SOAF. ENTSO-E acknoledges that on average, and/or at a large scale, wind contributes to securing supply; however at a smaller scale, e.g. in a small country depending on one wind inflow, wind power can statistically be down to zero and cannot be relied upon. "Non usable capacity" is however not a concept used in the TYNDP analyses.
EWEA |  |  | When evaluating resources of the required flexibility, only conventional power plants are currently considered on the generation side, but not possible contributions by the capacity credit of wind. Whereas, high shares of wind energy do not only increase flexibility need, but can also contribute by, for instance, providing frequency support-related grid support services . | ENTSO-E acknowledges that flexibility can be provided by (some) thermal units, storage facilities, demand side response and wind credit, and the TYNDP simulation resorted to all options, with different available potentials depending on the Visions. The potentials can be tuned in the scenarios for the TYNDP 2016.
Eurelectric |  |  | The selected scenarios do not sufficiently consider the macro-economic implications of top-down choices. As the current discussions on the consequences of the German “Energiewende” shows (see e.g. IHS 2014) a future with high cost choices for the European power system will have more far reaching impact on the demand side and on the CO2 emissions than is foreseen in the current scenarios. The consequences of macro-economic hypothesis such as GDP growth should be included to assess the impact of potential economic crisis (in lowering demand in Europe). If an economic decrease in Europe has no or limited impact on long term capacity needs, it should be mentioned and documented. Alternatively, it should be assessed as a 5th scenario or in a sensitivity analysis. A socio-economic assessment of long term investments based on analysis results of only 2030 is too limited. | The mentioned parameters (energy costs, GDP, economic downturn...) have been considered as best as possible. Scenario building is a difficult science where ENTSO-E asked their stakeholders' for support during the whole process of preparing the TYNDP scenarios, from Spring 2012 to Autumn 2014. The selection and appraisal of macroeconomic parameters in all scenarios have been discussed. The process restarts this Autumn until next Summer for the TYNDP 2016 scenarios. Most interested stakeholders can join the works of the Long term network stakeholders groups for a more active involvement and contribution.
Eurelectric |  |  | Modelling results for at least 2025 (but preferably also 2020) for all scenarios and stages of grid development would make priorities in time a more explicit support from the modelling results. | (see answer to comment row 114)
Eurelectric |  |  | The uncoordinated implementation of capacity markets across different countries may have an impact on the value of the suggested infrastructure investment, and long run investment incentives for generation. The possibility of cross-border participation in capacity mechanisms and the value for the interconnector related to this should be considered as well. In modelling all countries as being remunerated according to long run marginal cost in an energy only market disregards these important issues, and additional scenarios should take into account the possible existence of capacity markets. | ENTSOE agrees that the CBA methodology must be completed regarding the assessment of capacity and flexibility value brought by transmission or storage projects
Eurelectric |  |  | The energy mix forecasts by member states in in each scenario should be underpinned with data tables: this information is currently presented in graphic form, with all countries in the same scale making it difficult to read. | SOAF input data tables are available for generation capacity per type and country. ENTSO-E will however publish the source information for every pan-European market study in an XLS file along with the final version of the report.
Eurelectric |  |  | A reference to the IEA World Energy Outlook 2013 instead of World Energy Outlook 2010 is recommended regarding the CO2 prices and primary energy prices because these prices change significantly and unpredictably in the short term. | The scenario development process spanned over 2 years and make difficult a reference to a most recent publication. Regarding all assumptions, the most important is to encompass all possible futures with a wide range of prices. Regarding specifically fuel and CO2 prices, the TYNDP 2014 Visions show very different pattern, with a reverse merit order between gas and coal; and marginal costs for thermal units ranging from 50 to 100 €/MWh.
Eurelectric |  |  | Cost Benefit Analysis methodology Development of the transmission system in a cost-effective way remains clearly the key challenge for European TSOs. TYNDP 2014 applies the new CBA methodology developed by ENTSO-E as required by Regulation 347 that should be validated by ACER later this year. | -
Eurelectric |  |  | Firstly, the current CBA clustering rules are too superficial and clustering of projects obstructs transparency in selection criteria. In many cases the estimated cost range is very large with makes it hard to assess the socioeconomic contribution for respective project. While clustering has been applied for reasons of simplification, it makes the CBA calculation sensitive to number of assumptions, including the decision of what is the relevant area that the calculations cover. It would be important that in the future, the TYNDP compares the estimated benefits of each individual project against their estimated costs, and comment around the cost-benefit balance in a transparent and consistent manner as it has already started with the work on PCI CBA. Clustering should only be valid in cases where a ‘sub-project’ is a clear precondition for a ‘mother-project’. | Clustering aims at providing a high-level view of investment needs at pan-European level, as required by EC and ACER since the TYNDP 2010 and its long list of investments. Every investment ("sub-project") are prerequisites for (mother)projects : their GTC contribution demonstrate it.
Eurelectric |  |  | A clarification should be also provided to enlighten the reasoning of the assessment that the grid expansion proposed by the TYNDP brings social economic welfare benefits of the 150 B€ investment (p.6 of the executive summary). | The reduction of bulk power prices from 2 to 5 €/MWh corresponds to the generation costs savings that the projects of pan-European significance, jointly, enable: more interconnection capacity enables more exchanges, i.e. cheap generation means can evict more expensive generation means.
Eurelectric |  |  | Secondly, some of the CBA methodology criteria may need to be reassessed:  Security of supply (SoS) is one of the most important issues in the TYNDP and one of the main drivers for European network development. However, in our opinion the TYNDP does not address and analyze the SoS issues in a sufficient way. Differences between countries regarding production technology and access to flexibility and reserves in the system, and how these different technologies are interconnected and utilized in Europe is of imperative importance when addressing SoS. It is therefore important that ENTSO-E addresses these issues vigilantly and improves the TYNDP in this regard. Given the significant growth of RES with a considerable stochastic nature, a common stochastic (probabilistic) technique for calculating the reliability of the power systems either in isolated or interconnected mode should be proposed. | ENTSO-E has already noted that the CBA methodology has some needs for improvement especially concerning SoS assessment. However, with respect to modelling, ENTSO-E considers already differences between countries regarding production technology and access to flexibility and reserves in the system, their use and interconnection in Europe, or the stochastic nature of RES. How ENTSO-E can improve the modelling in this respect is to be clarified.
Eurelectric |  |  |  The existing CBA methodology recognizes that not all the attributes to analyse can be properly quantified in monetary terms. Knowing that this problem will not be overcome in the short term, it is crucial that any proposal that cannot prove that benefits are greater than costs is accompanied with different alternatives that allow deciding for the most affordable solution. | Precisely because not all benefits are monetised, it is difficult to tell that a project is or not beneficial in an absolute way. The proposed projects are the most efficient to address the diagnosed investment needs and proposing alternatives when they do not appear profitable may not be an option.
Eurelectric |  |  |  In the current CBA evaluation, integration of RES seems to be one of several benefits that are taken into account. Even though reaching RES targets is important, we cannot see that introduction of specific production technologies gives a social economic benefit in itself. Especially if these technologies trigger other expensive investments in order to secure the security of supply (SoS). One of the major benefits of RES is the reduction of emissions valued by the cost of emitting climate gases, which seemingly already is taken into account by the value of reduced emissions. | Generating with RES istead of fossil fuel-fired power plants saves fuel costs, hence the SEW value.
Eurelectric |  |  |  Loss variations are deemed as a benefit. However, we believe that the benefits regarding losses are in reducing them and not in the variations. | Indeed, losses variations can be a benefit if they are reduced or a bad mark if they are increased.
Eurelectric |  |  | Thirdly, it is important to try to make projects as comparable as possible in order to assess possible alternatives and even priority between projects and the order in which projects should be finalized in order to maximize European SEW. For the moment, the plans do not have any ranking or priority of the different projects even though the value of the calculated Social Economic Welfare (SEW) for each project gives an indication of such priority (i.e. projects with the highest SEW should be implemented first etc.). However, for many projects there is a large uncertainty regarding e.g. investment costs and hence the calculated SEW. Different methods for calculation and evaluation of input data will also reduce the possibility to compare projects. | -
Eurelectric |  |  | for TYNDP 2014 seems still primarily based on national plans instead of on the assessment of the common European investment needs. Even with the calculations provided for 2014 there are still large price differences in the system. This raises the question if the proposed projects actually give the highest SEW for Europe as a whole or if there are still other projects that should be included into the plan. As an example, the TYNDP analysis shows large price differences between the Nordic countries and Continental Europe for all the different visions, even when large planned interconnection projects are included. ENTSO-E should therefore in our view analyze further increases of interconnection capacity between these areas and study and evaluate additional interconnection projects. The TYNDP must in the end demonstrate that the proposed projects actually give the highest social-economic welfare for Europe and that no other/alternative projects would provide a higher social-economic welfare. Otherwise the project portfolio has to be adapted. | The TYNDP aims at identifying the envelop of projects that can be required to match all possible scenarios. The assessment of each project shows in which respect the project is useful in each considered scenario. The TYNDP 2014 stresses however, that the set of projects of pan-European significance presented in the report must be complemented to meet the Vision 4 scenario.
Eurelectric |  |  | ENTSO-E must play an important analytical and advisory role using the top-down approach in order to ensure consistency between the national plans and even more importantly point out projects of European interest; even those with limited national interests or even negative national interests.Generally, all bidding zone borders with regular congestions should be analysed in the Regional Investments Plans by CBA on alternative investments (possibly also on other borders) to reduce the congestions as far as possible in order to optimize social economical welfare gains. Analysis should be done based on the whole regional (or even wider) market benefits, including increasing power transit possibilities and possible reduction of other, e.g. national, grid investment needs. | (see answer to comment row 136)
Nordenergi |  |  | Ranking of projects: In addition, the plans do not have any ranking or priority of the different projects. Indirectly this could be said to be shown by the value of Social Economic Welfare (SEW) for each project, i.e. projects with the highest SEW should be implemented first etc. However, for many projects there is a large uncertainty regarding e.g. investment costs and hence the calculated SEW. Is the SEW calculation model and assumption identical for all projects or is it based on national calculations and assumptions? Different methods for calculation and evaluation of input data will not only decrease the possibility to compare projects but make any comparison almost impossible. In our view it is important to balance the necessity of keeping every project’s unique costs and benefits with an overall pedagogical aim of making the projects as comparable as possible in order to assess priority between them. | The goal of the CBA is to provide the means for stakholders to sort and rank the projects, not anticipating their preference.
Nordenergi |  |  | Seemingly the TYNDP is based on national plans and a process to evaluate common European investment needs. However, even with the given plan there are still large price differences in the system. This raises the question if the proposed projects actually give the highest SEW for Europe as a whole or if there still are projects that should be included into the plan. As an example the EU has set a goal to continue the market integration process in Europe. The TYNDP analysis show large price differences between the Nordic countries and Continental Europe for all the different visions, even when large planned interconnector (IC) projects are included. ENTSO-E should therefore in our view analyze a further increase of IC capacity between these areas and study and evaluate additional IC projects. | (see answer to comment row 259)

## CCS
Respondent Organization | Initial | Proposed | Comment | ENTSO-E answer
WWF AT | Regarding the inclusion of third party projects in the TYNDP and RgIPs 2014, a transparent and fair process was created in which non-TSO promoters had the possibility to include their transmission and storage projects, which fulfilled pan-European significance requirements. |  | The ENTSO-E seems not to have the expertise to assess hydro pump-storages, which are meant to be included into the TYNDP for Electricity. It is to be critiziced that the main actor in the assessment of these kinds of projects is the project promoter himself. It is to be made transparent in which way hydro-pump storages (as third party projects) are assessed and by whom exactly has the information been provided and the assessment carried out. Recommendable to have external consultants or a separate body dedicated to TYNDP assessment of third party projects | All TYNDP projects (public and 3rd party projects) are assessed using a common approach in line with the CBA guidelines approved after several public workshop where different stakeholders took part. Improvements of the CBA for next TYNDP editions are being planned. The information provided by 3rd party promoters is to be considered as confidential as ENTSO-E is not the owner. The publication of such information can just be done by the promoters themselves.
WWF AT | Integration of storage plants, mainly hydro in the Alps region, facilitates the efficient use of RES: The divergence in the generation time and demand resulting from the integration of volatile RES is another rising and sustainable challenge for the overall power system, leading to the necessity for additional transport and storages capacities as well as other innovative measures. Considerable storage potential is available in the very centre of the region, particularly in the form of existing and planned hydro pumped storage power plants located mainly in the Alps. |  | It has been claimed, that the project is needed as part of Europe’s “green battery” in the Alps for stabilizing the supply of electricity within the EU. However, this claim cannot be considered true, because it was based on out-dated higher presumptions of needed energy storage. Flexibility of power generation and demand is able to manage a 90 percent share of renewables in Germany and 80 percent in Europe. | Flexibility in power generation and demand helps integrating renewable power efficiently. However, in order to achieve a significant effect, this functionality has to be introduced in a large scale to the loads (and consumers) and comes along with the necessity of appropriate power plants (which also do need a certain market model in order to be economically successful). Such developments are addressed in the scenario building for the TYNDP, presently ongoing for the next release.
WWF AT | Drivers for Power System Evolution: Integration of storage plants, mainly hydro in the Alps region, facilitates the efficient use of RES |  | To achieve the objectives of European energy policy plays it is to be admitted that flexibility in the supply system plays a central role in the future. This can be covered to a large extent by network expansions, the European electricity market itself, load management, flexible biogas plants, combined heat and power and Power-to-heat. Thus it is not comprehensible that all four Scenarios or Visions presented, put high emphasis on the expansion of the energy (meaning hydro) storages in the Alps for the achievement of EU Energy objectives (including massive promotion of RES in the near future). | Within the whole TYNDP process a scenario building took place with public involvement. The common expectation of the future is, that load management and e.g. flexible biogas plants will have a potential that may fall shortto meet the requirements of a very volatile renewable generation. Therefore the transition to types of energy with high installed capacity and low full load equivalent hours (as RES) requires besides a capable grid also storage facilities. (see ENTSO-E website, 3rd 2030 Visions workshop).
WWF AT | Third party storage projects: The integration of storage plants is a main driver of grid development and reduces the divergence in time between generation and demand. In all Visions, a significant increase of the installed HSPP capacities is assumed (especially in the Alps). |  | See comment above. | (same answer above)
WWF AT | In the region CCS four HSPP projects from third party promoters have been investigated - three projects in Austria and one in Germany. These projects were assessed in line with the Third Party Procedure for promoters of storage projects. The detailed descriptions of the projects and the assessment results are published in the appendix. |  | Information provided on the Assessment of third party projects is not sufficient (see Appendix I) the Regional Investment Plan for CCS does not apply the same quality criteria to transmission projects and to third party projects on the other hand. In order to allow for effective participation in the consultation proceedings the information on the candidate projects and the assessment method as well as the concrete information shall be made transperent in a comprehensible manner. | The information used for the project assessment was provided by the 3rd party promoters during their application to the TYNDP. As this information does not belong to ENTSO-E or the participating TSOs, it is considered as confidential and does not get published in the same quality as common in the frame of public TSOs projects.
WWF AT | In the CCS Region the five main drivers for investment are: • Massive RES integration • The Integration of storage plants, mainly hydro in the Alps region, facilitates efficient use of RES • Wide area energy flows • Nuclear (and old conventional generation) reduction • The system security and Security of Supply of some European cities and regions |  | See comments ad 4.2 and 5.2. | (same answer above)
WWF AT |  |  | The assessment of storage projects within the RIPlan CCS is incomplete. The assessment graphic in 11.5 shows only an evaluation with respect to the criteria of technical resilience (B.6), flexibility (B.7), environmental (S.1.) and social impact (S.2.). Although we highly appreciate the introduction of environmental indicators when assessing energy infrastructure projects, it is not comprehensible why other criteria – e.g. the financial viability of these projects (C.1.), are not visible in the evaluation. Further it needs to be shown how each and every storage project does provide to the main objectives of EU energy policy (Security of Supply, Market integration and Sustainability). If the assessment of energy storage projects in the TYNDP provides the sole basis for following PCI selection process – it serves as the assessment for every PCI candidate. Thus these projects need to be thoroughly assessed and evaluated. If not, no qualitative and thorough selection of PCIs can be carried out in the following process. Further it is to be suggested to provide for a more comprehensible summary of the Draft Plan, indicating Visions and Scenarios preferred and why certain projects fit into these Visions and Scenarios. | Detailed project information in case of 3rd party projects is considered as confidential and can not be published within the report (this affects also the costs (C.1)). Further to that, the storages assessed in the TYNDP process were not chosen by ENTSO-E but brought in by an application of the project promoter (during the process two application windows were opened for an official introduction of 3rd party projects).
WWF AT |  |  | Project 222: The extension of the Kaunertal plant shall provide for additional electricity production of about 621,5 GWh. The pump storage process comes along with efficiency losses – total energy balance of the planned Tyrolean hydro power and storage plants (respectively the additional amount of renewable electricity) can be estimated at 320 GWh per year. The project consists of two parts: 1. the storage shall be extended (=electricity storage) by building an additional upper-reservoir in the Platzer Valley (Platzertal) and the required technical infrastructure (pump-turbines) to enable pump-storage operation between the two water storages. 2. the production capacity of the plant shall be increased (=electricity production) by building a new downstream-power station at Prutz. According to media reports TIWAG director Mr. Wallnöfer himself stated that without the water from Ötztal (= electricity production part of the project) the expansion of the Kaunertal power plant could not be realized. This comment is to be seen very critical with respect to the projects current PCI status: The status is to be dedicated to energy infrastructure projects only - if the whole project (pumped storage plus additional electricity production) is not viable without the electricity production part it completely loses its PCI-justification. Only the storage is the project part which is eligible for the PCI designation process. The extension of the electricity production capacity is not eligible according to the Regulation and should not profit from the benefits of being PCI – meaning finance, faster permitting, higher priority of project on national level etc. Thus it is also questionable whether to include it into the current TYNDP. Security of Supply: Recent studies outline, that an increase of supply capacity in Europe for balancing energy is currently no basic condition for the achievement of European Energy Transition (cp. Frauenhofer IWES, Roadmap Speicher. 2014, cp. also Art 4/1 c. ii. TEN-E Regulation). It has been claimed, that the project is needed as part of Europe’s “green battery” in the Alps for stabilizing the supply of electricity within the EU. However, this claim cannot be considered up to date, because it was based on out-dated higher presumptions of needed energy storage. Flexibility of power generation and demand is able to manage a 90 percent share of renewables in Germany and 80 percent in Europe. Competitiveness: Currently, storage in the EU energy system is almost exclusively pumped hydro-storage, mainly in mountainous areas (Alps, Pyrenees, Scottish Highlands, Ardennes, Carparthians). This form of electricity storage does not longer meet the requirements of the European Energy Market –Europe’s grids continue integrating day by day and reduce the need of storage units held available. Furthermore, German “Energiewende” erodes pumped hydro-storage’s business model: Feed in of photovoltaic power cuts progressively price peaks at noontime, so there are too little hours per year left for pumped hydro plants to run profitable. This is why the market faces a problem for building new large capacity even under the old generation scheme: economically pumped hydro is less competitive as other options. It is to be expected that (if) the project receives development consent it might be commissioned by 2023. At the same time it is to be expected, that new electricity storage methodologies – such as compressed-air Energy storage power plants or power to gas technologies – might be made competitive by 2020 under appropriate conditions. The Kaunertal Extension project is currently one of the hugest and most expensive (1.2 billion Euros) power plant projects in Europe. According to TIWAG itself the project is not economically viable if it does not contain an increase in electricity production as an addition to the construction of a hydro pumped storage. Electricity production facilities are not eligible for funding, prioritization and accelerated permitting proceedings promoted for by the TEN-E Regulation. But especially this part of Kaunertal Extension project is the most conflictual one regarding environmental impacts, competition with other planned projects and the justification of its energy political importance (PCI status). S.1. Environmental impacts: The rivers affected by the project are listed in the actual National Water Management Plan (NGP 2009) with best ecological status according to the WFD. Damming and redirection of these rivers would adversely affect the ecological status of these rivers. This constitutes an infringement of the prevention of deterioration according to Art 4 WFD. Gurgler and Venter Ache (two of the affected rivers) have been nominated to river sanctuaries of Austria in 1998 by the Ministry of Environment and the WWF. For the realization of the project about 25 km of large tunnel systems (with a diameter up to 6m) need to be constructed through the Natura 2000 area "Ötztal Alps" and the natural park "Ötztal" this threatens the established nature conservation objective for the mentioned areas. Furthermore the damming of Platzertal would destroy a previously undeveloped mountain valley, which manifests itself through unique cultural and ecological features. The valley is part of an “alpine wilderness area network " and stated as an important refuge zone for typical alpine species. Thus environmental impacts caused by this projects have to be considered rather high. | ENTSO-E provides the basis for the selection of projects of common interests in form of the TYNDP. The selection of PCIs itself is carried out by the European Commission and Member States. The assumptions of our scenarios are defined and explained within the TYNDP 2014 document. Before the TYNDP process itself, the scenarios were defined and passed through a public consultation and were developed within stakeholder workshops etc. with a high involvement of the stakeholders. S1 and S2 indicators must be re-defined for storage and the final release of the TYNDP will bear for storage project "NA" (instead of "less than 15km"; the latter does indeed not reflect the environmental impact of storage projects. Environmental impact of hydro-storage is however not ENTSO-E's expertise and support is needed in this respect.
TIWAG-Tiroler Wasserkraft AG |  | We attatch our response to the TYNDP 2014 Consultation, Pumped Hydro Storage Assessment | We consider TYNDP 2014 as one of the best start up strategy papers to give energy transition of the electricity system a well-organized and structured technical framework. We are aware of the relevance of this paper not only for experts of the energy sector, but also for policy makers and other persons interested in that topic. TIWAG welcomes the inclusion of Hydro Power Storage as 3rd party projects to the TYNDP 2014. | Thank you for your positive words acknowledging our efforts. They encourage us to improve the quality and transparency of our publications.
TIWAG-Tiroler Wasserkraft AG |  |  | In general TIWAG is affected by this paper as a market player and in particular as one of the most important Austrian (cross-border-) ancillary and flexibility service providers operating hydro storage and hydro-pumped storage power plants during the last 70 years. We welcome that the alpine region and its potential of hydro storages is addressed as an important factor to promote the RES integration at an European scale. | This comment fully supports ENTSO-E's conclusions.
TIWAG-Tiroler Wasserkraft AG |  |  | With respect also to the latest German Grid development plan we may assume, that until 2030 HPS will play a key role for system stability and security of supply focusing on (market based) ancillary service products at low costs, high flexibility, best efficiency (economical as well as energetical) and CO2 neutrality. Additionally, from 2030 on they will expand their role in short, medium and long term storage for energy shifting purposes. | The CBA assessment relies on simulation that prevent a proper appraisal of the close-to-real-time phenomena and benefits regarding flexibility and ancillary services. This is stressed as a limitation of our assessments. It is true both for transmission and storage, but all the more sensitive for storage that their pay-back may rely on provinding flexibility.
TIWAG-Tiroler Wasserkraft AG |  |  | TIWAG intends to expand these services inter alia by extending the existing power stations Sellrain-Silz/Kühtai and Kaunertal Power Station resulting in enormous investments for the benefit of the region and the European industry. | -
TIWAG-Tiroler Wasserkraft AG |  |  | The “Extension of the Pump Storage Powerplant Kaunertal” is part of the 1rst EU-wide PCI-list (project index 222) and is affected by the CBA assessment for 3rd party projects within TYNDP 2014 (see page 296 of the regional investment plan 2014, Continental Central South Region). Within this extension Kaunertal Power Station not only will provide ancillary services and flexibility products but also produce additional renewable energy (in total 622 GWh/a) by additional natural inflow. | The project "Extension of the Pump Storage Powerplant Kaunertal" was included into the assessment process based on the data TIWAG delivered during the 3rd party project application. During the project assessment, it is currently not possible to respect ancillary services and flexibility products. The assessment results were derived by consideration of the installed capacity, the reservoir size and the natural inflow.
TIWAG-Tiroler Wasserkraft AG |  |  | Thus, we assume it’s additional CO2-avoidance potential by approx. more than 500 kt/a. | This comment supports ENTSO-Es conclusions. The updated assessment results are in the appendix of TYNDP and Regional Investment Plan.
TIWAG-Tiroler Wasserkraft AG |  | Add at 11.5., Page 295, Regional Investment Plan 2014, CCS: Pumped Hydro Storages have played a significant role and will do so for highly efficient RES-integration, system stabilization and security of supply within a time frame less than 60 minutes.. Respecting the enormous complexity of a wide area simulation, as a convention for TYNDP 2014, the assessment is done at a 60 minutes’ time frame and these basic benefits are out of scope. However, it is expected to be part of future versions. Therefore not all benefits of PHS are part of this assessment. For efficiency reasons the assessment scheme mainly was developed for transmission line projects, where more aspects for KPI declarations are needed. Accordingly, storage projects systematically may not get the full points of some KPI’s. | (Pumped) Hydro Storage power plants have played a significant role for a highly efficient system stabilization and security of supply and thus have played a significant role for a cost effective big scale RES-integration during the past years. The German Grid Development Plan 2014 (NEP 2014) estimates an additional PHS-demand with of approx. 6 GW (!) for load frequency control reserves solely for this area within the coming 15 years. These services are mainly driven by power demand and are operated within a time frame less than 60 minutes. TYNDP 2014 and other recently published highly qualified strategy papers underline clearly, that the increasing divergency of RES-generation and demand will lead to a significant additional amount of energy driven storage capacity with medium and long term (seasonal) energy shifting. Hydro pumped storage power plants mainly in the Alps will play a basic role to meet this challenge (s. page 8, investment plan, CCS-Region). This demand is expected approx. from the year 2025 on. ENTSO-E clearly stated at the stakeholder workshops, that all assessment calculations are done at a 60 minutes time frame. Therefore all results reflect on steady state conditions and discuss more or less energy balancing aspects. This means, that power relevant aspects being relevant for PHS-LFC-services – as a con-vention – have not been assessed. While it is clear for experts that within this well defined scope only a part of PHS-benefits are assessable, the latest discussions point out, that it may be unclear for a number of stakeholders in particular for policy decision makers. To avoid any misunderstanding and other negative effects, we suggest to add the requested commentary (here at collum "E" - Proposed version) to chapter 11.5, storage projects (p. 295, Regional Investment Plan 2014, CCS): | ENTSO-E acknowledges all benefits of storage projects are not captured: the implementation of the CBA only captures the 'energy' part of the benefits, ie. only the ability to buy at cheap hours and sell at peaks and none of the operating benefits. A caveat is provided in the CBA methodology and the introductory page of the Appendix 1.3 (storage assessment) of the TYNDP report provides an explicit caveat in this respect, insisting the valuation is still to be completed with respect to 'capacity' and 'flexibility' parts of the benefits. A clarification that this comes from the current scope of our methodologies and to the 60 minutes-quantum in the simulations will be added. Also as the assessment of KPI was developed for transmission projects; storage projects systematically may not get the full points of some KPIs. Last, S1 and S2 indicators must be re-defined for storage and the final release of the TYNDP will bear for storage project "NA" (instead of "less than 15km"; the latter does indeed not reflect the envisronmentalimpact of storage projects. Environmental impact of hydro-storage is however not ENTSO-E's expertise and support is needed in this respect.
TIWAG-Tiroler Wasserkraft AG |  |  | We ask to check: • the CO2-avoidance potential of Kaunertal extension project for the given additional natural inflow of 622 GWh/a as well as • the positive effect of this project in case of voltage collapse (B.7), as this power plant is part of the black start-capability- and U/Q-control-concept of the entire power plant. | A inspection of the used input data showed a different interpretation especially at the natural inflow values. These were corrected and a reasessment of the project performed. Based on this outcomes the results in the TYNDP and RgIP are updated and can be found in the appendix.
Edison |  |  | Edison welcomes the opportunity to answer this consultation of ENTSO-E on the TYNDP 2014 Package and wishes to provide some specific comments on the Regional Investment Plan Continental Central South (CCS):  The costs related to the energy mix evolution for each country and generation type in the different scenarios considered should be provided in data tables and not only through a graphical representation (see Chapter 3.2). A higher level of transparency on these estimations would allow a better understanding of the outcome of the market studies run by ENTSO-E and, in particular, the results of the optimization of generation portfolios across borders. Moreover, better transparency on these data would enhance the comparability between the assessment of projects made within national investment plans and the CBA results provided in the TYNDP and regional plans. For example, it seems from the CCS Plan that the generation marginal cost differential between Italy and Montenegro, which influences the calculation of the CBA indicator B2 (Socio Economic Welfare – SEW) for the IT-ME interconnection (project 28), is at the maximum 10 €/MWh, depending on the scenario considered. Yet, in the national investment plan of Terna1 this project shows a Profitability Index (IP)2 of 2,2 which seems to imply a price differential between Italy and Montenegro (PIT>PME) of about 30 €/MWh for twenty years. The assumptions taken into account in the two plans do not seem to be consistent, thus increasing the uncertainty on the evaluation of the real impact of this project also compared with other investments in interconnection capacity. For this reason, Edison claims a better coordination between the analyses made in national and European/regional investment plans. | XLS spreadsheets are already available wrt SOAF data, displaying especially the basic assumptions for the generation mix in every country. The material displayed on the ENSTO-E extranet about the 3rd workshop on scenarios gives further information. ENTSO-E will also publish the source information for every pan-European market study in an XLS file along with the final version of the report.
Edison |  |  | As regards the identification of bottlenecks, we believe that they should be considered as such if significant issues related to security of supply, RES integration or access to cheap generation are at stake. On the contrary, in the current version of the CCS plan the results of the CBA of the interconnection between Sicily and Tunisia (project 29), which is aimed to solve the bottleneck identified between Italy and North Africa, does not seem to show significant benefits according to the criteria identified by ENTSO-E. This seems to be especially true if those benefits are compared with the much higher ones derived from interconnections between European countries or between bidding areas within countries (e.g. in Italy). Therefore, we suggest that ENTSO-E should identify North Africa as a region of potential market integration between the European market and third countries rather than as a bottleneck which needs to be solved through specific investments. | A bottleneck between North Africa and Italy, is mentioned as there is presently no interconnection at all, and that the prospect of building one has been considered.
Edison |  |  | The results of the market studies shown in Section 3 of the Plan should be integrated with the figures related to adequacy forecast in order to allow a better understanding of the reasons of the need to cover part of the annual national demand with foreign generation. In particular it would be useful to clarify if this is due to generation adequacy problems or to the availability of cheaper generation resources located abroad. | Adequacy issues are addressed in the SOAF report. But it is important to notice that the 2030 Visions are by essence "adequate scenarios", at European level at least: the TYNDP checks how the grid must be eventually adapted to access the expected potential of the generation means.
Eurelectric |  |  | The development of the German transmission system and of the Swiss-German interconnection: The contribution of new and planned pumped storage power plants in the Alps to balance the intermittent Renewable Energy Sources (RES) is strongly dependent on the development of the German transmission network on the North-South corridor. The development of the grid infrastructure to transfer the volatile energy, especially from off-shore wind, to the flexible pumped storage plants should be a priority in order to consider relevant scenarios for increasing the share of RES. Besides the increase of the German North-South transfer capacity and the elimination of the respective bottlenecks, the resulting strengthening of the interconnection CH-DE is of vital importance in this respect. | -
Eurelectric |  |  | The costs related to the energy mix evolution for each country and generation type in the different scenarios considered should be provided in data tables and not only through graphical representation (see Chapter 3.2). A higher level of transparency on these estimations would allow a better understanding of the outcome of the market studies run by ENTSO-E and, in particular, the results of the optimization of generation portfolios across borders. Moreover, better transparency on these data would enhance the comparability between the assessment of projects made within national investment plans and the CBA results provided in the TYNDP and regional plans. For example, it seems from the CCS Plan that the generation marginal cost differential between Italy and Montenegro, which influences the calculation of the CBA indicator B2 (SEW) for the IT-ME interconnection (project 28), is at the maximum 10 €/MWh, depending on the scenario considered. Yet, in the national investment plan of Terna2 this project shows a Profitability Index (IP)3 of 2,2 which seems to imply a price differential between Italy and Montenegro (PIT>PME) of about 30 €/MWh for twenty years. The assumptions taken into account in the two plans do not seem to be consistent, thus increasing the uncertainty on the evaluation of the real impact of this project also compared with other investments in interconnection capacity. For this reason, EURELECTRIC claims a better coordination between the analyses made in national and European/regional investment plans. | (see answer to comment row 18)
Eurelectric |  |  | As regards the identification of bottlenecks, we believe that they should be considered as such if significant issues related to security of supply, RES integration or access to cheap generation are at stake. On the contrary, in the current version of the CCS plan the results of the CBA of the interconnection between Sicily and Tunisia (project 29), which is aimed to solve the bottleneck identified between Italy and North Africa, does not seem to show significant benefits according to the criteria identified by ENTSO-E. This seems to be especially true if those benefits are compared to the much higher benefits generated by interconnection between European countries or aimed at solving congestions within countries (e.g. in Italy). Therefore, we suggest that in such case ENTSO-E identifies this area as a region of potential market integration between the European market and third countries rather than as a bottleneck which needs to be solved through specific investments. | (see answer to comment row 19)
Eurelectric |  |  | The results of the market studies shown in Section 3 of the Plan should be integrated with the figures related to adequacy forecast in order to allow a better understanding of the need to cover part of the annual national demand with foreign generation. In particular it would be useful to clarify if this is due to generation adequacy problems or due to the availability of cheaper generation resources located abroad. | (see answer to comment row 20)

## CSW
Respondent Organization | Initial | Proposed | Comment | ENTSO-E answer
Eurelectric |  |  | EURELECTRIC agrees with the insufficient cross border interconnection capacities and the resulting investment needs. We appreciate that domestic projects are also mentioned (as congestion within Spain, 25% of projected investment costs have to go into domestic projects, p. 10) | As mentioned in the report 25% of the total investment in the region is referred to internal investments within the region. As described in the chapter 5.2 the internal investments are related to existing and future generation evacuation and security of supply. In figure 5-2 the bottlenecks in the region are identified by each type.
Eurelectric |  |  | ENTSO-E regional group singles out (p 12) that even all projects are not sufficient for meeting the 2030 challenge- new projects are needed in interconnecting the Iberian peninsula and rest of Europe. The major challenge is that grid development might lag behind 2030 RES penetration. | The comment is in line with ENTSO-E conclusions. This issue will continue to be addressed within the RG CSW framework. Euroelectric, as well as other bodies or persons can help efficiently by supporting interconnection projects with public and authorities.
Eurelectric |  |  | As it is stressed in the report, interconnection between Spain and France is useful whatever the scenario under the analysis is. In short, any interconnection capacity project would be proven helpful to solve the problem of transmission adequacy. However, there are only two expensive projects currently proposed: projects 16 & 182, consisting of two HVDC submarine lines, which would have a great impact on transmission tariffs, and which are not deemed sufficient to cover the capacity needs. As any alternative proposal would likely result in similar benefits, because it is placed in the most critical area in the region, the evaluation and comparison of alternative solutions could increase cost-efficiency greatly, therefore being very welcomed by stakeholders. The most critical barrier in the CSW region could be social opposition. However, taking into account that they could benefit from the particular advantages of PCIs to obtain the permits, TSOs should consider new and reinforced overhead lines between France and Spain. | Project 16 (Western interconnection FR-ES) is promoted by TSOs’ and it is the result of a joint in-depth analysis of the whole French-Spanish border (except the region of Oriental Pyrenees as agreed during the permitting process of the Eastern Interconnection), taking into consideration social, environmental, and technical constraints, and the impact on internal grids. In cooperation with both goverments all the possibilities had been analyzed, it was agreed that a submarine link could be the most feasible option. On the other hand, Project 182 (BRITIB) is promoted by a 3rd party, and it is considered as a non regulated investment . As mentioned in the report new projects will be needed between the Iberian Peninsula and the rest of Europe and new planning studies will continue in the framework of the RG CSW (these studies already started on the TYNDP2016 framework).
Eurelectric | ENTSO-E’s assessment of investment needs (p. 50) defines the need for new investment to reinforce Spanish-Portuguese interconnection: “Although the 2013 NTC values between Portugal and Spain (1800-2200 MW from Portugal to Spain and 1800-2200 MW from Spain to Portugal) are higher than those between France and Spain, some constraints still occur (in 2013 the congestion rate was 12%) and additional investments are needed to achieve the main political goals established for reaching a complete operational Iberian Electricity Market (MIBEL)”. | Despite the fact that the situation is not perfect, we do not see the same urgency for grid investment as in the case of the border between Spain-France. Even though the congestion rate in Spain-Portugal border was 12% in 2013, the price spread between both areas during these congested hours was less than 1.5%. EURELECTRIC believes that ENTSO-E should instead focus on Spanish-French border which suffers from a structural market congestion between price zones (the congestion rate is 62%), and has a very low value of interconnections. A definitive and decisive support is needed to reinforce this interconnection and integrate the Iberian Peninsula in the European market. |  | The real bottleneck for the integration of the Iberian market in the European market is the Spain-France interconnection; this issue has been specifically addressed throughout the report, and important reinforcements in this interconnection are analysed, though additional reinforcement is deemed necessary. Although Iberian Penninsula-France border is the main priority, a fully integrated Iberian market requires an appropriate Spain-Portugal interconnection capacity. It will increase the social economic welfare and reduce the spilled energy in the Iberian Peninsula.
Eurelectric | As far as financing of transmission grid development is concerned, ENTSO E points out that: “In the CSW region, TSO´s financial ratios could deteriorate where remuneration is delayed until the end of the construction or even further. This can prove to be meaningful given the large size and recurrence of the TSOs’ investment effort. Transmission investments should be remunerated during the construction phase, and not only since or even after the date of commissioning, thus avoiding deteriorations in TSO´s financial ratios during the construction period.” |  | We disagree with this view. With a significant part of the investment already recouped, there will be reduced incentives to deliver and set up high-quality infrastructure on time. It is however important that investments will be remunerated as soon as they are completed. | Having projects that take several years to be commissioned and taking into account that some projects require large investments efforts from the TSOs, and that are different economic/financial realities with the three TSOs in the region, we consider that the remuneration of the Transmission investments could be done during the construction phase when necessary or at least as soon as project is commissionned . If nothing is done in this respect, also the potential need for implementing a huge amount of new investments could put TSOs, and consequently power supply, at risk.
GAS NATURAL | The regional analysis shows that there are important transmission needs arising from now until 2030 | SIMILARLY TO CONCLUSIONS OF THE TYNDP 2012, WHERE AN ANALYSIS OF THE TRANSMISSION NEEDS FOR THE PERIOD 2012-2022 WAS MADE, the regional analysis shows… | Conclusions of the ENTSOE TYNDP 2014 pretty much looklike to the conclusions of the TYNDP 2012, even if they cover a longer period | The regional analysis shows that there are important transmission needs arising from now until 2030. This need confirms the TYNDP 2012 conclusions. The TYNDP 2012 already gave an outlook beyond 2022, but no systematic. A similar comment is in chapter 11.1 "Looking further forwards to 2030, the TYNDP 2014 confirms the conclusions of the TYNDP 2012".
GAS NATURAL | All the interconnection projects included in the CSW RgIP show important benefits for the European system: | All the interconnection projects included in the CSW RgIP show important benefits for the European system, ENCOURAGING THE EVALUATION AND COMPARISON OF ALTERNATIVES DUE TO THESE POSITIVE RESULTS: | Considered that even costly projects show important benefits, we would like to encourage TSOs to evaluate other alternatives (e.g. overhead lines) and to compare the results | As mentioned in the report, new projects will be needed between the Iberian Peninsula and the rest of the Europe and new planning studies should continue in the framework of the Regional Investment Plan Continental South West (these studies already started in the TYNDP 2016 framework) in order to assess the possible alternatives to reinforce the interconnections within the region, comparing project costs and benefits.
GAS NATURAL | The other main driver (...) is the insufficient cross-border capacity between the Iberian Peninsula (in particular Spain) and the rest of the European Continent |  | Considered that they could benefit from the particular advantages of PCIs, why aren't there other interconnection projects proposed in the TYNDP 2014? | All the interconnections of the Iberia peninsula and its neighbours, which are least under consideration phase, are incorporated in the RgIP (including one 3rd party projects). These projects have been identified as pre-requisite steps to any further interconnection reinforcements. Experience showed the need for step by step projects. As mentioned in the report new projects will be needed between the Iberian Peninsla and the rest of Europe and new planning studies will continue in the framework of the RG CSW (these studies already started on the TYNDP2016 framework).
GAS NATURAL | The studies still show a high congestion level (40-60%) for all Visions. |  | Considered that they could benefit from the particular advantages of PCIs, why aren't there other interconnection projects proposed in the TYNDP 2014? | see answers above
GAS NATURAL | There is the need for a further increase in this interconnection capacity to values in the range of 7-10 GW in Visions 1 and 2, and greater than 10 GW in Visions 3 and 4 |  | Considered that they could benefit from the particular advantages of PCIs, why aren't there other interconnection projects proposed in the TYNDP 2014? | see answers above
GAS NATURAL | Long term includes some more expensive projects, especially regarding interconnections, as some of them are submarine and include HVDC technology. | Long term includes some more expensive projects, especially regarding interconnections, as some of them are submarine and include HVDC technology, WHICH WOULD HAVE A GREATER IMPACT ON TRANSMISSION TARIFFS | Why aren't there other alternatives less expensive? In particular we would like to refer to the congested Spain-France border, where the projects proposed only recur to expensive technologies | see answers above
GAS NATURAL | The proposed projects cover the described investment needs | The proposed projects COULD cover SOME OF the described investment needs | Stakeholders could prefer to opt for other potential alternatives. Additionnally, as the report concludes they do not cover all the investment needs. | The projects do answer the identified investment needs although they must be completed. On page 10, Regional Investment Plan Continental South West states "The proposed projects cover most of the described investment needs".
GAS NATURAL | So in order to reach the EC objectives new projects will be needed | So in order to reach the EC objectives new projects will be needed. STAKEHOLDERS HAVE ALSO EXPRESSED THEIR DESIRE FOR ADDITIONAL ALTERNATIVE PROJECTS TO BE EVALUATED AND COMPARED WITH THOSE PROPOSED IN THE PRESENT TYNDP 2014 |  | Part of the analysis of different alternatives has been done internally during TYNDP2014 process and is being analysed under the RG CSW, nevertheless this issue is something that could be presented in more detail in the next Regional Investment Plan.
GAS NATURAL | A major challenge is that the grid development may not be completed in time if the RES target are met as planned by 2030 | The achievement of 2030 targets could be endangered if there is not a sufficient grid development in time | Conversely to ENTSOE, we believe that Member States could not be asked to fulfill their commitments if there is not an adequate infrastructure development, as the economic burden for consumers would be unacceptable | The English wording is inappropriate and section 1.5.4 of the Regional Investment Plan Continental South West will be amended as follows: "A major challenge is that the grid development may not be completed in time whereas RES target are met as planned by 2030." ENTSO-E fosters the timely development of grid to enable RES development. Globally, the development of the infrastructure and the RES deployment shall go hand in hand as such avoiding the "chicken and egg" problem. In order for the citizens to benefit of the RES development the infrastructure shall be supported to be developed in the same pace. Also huge amounts of investments in a short period of time (without start the recovering of the investment) could deteriorate the TSO's financial ratios and put investments at risk.
GAS NATURAL | Although grid projects prove beneficial for the European community as a whole, with a net reduction of the power supply costs, they represent large investments and financing them still remains an issue for TSOs in times of limited public finances, and therefore securing the perspectives of investors is key for success | DELETED | This is not a real issue for TSOs In the CSW region to be highlighted. Investment costs -also covering financial costs- are recovered via regulated third party access, passed onto consumers | Transmission costs are indeed recovered via regulated tariffs. But Gas natural earlier expressed concerns about "expensive options" for reinforcing the interconnection and it is important to stress that consumers, benefiting from the projects will also face higher transmission tariffs.
GAS NATURAL | This RgIP aims to describe the investment needs and assess the associated planned projects for 2030 | This RgIP aims to describe the investment needs and assess the POTENTIAL planned projects for 2030 |  | ENTSO-E believes the TYNDP projects are required to answer the investment needs and proposes them as best options to answer the investment needs.
GAS NATURAL | projects of regional and/or European significance, which allow the main European targets to be met with particular regard to the development of the Internal Electricity Market (IEM) and the integration of Renewable Energy Sources | projects of regional and/or European significance, PROPOSED TO ACHIEVE THAT the main European targets ARE met with particular regard to the development of the Internal Electricity Market (IEM) and the integration of Renewable Energy Sources | The projects are proposed to meet European targets, but they are not the only projects that would allow it, as other alternatives could be also valuable and could be appreciated. The TYNDP assesses some potential solutions | (see answer above)
GAS NATURAL |  |  | Considering the size of the Spanish power market (5th biggest) we are surprised to see that ENTSOE estimates that Spain would have the 2nd greatest amount of RES installed capacity (hydro excluded) in the 4 Visions, especially when there is a permanent lack of capacity of interconnection between Spain and France | The installation of RES generation in those countries with greater natural resources is not surprising, but quite logical indeed. This has been acknowledged when the scenarios have been consulted. ENTSO-E agrees that in such a case, and specially in electric islands like the Iberian peninsula, the interconnection capacity must be expanded.
GAS NATURAL | Cost Benefit Analysis, combined with multi-criteria assessment is essential to identify transmission projects that significantly contribute to European energy policies and that are robust enough to provide value for society in a large range of possible future energy projections | Cost Benefit Analysis, combined with multi-criteria assessment is USEFUL to identify AMONG PROPOSED transmission projects that significantly contribute to European energy policies and that are robust enough to provide value for society | CBA only analyses the currently proposed projects | (see answer above)
GAS NATURAL | , while at the same time being efficient in order to minimise costs for consumers | DELETED | The evaluation and comparison of alternative solutions to identify critical investment gaps (e.g. between Spain and France) would increase cost-efficiency greatly. There are only two expensive projects currently proposed (proj 16 & 182) | (see answer above)
GAS NATURAL | Vision 2: "Money Rules" | TO BE MODIFIED | TO BE MODIFIED IN ALL TYNDP PACKAGE. The Vision 2 gives more consideration to economic constraints and affordability. "Money Rules" has an undesirable negative connotation that should be avoided | The scenarios and their names have been consulted with stakeholders during more than 2 years and discussed in the long term network stakeholders group . But the comments will be taken into account when naming the TYNDP 2016 visions.
GAS NATURAL | Vision 1: "Slow progress" | Vision 1: "Business as usual" | TO BE MODIFIED IN ALL TYNDP PACKAGE. The Vision 1 gives more consideration to present conditions. "Slow progress" has an undesirable negative connotation that should be avoided | The scenarios and their names have been consulted with stakeholders during more than 2 years and discussed in the long term network stakeholders group . But the comments will be taken into account when naming the TYNDP 2016 visions.
GAS NATURAL | new and efficient but usually expensive technologies are considered in certain project definition, such as VSC in HVDC |  | Why are these expensive technologies the most convenient instead of using other less expensive? Justification would be needed | No technology is excluded a priori. The decision on the type of technology ( overhead line, DC...) depends on many, mostly geographical, factors: distance to cover, topographical characteristics of the crossed area, environmentally sensitive or urbanised ares; operational issues (e.g. synchronous interconnection or not) are also to be considered. TSOs resort to the least expensive solutions that can meet all the constraints. In fact these technologies, proved to be ones that allow to overcome the technical constraints faced in the particular case of FR-ES interconnection development. In addition, also the 3rd party promotors adopted the same type of technologies.
GAS NATURAL | Long term includes some more expensive projects, especially regarding interconnections, as some of them are submarine and include HVDC technology. |  | Why are these expensive technologies the most convenient instead of using other less expensive? Have alternative overhead lines been assessed? Why have they been discarded? | (see answer above)
GAS NATURAL | Only 15% of the CSW projects allow a GTC increase greater than 2000 MW. In this region, this type of GTC increase corresponds for instance to the Western Interconnection project between France and Spain | Only 15% of the CSW projects allow a GTC increase greater than 2000 MW. In this region, this type of GTC increase IS EASILY ACHIEVED for instance between France and Spain DUE TO THE EXISTING SCARCITY OF GTC | As probably any alternative would have the same results, because it is placed in the most critical CSW area, we would prefer to highlight the importance of solving the general investment gap between both countries | The original text is factual and specific and is not amended. TSOs investigated alternatives before concluding the project in the Biscay Gulf is the best option for increasing the interconnection capacity.
GAS NATURAL | the greater is the RES installed capacity in scenarios analysed, the greater is the economic benefit across Europe. This is a consequence of the replacement of conventional thermal generation by RES with zero marginal costs | This is a consequence of the replacement of conventional thermal generation by RES with zero marginal costs (RES SUPPORT SCHEMES, CRMS, BALANCING COSTS AND REINFORCEMENTS AT DISTRIBUTION LEVEL NOT HAVING BEEN CONSIDERED) |  | The methodology indeed explicitly considers variable operation costs.
GAS NATURAL | CSW results demonstrate that the project portfolio proposed for this region can be ‘profitable’ in a 10-15 years period, when comparing its costs to only to the socio-economic welfare | CSW results SUGGEST that the project portfolio proposed for this region can be ‘profitable’ in a 10-15 years period, when comparing its costs to only to the socio-economic welfare ACCORDING TO OUR ESTIMATES | TYNDP results could not be interpreted as a demonstration | ENTSO-E believes the TYNDP is a demonstration, and understands the following releases of the reports must be improved to be convincing in this respect.
GAS NATURAL | They are in line with the “EU 10% objective” which were stated in the conclusions from the EU Council of 20 and 21 March 2014 |  | The EC's European Energy Security Strategy (June 2014) has proposed extending from 10% to 15% in 2030. Maybe 15% should be used instead of 10% | The Conclusions of the Council of 23-24th October are expected to clarify this issue, and are not yet known when finalising the reports. In June the European Commission proposes to "extend the current 10% interconnection target to 15% by 2030 while taking into account the cost aspects and the potential of commercial exchanges in the relevant regions".
GAS NATURAL |  | NEW: As it has been noticed, interconnection between Spain and France is useful whatever the scenario under analysis is. In short, any interconnection capacity project would be proven helpful to solve the problem of transmission adequacy. Therefore, the study an comparison of alternatives is welcomed. |  | (see previous answers)
GAS NATURAL | This enhanced methodology enables to demonstrate strong conclusions: the projects of pan-European significance are key to make an energy transition in Europe | This enhanced methodology enables to INFER GUIDING conclusions: the projects of pan-European significance are key to make an energy transition in Europe |  | (see previous answers)
GAS NATURAL | Depending on the Vision, RES is expected to develop in large amounts by 2030, compared today's situation. | Depending on the Vision, RES is expected to develop in large amounts by 2030, compared today's situation. OBVIOUSLY, RES AND INFRASTRUCTURE DEVELOPMENT ARE INTERDEPENDANT. CONSIDERING THE CURRENT LEVEL OF RES GENERATION IN CSW, IF THERE IS NO SIGNIFICANT IMPROVEMENT OF INTERCONNECTIONS WITH THE EUROPEAN GRID, FURTHER RES DEVELOPMENT COULD BE LIKELY ENDANGERED AT NATIONAL LEVEL | National climate and energy objectives could be endangered if there is not an integration of generation. Lack of sufficient capacity of interconnction is seen by stakeholders as a barrier to the development of RES at national level | (see previous answers)
GAS NATURAL | basically they enable any RES surplus in one area to find outlets in a neighbouring one, and make market more resilient and less subject to price tensions | basically they enable any RES surplus in one area to find outlets in a neighbouring one | Market evolution is tensioned particularly by the penetration of low marginal operating cost technologies. Growing pressure on capacity markets will likely happen as the former energy only markets do not provide an adequate price signal for the provision of energy supply (a combination of energy and capacity) | The increased meshing of networks does enable more liquidity on markets, hence making them more resilient and less subject to price tensions. This does not prevent any tension to occur.
GAS NATURAL | In addition, in the 2030 horizon the development of carbon-free technology (RES, and carbon capture and storage mainly...) instead of fossil fuel technology without carbon capture and storage is the main key to reducing CO2 emissions in the power industry | Deleted | Market players will find key energy supply solutions to fulfill European targets | The statement is a fact, and does not deny the fact that market players will be key players to make it happen.
GAS NATURAL | In Vision 1, the consequence of the interconnection projects in the CSW region is an increase of 5 Mtons/y of CO2 in the region, and in Vision 4, a reduction of CO2 emission of 13 Mtons/y. | In Vision 1, the DEEMED IMPACT of the interconnection projects in the CSW region WOULD BE an increase of 5 Mtons/y of CO2 in the region, and in Vision 4, a reduction of CO2 emission of 13 Mtons/y HAS BEEN ESTIMATED. |  | Of course, all figures reported in the Regional Investment Plan Continental South West and in the TYNDP are results of the underlying analyses and scenarios considered. The proposed wording would make the text quite difficult to read.
GAS NATURAL | The new generation assets tend to be built farther to load centres than they are presently, and the transmission distance hence increase, and therefore the losses. | DELETED | As this is contrary to the European trend to foster distributed generation and demand side response measures, we would like to be cautious about that kind of statements. In any case,it is difficult to foresee where market players will find key places to develop most suitable solutions | The text will be maintained. As a matter of fact, RES sources are built first where potential is highest, and in large facilities more than triggered by the will to more decentralisation.
GAS NATURAL | It results in cheaper electricity, a more reliable and optimised supply but also, by essence it tends to enable longer power exchanges and induce therefore higher losses. | It tends to enable longer power exchanges which could induce therefore higher losses. | Electricity prices depend on many non-static variables. Increased competition optimises prices, but no conclusion on the resulting price can be inferred. The level of competition is not linked with the reliability of supply | The text will be maintained: electricity prices do depend on many parameters, under perfect market conditions that are considered on TYNDP frameword, but ceteris paribus, increasing exchange capabilities tend to give a better access to cheaper energy sources and on the long haul to result in cheaper bulk energy prices.
GAS NATURAL | This renewal of the generation infrastructure in the region and neighbouring regions is the major challenge for grid planning and operation | Grid planning and operation in duly time is the major challenge if it is deemed a renewal of the generation infrastructure in the region |  | The text will be maintained, as transmission developement is triggered by the renewal of generation.

## BS
Respondent Organization | Initial | Proposed | Comment | Confidentiality | ENTSO-E answer
Fortum Oyj |  |  | All bidding zone borders with regular congestions should be analysed in the Regional Investments Plans by CBA on alternative investments (possibly also on other borders) to reduce the congestions as far as feasible. Analysis should be done based on the whole regional (or even wider) market benefits, including increasing power transit possibilities and possible reduction of other, e.g. national, grid investment needs. |  | All presented results are based on regional studies and the emphasis is to get an overview of how the different areas interact with each other and creating a need for power transfer.
Fortum Oyj |  |  | Generation capacity assumptions (e.g. on fossil fuels and nuclear) seem to be partly based on official plans and not on realistic commercial profitability and feasibility for existing plants and new investments. |  | As a part of the scenario-process, the future is described through 4 different Visions. Each vision desribes a generation-mix, which is assumed to be realistic based on assumptions (political, economical etc.) within each vision. The goal of the visions is to investigate the cornerpoints of the possible future, not to forecast the exact future. The visions are developed based on wider European viewpoint and coherence and therefore may not take into account all national development aspects. This issue will be further improved in TYNDP 2016.
Fortum Oyj |  |  | There are still tendencies to make CBA from a national point of view. Additionally, if congestion income for TSOs is calculated as a positive component in CBA, the analysis would give distorted results. |  | Cost benefit analysis is performed for the region as a whole and all results will include all countries in the regional group. National results are not relevant to bring forward in a Regional Investment Plan and the analysis is not focused on generating such results.
Fortum Oyj | Figures 5 and 46 |  | In these figures there seems to be a fairly large east-west flow in Visions 1&2 in the picture, not accounted for in the text, and possibly based on too high assumptions on Finnish and Baltic generation and imports from Russia. This kind of conclusions holds some extra interest given the quite surprising deletion of the “Västlänken” project between Norway and Sweden and the further postponement of the new 400 kV line between northern Sweden and Finland. |  | The results confirm higher east-west direction flows in V1 and V2. The bottlenecks presented on figure 42 are based on situation 2030. Even though there appears large east-west flow in especially visions 1 and 2 based on the scenario assumptions, the grid presented is enough to handle that with the presented projects, so that Hasle corridor did not appear as bottleneck on 2030.
Fortum Oyj | Figures 9, 42, 44 and 45 |  | It is surprising that in these figures no possible bottlenecks are assumed for the Hasle cut (Southern Norway -Sweden) although this cut has in practice been regularly congested even when full capacity has been in use. |  | The bottlenecks presented on figure 42 are based on situation 2030. Even though there appears large east-west flow in especially visions 1 and 2 based on the scenario assumptions, the grid presented is enough to handle that with the presented projects, so that Hasle corridor did not appear as bottleneck on 2030.
Fortum Oyj | Project 111: 3rd AC Finland-Sweden north |  | Project 111 (3rd AC Finland-Sweden north) is further delayed, although this border is currently highly congested towards Finland, and the investment could give clear benefits both for power transit from northern Scandinavia to Baltics and Poland, export of increasing RES generation in northern Sweden and Norway, and for security of supply in Finland. It could also reduce investment needs internally in Sweden (project 126 and projects 93/895 and 104/398). Thus this project 111 should prioritised higher and the construction of it (and the connecting Finnish internal project 96) should be started at the latest in 2016 when the current internal Finnish grid reinforcement (project 64) is commissioned. |  | It is true that the border is quite congested right at the moment. Project benefits are assessed with TOOT methodology, which means that when assessing it has been assumed that the other projects have already been commissioned. It has not been assessed, whether a project diminishes a need for other projects. The benefits are assessed in a future situation, not in a current situation. The project has a positive effect especially for Finnish security of the system. It has been prioritised after Swedish internal connections due to large number of planned projects in Sweden.
Fortum Oyj | 11.1 Appendix 3 - Installed generation and demand in the Baltic Sea Region & 11.2 Appendix 4 - Flow and price differences of Visions |  | The high east-to-west flow in Vision 1 seems to result from big (9 TWh) net imports from Russia to Finland and from high fossil capacity and generation in Finland, combined with new nuclear power in Lithuania and Poland, as well as solid fossil fuel capacity in LV&LT. At least in a combination, all these assumptions are not realistic. Thus an opposite flow NO-SE-FI-Baltics-PL would be more probable. |  | The market model assumptions in Vision 1 will give high east-west flows whereas other visions will give different pictures of the market flows. It is important to span the possible future developments of the energy systems even if the solutions from each separate vision may seem unrealistic.
Vattenfall AB | figure 34 |  | Clarification, yearly average cost differences for UK and Nordic seems to differ between the color code per country and the difference over a hypothetic interconnector. |  | The yearly average marginal cost of an area and the average of hourly differences between the two different area marginal prices can be independent of each other. The results on the mentioned figure 34 illustrate that the yearly average price of UK and Nordic does not differ very much, but when looking at hourly differences the deviations are much larger in both directions.
Vattenfall AB | figure 42 |  | Clarification, loooking at the duration graph on page 63 (figure 50) it seems like there is also a market integration bottleneck between Nordics and continental. |  | This is partially true, especially in case of Vision 4. This is taken into account and it is expressed in chapter 6.1 Target capacities, where in Vision 4 an increased amount of interconnecion capacity is foreseen compared to vision 1. The crossection flows situation on figure 50 takes into account all planned interconnector capacities in place on the mentioned cross-section, called as reference case. Additional transmissioncapacities can be foreseen in Vision 4 but these are not studied as for other visions the proposed capacities were showing adequate results.
Nordenergi |  |  | Nordenergi, the joint collaboration between the Nordic associations for electricity producers, suppliers and distributors, welcomes the opportunity to comment upon the draft Ten-Year Network Development Plan for 2014. The work has been aspiring and the reports from the different regions are ambitious. Some of the reporting has clearly improved since the pilot TYNDP 2010, and Nordenergi’s comments should be seen in the light that we recognize the complexity of the issues involved, and we do see that the TYNDP 2014 is a further step in the direction of a transparent process for developing the regulated infrastructure of the European electricity market. Our comments concern the general documents, the Baltic and Nordic Sea regions of the TYNDP 2014. | confidential | -
Nordenergi |  |  | Infrastructure creates options. Compared to the vast sums expected to be invested in electricity generation, the infrastructure investments, however large, are small in comparison. But as long as the European power systems are fundamentally different, the option values created by building new infrastructure must be accounted for. In the Baltic and Nordic Sea regions, all bidding areas have their own characteristics. This fundamental truth makes it more likely that there will be too little infrastructure built than too much. |  | Different technical and regulatory background always complexify the set up of new projects. Yet, the TYNDP, with its focus on technical issues, leaving aside organisation and regulatory concerns, is efficient in identifying appropriate options for grid reinforcements. It is then up to authorities and operators locally to make them happen.
Nordenergi |  |  | The cohesion of Nordic and Baltic Sea markets suffers from various bottlenecks in the area. Although many important investments have been carried out as scheduled, other important investments have either been cancelled or delayed in to the future. Nordenergi encourages TSOs to further improve their cooperation in order to strive for a common and more coherent market. |  | ENTSO-E, and especially its Baltic Sea Regional Group, have investigated the influence of the project delays and according to results it can have really huge influence for the socio economic benefit as presented in Appendix 7 on figure 107 of the Regional Investment Plan. So we support the opinion.
Nordenergi |  |  | Our main point number 1: Many of the proposed projects are already delayed for several different reasons. We suggest that a simple list of the delayed projects is compiled and presented in the beginning of each regional plan with reasons for non-implementation/delay, as well as the actions which need to be taken. Main point 1. is elaborated as follows: It is commendable to have a planning to 2030. However, Nordenergi thinks that the plan should include more comments on the midpoint, 2023−2024. This should be made in connection with a simple list naming the delayed projects, the estimated change in finalization date and reason for the delay (e.g. permitting, technical problems, etc). |  | The full list of the projects and the status information is given in the table in Appendix 1, section 11.1.2. The table includes the project evolution information since TYNDP 2010 and also gives additional information of current status.
Nordenergi |  |  | Our main point number 2: The scenarios and their impact still need to be improved. In addition, the current scenarios give a false impression of precision, e.g. energy policy changes such as capacity markets will have a strong impact on merit orders and spot prices. Main point 2. is elaborated as follows: The scenarios hardly consider the macro-economic implications. For example, the energy intensive industry can only remain in Europe if the costs are comparable to the rest of the world. As the current discussions on the consequences of Energiewende shows (e.g. IHS 2014) a future with high cost choices for the European power system will have more far reaching impact on the demand side, than are foreseen in the current scenarios. The European electricity market is in a flux, and depending on decisions on continuing renewable energy supports systems, the introduction of capacity markets in some countries, balancing responsibility for all generation in the system or not and progress in the intraday and balancing markets integration or not, the value of cross border capacity between countries and investment in transmission capacity can be highly affected. Nordenergi thus encourages ENTSO-E to also include some political cases that lead to changes in the electricity market, prices and trade patterns in further scenarios and assess how that impacts on investment incentives. |  | Scenario building is a difficult science where ENTSO-E asked their stakeholders' for support during the whole process of preparing the TYNDP scenarios, from Spring 2012 to Autumn 2014. The selection and appraisal of macroeconomic parameters in all scenarios have been discussed. The process restarts this Autumn until next Summer for the TYNDP 2016 scenarios. Most interested stakeholders can join the works of the Long term network stakeholders groups for a more active involvement and contribution.
Nordenergi |  |  | Our main point number 3: Stakeholder representation in both the European and regional planning works needs to be improved. Main point 3. is elaborated as follows: The idea of a Stakeholder development group is very good. The strengthening of the future group to represent all generation interests is a step into the right direction. Additionally, it is important that the stakeholders also can represent the different European regions, in our view, as there is currently regional divergence in regulation and design of markets through for example the introduction of national capacity markets in some but not all regions. In addition we suggest that similar stakeholder groups are installed at the level of the regional investment plan, since that would allow a better access to the regional expertise and detailed knowledge of more local/regional actors. Finally, we propose that the groups can invite in experts from the universities or other countries such as the New York ISO to draw on their expertise when needed. |  | Stakeholders' involvement can certainly be improved. The next move is ensuring an active participation in the framework of the Long term network development stakeholders group. Participation can be arranged from a distance. Most important is actual contribution from the stakeholders with respect to scenario inputs or modelling pieces and acknowledgement for our joint works. Outsider experts such as universities can already now be invited to present issues on their expertise to the LTND SG meeting. ENTSO-E needs others' expertise but has not identified all possible interested parties, nor can force anybody. Beyond the LTND SG, regional workshops and consultation will still be regularly organised during the process, where stakeholders can give input and take part in the process.
Nordenergi |  |  | Our main point number 4: Nordenergi thinks a ranking of the projects following a transparent methodology would be helpful. In addition Nordenergi thinks it needs to be clarified how and why projects are clustered. Clustering decreases the transparency. Main point 4. is elaborated as follows: Clustering of projects obstructs transparency in selection criteria. The CBA methodology should be based on individual assessments where the cost of each individual transmission project is valued against the assessed benefit of that given project. Such an assessment is needed to secure a transparent build-out of the grid. Clustering should only be valid in cases where a ‘sub-project’ is a clear precondition for a ‘mother-project’. The current CBA clustering rules are too superficial. Additionally, it should be possible to rank the projects with respect to the value achieved and the cost for the project. |  | ENTSO-E strived to give enough information based on the CBA methodology for the stakeholders to make their ranking, as everyone would weight criteria differently. Clustering rules were tightened in the CBA methodology compared to the TYNDP 2012 based on stakeholders' feedback. Clustering rule is now that the investments are supporting same grid transfer capacity and that the effect should be at least 20% of the total capacity increase. In addition the investments should be not futher apart than 5 years. Typically a cross-border interconnector is clustered with the needed internal reinforcements needed to achieve the wanted interconnection capacity.
Nordenergi |  |  | Our main point number 5: In-depth reporting on the bottlenecks is missing. Main point 5. is elaborated as follows: The section on bottleneck locations and typology is too superficial. The bottlenecks are the fundamental issue that is being addressed by the TYNDP, and Nordenergi encourages the TYNDP to portray a detailed description of individual key bottlenecks and furthermore be much more specific in the report in regards to assessing to what extent the suggested TYNDP investments will mitigate the given bottlenecks and on which timescale. This way a much needed transparency on the individual key bottlenecks is secured and ACER and the NRAs would have a better understanding of which bottlenecks are addressed to what extent and on which time scale, leaving the NRAs a better basis for assessing when further action in form of changing the congestion management regime is needed. |  | The TYNDP is trade off between a synthetic overview and detailed information. Bottlenecks are located on boundaries; and the analysis of the bulk power flows through the boundaries compared to the boundary capacity enable a characterisation (frequency, magnitude) of the bottleneck. Mostly, such results are displayed in the Regional Investment Plans as monotonous (or not) hourly load curve (see for instance Regional Investment Plan Baltic Sea, § 4.5)
Nordenergi |  |  | Modelling: As is shown in the tables in Appendix 3, Baltic Sea region TYNDP, all countries will more or less install a huge overcapacity. Alas, the numbers are not easily comparable as the generation is reported in MW and consumption in TWh. This can easily be resolved though as figure 26 clearly indicates that there are energy numbers available per region, and per technology. With regards to supply and demand balance, the numbers reported do indicate that ENTSO-E foresees that the current German conundrum will remain unsolved. This brings us to an extremely serious and potentially devastating modelling issue. For example, figure 28 compares the different average marginal costs between the regions. As a long run trading projection this only works if the marginal costs include the full costs, in so far that the capital costs are included, i.e. the long run marginal costs. Now, if some areas decide to remunerate capital through regulated mechanisms such as capacity mechanisms, the energy prices will be depressed in these areas and the flows may go counter to what real long run marginal costs would demand. This can create serious issues for cost efficiency and long run investment in transmission capacity and generation capacity in neighbouring countries, which are similar to the consequences of price dumping cases. The chapter in price differences and trade flows therefore only makes sense in regions where a continuing energy-only market is probable. Nordenergi regrets that these questions are not addressed for example in an additional sensitivity case or test to the main scenario. |  | The production capacities presented in the Appendix 3 are presenting the installed capacity. The produced energy is then a result of the market model runs based on the visions assumptions, and the balance can be seen on the cross-border energy flows as presented on Appendix 4. There are restrictions on using the market models, as stated they assume energy-only market, perfect competition, they only take into account marginal costs, not captial costs. It is worth to note that these presented average marginal costs do not represent a full cost, nor do they try to represent a true market price.
Nordenergi |  |  | Ranking of projects: In addition, the plans do not have any ranking or priority of the different projects. Indirectly this could be said to be shown by the value of Social Economic Welfare (SEW) for each project, i.e. projects with the highest SEW should be implemented first etc. However, for many projects there is a large uncertainty regarding e.g. investment costs and hence the calculated SEW. Is the SEW calculation model and assumption identical for all projects or is it based on national calculations and assumptions? Different methods for calculation and evaluation of input data will not only decrease the possibility to compare projects but make any comparison almost impossible. In our view it is important to balance the necessity of keeping every project’s unique costs and benefits with an overall pedagogical aim of making the projects as comparable as possible in order to assess priority between them. Seemingly the TYNDP is based on national plans and a process to evaluate common European investment needs. However, even with the given plan there are still large price differences in the system. This raises the question if the proposed projects actually give the highest SEW for Europe as a whole or if there still are projects that should be included into the plan. As an example the EU has set a goal to continue the market integration process in Europe. The TYNDP analysis show large price differences between the Nordic countries and Continental Europe for all the different visions, even when large planned interconnector (IC) projects are included. ENTSO-E should therefore in our view analyze a further increase of IC capacity between these areas and study and evaluate additional IC projects. |  | (split into 2 comments/answers) - The goal of the CBA is to provide the means for stakholders to sort and rank the projects, not anticipating their preference. - The TYNDP aims at identifying the envelop of projects that can be required to match all possible scenarios. The assessment of each project shows in which respect the project is useful in each considered scenario. The TYNDP 2014 stresses however, that the set of projects of pan-European significance presented in the report must be complemented to meet the Vision 4 scenario.
Nordenergi |  |  | CBA methodology: The CBA methodology and the subsequent possibility to conduct a cross border cost allocation are the key enablers for the development of a European grid infrastructure. Nordenergi would like to emphasize the importance of the work on and the timely finalization on the CBA methodology. The cost-benefit calculations are also sensitive to several assumptions. Currently it is not obvious whether the SEW calculation is based on national or European methodology i.e. whether the numbers are comparable at all. The cost-benefit calculations are also sensitive to several assumptions, none the least, the choice of what is the relevant area that the calculations cover. TSOs look at different areas, with some looking primarily at national benefit and costs for TSOs, while others also look at a wider regional or European perspective. When stated that the TSOs in the TYNDP 2014 are looking at “optimum solutions”, these solutions must be firmly put in the context of assumptions and national restrictions. Given that the infrastructure packages recognize the need to facilitate the realization of projects with benefits in third countries, Nordenergi would encourage ENTSO-E to publish the CBA results of analyzed projects including cross border distributional effects to facilitate a more open discussion on the realization of affected projects. Nordenergi would also encourage a more open discussion on how the diversity of organizational structures of the TSOs, and the owners instructions, affect the decision to go ahead, or as it were, cancel decisions. Nordenergi would like to point out that a transparent decision making process and access to the assumptions and data that lead to a decision are especially important the more uncertain the future is. In our view the major benefit of a scenario approach chosen by the TSOs is therefore the discussion they stimulate, i.e. what kind of development is reasonable under different assumptions about the future. Given that grid building and planning is also affected by highly specific local conditions, some of the discussion should be even more decentralized, as in for example the work with Svenska Kraftnät’s grid plan for 2025 where Swedish actors could give a more detailed view on a line-by-line, project-by-project basis. Transparency would also ensure certain coherence between national and European grid scenarios. The table of cost/benefit results for each project gives a fairly rough estimate of the costs but is hard to find the aggregate estimates of the benefits. This is clearly difficult in the case of infrastructure. However, a cost and benefit analysis should clearly include both. For example, one of the projects in the Nordics discussed since 1989, the strengthening of the Hasle cut was surprisingly (for the market participants) cancelled or delayed indeterminably with reference to unclear benefits. There could be some improvement of the reporting, for example by given the best and the worst sums per project. Several projects operate with large differences in possible/anticipated investment costs, e.g. NSI and NorthConnect etc. This creates a large uncertainty regarding potential future costs and SEW. The reason for these rather large uncertainties should be explained and if possible reduced. In addition, a search for the discount rate used in the calculations yields no result. Discount rates are one of the key factors in modern cost benefit analysis and thus can play a key role for the overall profitability of a project. Loss variations are deemed as a benefit. However, we believe that the benefits regarding losses are in reducing them and not in the variations. Developing new generation far away from load may create new bottlenecks on the way to the consumer, long transmission lines and power transport hence, increasing losses. In what way does the TYNDP take into consideration pricing signals in the market and through tariffs in order to facilitate new generation is located in order to reduce bottlenecks, network investment needs and losses? |  | Regional groups of ENTSO-E have performed the CBA assessement of the projects based on the common CBA methodology. It has been recognized already some improvement needs for the methodology. The assessment has also been performed against the common pan-european visions, so the results are comparable. The tools used are not the same on each region. The results reported are either the pan-european benefits/effects or regional benefits/effects, where it has been deemed that the effect of the project is neglible in the other regions. The national benefis have not been assessed during the TYNDP and Regional investment plan process. ENTSO-E has assessed all the projects in four visions just to cover some of the uncertainties of the future system evolution. All the CBA indicators are shown in the cost/benefit tables. For losses, projects can either increase or diminish losses, this is the reason why the indicator is called losses variation.
Nordenergi |  |  | Benefits of RES integration, CO2 reduction and Security of supply: In the CBA evaluation, integration of RES seems to be one of several benefits that are taken into account. Even though reaching RES targets is important, we cannot see that introduction of specific production technologies gives a social economic benefit in itself. Especially if these technologies trigger other expensive investments in order to secure Security of Supply and a stable grid. Thus the measure must to some extent be coupled to some target achievement decided on beforehand. In addition, it is somewhat difficult to see how increased infrastructure can change the overall CO2-emissions if not a direct link is made to EU’s CO2-cap. Transmission may lower the cost of using for example nuclear or wind power by enhancing the trade of electricity by these sources. However, that trade in itself does not affect the CO2-cap which is set by a regulatory decision by the EU Commission. Security of supply (SoS) is one of the most important issues in the TYNDP and one of the main drivers for European network development. However, in our opinion the TYNDP does not in a sufficient way address and analyze the SoS issues. Differences between countries regarding production technology and access to flexibility and reserves, and how these different technologies are interconnected and utilized in Europe is of imperative importance when addressing SoS. In our view it is therefore important that ENTSO-E addresses these issues vigilantly and improves the TYNDP to this regard. A lot of the projects (disregarding the subsea projects) are still planned as overhead lines. However, the environmental disturbance of overhead lines as compared to underground cabling is large, which can lead to delayed permitting procedures. Thus, even if cabling may be more expensive it may gain time, and advance the benefits of a project time-wise. Hence Nordenergi proposes that projects that are delayed due to environmental resistance traceable to overhead lines, some comment to the effect on how much benefits that are lost for every year of delay would be an improvement in the TYNDP. In addition the TSO should give an assessment of how much more mitigating actions such as cabling would cost. Armed with this it could be possible to discuss whether the more expensive alternative of cabling is worth investigating. A fair amount of projects in the Baltic Sea Region has been delayed or in the worst cases cancelled. To increase political pressure on the national/local authorities, Nordenergi thus proposes that relevant local/regional/national authorities are invited to the respective stakeholder groups. A final comment is on the decision to move the PCIs to the appendixes and annexes. For the less initiated reader it may appear as those projects have less socioeconomic value than those supported by ENTSO-E. This is of course not so. Thus Nordenergi proposes that these projects are given a more prominent place in the report. |  | ENTSO-E has already noted that the CBA methodology has some needs for improvement especially concerning SoS assessment. RES has been taken in as one CBA indicator due to the European goals as well as the CO2 indicator. CO2-cap has not been included on the assessment, rather the actual CO2 emissions in the various visions.
Finnish Energy Industries |  |  | Introduction Finnish Energy Industries (ET) welcomes the opportunity to comment upon the draft Ten Year Network Development Plan (TYNDP) for 2014. TYNDP 2014 is the third TYNDP. We have seen an improving process and the TYNDP 2014 package provides a good overview on the grid investments needed in Europe and the methodology how to assess these needs. Our comments concern primarily the Regional Investment Plan Baltic Sea and where applicable, the Full Report. | confidential | -
Finnish Energy Industries |  |  | Scenarios It is unclear how the political interventions are accounted in scenarios. However, it seems that ENTSO-E would have included some Capacity Support Systems in the scenarios. All politically decided support systems include risks; political risks, operational risks and functionality risks. Indeed, it is uncertain how decided or planned support schemes affect the investments and how robust they are politically. Compared to the vast sums expected to be invested in electricity generation, the infrastructure investments, however large, are small in comparison. |  | The base assumption on the scenarios was that countries are adequate on power. This in some cases may not in reality be possible without a cpaacity mechanism, this is true. ENTSO-E did not however specifically address the issue of capacity mechanism during TYNDP process
Finnish Energy Industries |  |  | Stakeholder interaction We welcome the idea of a Stakeholder development group. We suggest that similar stakeholder groups are installed at the level of the regional investment plan, since that would allow a better access to the regional expertise and detailed knowledge of more local/regional actors. |  | At this time ENTSO-E is not planning to organise stakeholder groups regionally. ENTSO-E and the regional groups strive to improve the stakeholder commitment to the TYNDP and REGIP process even further. At the moment ENTOS-E plans to have regional workshops on proper times during the process where also regional stakeholder can bring their expertise to the process. We take this suggestion for further thinking.
Finnish Energy Industries |  |  | Execution and follow-up of investment plans The TYNDPs have improved, but their execution measures remain poor. Too many important grid enforcements have been either cancelled or delayed. We urge ENTSO-E to take a closer look in the reasons and make a work plan how to tackle these deletions and delays. The TYNDP 2016 should include in each Regional Plan a section where the reasons for delays of individual grid projects are listed and complemented with action plan how the project responsible TSOs area planning to tackle the issues having led to delay. |  | ENTSO-E follows the status of the projects every year, in odd years ENTSO-E has prepared a separate report on the status of the presented projects.
Finnish Energy Industries |  |  | Investments in the Baltic Sea Region The investments plans for the coming decade are the core content of TYNDP. We regret to see, that the investments needs remain under-estimated compared to the needs. The cohesion of Nordic and Baltic Sea markets suffers from various bottlenecks in the area. Although many important investments have been carried out as scheduled, other important investments have either been cancelled or delayed in to the future. We encourage TSOs to further improve their cooperation in order to strive for a common and more coherent market. There seems to be a fairly large east-west flow in Visions 1 and 2, possibly based on too high assumptions on Finnish and Baltic generation and imports from Russia. These kinds of conclusions holds some extra interest given the deletion of the “Västlänken” project between Norway and Sweden and the further postponement of the new 400 kV line between northern Sweden and Finland. Hence, we draw the attention of ENTSO-E to these two obvious faults in Regional Investment Plan Baltic Sea. The important grid improvement Västlänken has been cancelled and the new AC line to strengthen capacity between Finland and Sweden post-poned. |  | Even though there appears large east-west flow in especially visions 1 and 2 based on the scenario assumptions, the grid presented is enough to handle that with the presented projects, so that Hasle corridor did not appear as bottleneck on 2030. In visions 3 and 4 the assumptions are such that the flow from Russia is not so large. RGBS prepared also a regional sensitivity based on Vision 3 where the flow is more from west to east as commented.
Finnish Energy Industries |  |  | The Sweden 1 − Finland (SE1−FI) 400 kV AC line has three significant benefits possibly not accounted in planning. The need for the new interconnector is obvious. There is currently a structural bottleneck between SE1 and FI which restricts the free flow of electricity and causes continuously welfare losses for Finnish consumers and Swedish generators. First, the project will benefit the whole Baltic Sea Region at quite low costs. The benefits for the project should be calculated for the whole region taking into account that it would also reduce needs for other investments. Examples of benefits are increased capacity to transport electricity from northern Norway and Sweden southwards as more pressure on the Swedish grid capacity would result from the increasing of wind power in SE1 and NO4. The strengthening of SE1−FI capacity means that power can be transmitted from northern Sweden and northern Norway through Finland and Baltics to Poland and southern Sweden by utilising the already existing and coming interconnectors. This will also be aligned with the concept of using hydropower to accommodate a continental shift to reduce fossil-fired generation. Fingrid would get more of the needed security of supply as grid import reserve, after 1600 MW Olkiluoto 3 generator is taken into operation. Second, the new interconnector will help Svenska Kraftnät while it enforces the internal Swedish connection. Without adequate transmission capacity SvK may be forced to diminish transmission capacities in areas where it will be performing grid upgrades. This is likely to worsen the cohesion of Nordic market and create additional welfare losses for the whole Nordic-Baltic market. Third, Fennoskan 1 cable suffers from aging. As the reliability of this cable weakens, new interconnectors are needed even more. Having more capacity between Finland and Sweden will ease the situation, when Fennoskan 1 cable needs to be replaced. We urge the TSOs to rethink the timing of this interconnector as we find that the building should start ASAP. |  | It is true that the border is quite congested right at the moment. Project benefits are assessed with TOOT methodology, which means that when assessing it has been assumed that the other projects have already been commissioned. It has not been assessed, whether a project diminishes a need for other projects. The benefits are assessed in a future situation, not in a current situation. The project has a positive effect especially for Finnish security of the system. It has been prioritised after Swedish internal connections due to large number of planned projects in Sweden.
Finnish Energy Industries |  |  | Västlänken and the solutions for to tackle congestion in Hasle have been notified for almost 60 years, but unfortunately the project still waits to be executed. We would like to draw ENTSO-E’s attention to the fact, that due to the restriction in Southern Norway, Statnett continuously protects the people in Oslo region from high electricity prices at the cost of market’s functioning and the people in Sweden, Denmark and Finland. Whereas the TYNDP 2014 takes into account the needs to transfer electricity in the North−South direction, it seems to have forgotten the important West−East direction. |  | Even though there appears large east-west flow in especially visions 1 and 2 based on the scenario assumptions, the grid presented is enough to handle that with the presented projects, so that Hasle corridor did not appear as bottleneck on 2030. In visions 3 and 4 the assumptions are such that the flow from Russia is not so large. RGBS prepared also a regional sensitivity based on Vision 3 where the flow is more from west to east as commented.
Eurelectric |  |  | The table on cost/benefit results for each project gives a fairly rough estimate of the costs but fails to provide an aggregated estimation of the benefits. This is particularly relevant with respect to one of the projects in the Nordics discussed since 1989, the strengthening of the Hasle cut (project 67/402). Surprisingly for the market participants, this project has been cancelled or delayed indeterminably with reference to unclear benefits. Probably higher later benefits (when older Swedish nuclear units are decommissioned and the Hansa PowerBridge, project 176, is realised) have not been discussed. There could be some improvement of the reporting, for example by providing minimum to maximum ranges per project. In addition, a search for the discount rate used in the calculations yields no result in spite of the fact discount rates are one of the key factors in modern cost benefit analysis and thus can play a key role for the overall profitability of a project. |  | The benefits are assessed against four different visions, which should give a range of the benefits for the projects. Benefits are also assessed with TOOT methodology which means that the other projects are assumed to be operational in the assessed situation.
Eurelectric |  |  | A lot of the projects (notwithstanding the subsea projects) are still planned as overhead lines. However, the environmental disturbance of overhead lines as compared to underground cabling is large. A fair amount of the projects proposed are delayed, none the least because of the lengthy permitting procedures. Even if cabling may be more expensive, it may gain time and advance the benefits of a project time-wise. In case of exceptional delays in projects mentioned in previous TYNDP for example, cabling could be evaluated. |  | While planning the projects TSO's are searching for the best technical and economical solution. When cables are a technically feasible solution their economical viablility can be assessed.
Eurelectric |  |  | In, Figure 5 of the executive summary, there seems to be a fairly large east-west flow in Visions 1&2 in the picture, not accounted for in the text and possibly based on too high assumptions on Finnish and Baltic generation and imports from Russia. This kind of conclusions holds some extra interest given the quite surprising deletion of the “Västlänken” project between Norway and 12 Sweden and the further postponement of the new 400 kV line between northern Sweden and Finland. Another issue connected to that area are the dynamic stability problems on the Oslo fjord cut (west-east), when there are simultaneously exports to Sweden and high load in the Oslo area. HVDC light technology might improve these stability issues and could lead to higher available transmission capacity between NO1 and SW3. It could be interesting to take those types of measures into consideration as well. And finally, the large east-west flow as mentioned in Figure 5 in Vision 1 seems to result from big (9 TWh) net imports from Russia to Finland and from high fossil capacity and generation in Finland, combined with new nuclear power in Lithuania and Poland, as well as solid fossil fuel capacity in LV&LT. At least in a combination, all these assumptions are not realistic. Thus an opposite flow NO-SE-FI-Baltics-PL would be more probable. |  | The bottlenecks presented on figure 42 are based on situation 2030. Even though there appears large east-west flow in especially visions 1 and 2 based on the scenario assumptions, the grid presented is enough to handle that with the presented projects, so that Hasle corridor did not appear as bottleneck on 2030. In visions 3 and 4 the assumptions are such that the flow from Russia is not so large. RGBS prepared also a regional sensitivity based on Vision 3 where the flow is more from west to east as commented.
Eurelectric |  |  | In the discussion of capacity allocation methods, one of the proposed methods is the flow based allocation method. If the Nordic synchronous zone was to adopt the flow based allocation methods there would be more than 180 critical branches, i.e. some kind of bottlenecks. The resolution of figure 42 does not in any way convey the kind of necessary resolution for the stakeholders to participate in a serious discussion on other possible projects than those proposed by ENTSO-E. It is especially surprising that in this figure no possible bottlenecks are assumed for the Hasle cut (Southern Norway -Sweden) although this cut has in practice been regularly congested even when full capacity has been in use. |  | Flow based market models were actually used during the regional study process (see ch. 2.3.1). More detailed flow based market analysis will be done in future releases of TYNDP after flow based models are fully implemented. In TYNDP 2014 most critical crossborders were investigated in 2030 analysis and with the possible future projects in RegIP 2014 implemented. Due to the regioonal scope the study results presented in the report are generalized, showing flows on main boundaries - between the countries and subregions (Nordic, Baltics, CE). The reference scenario includes interconnections assessed with the TOOT methodology. The results confirm high east-west direction flows in Visions 1 and 2 but the grid presented is enough to handle that with the presented projects, so that Hasle corridor do not appear as bottleneck in 2030 visions.
Eurelectric |  |  | There should be at least two further projects to consider in an effort to manage the flows that occur when countries around the Baltic Sea are increasing their share of wind power and solar power: Sweden - Poland cable 2 and Sweden - Lithuania cable 2. Both cables should be in operation by 2030. But the TYNDP does not refer sufficiently to these needs, as a result of increasing variability and increased peak generation. |  | RG Baltic Sea did study some alternative connections between Sweden and other countries. The most beneficial one has been included to the list of projects.
Eurelectric |  |  | Some of the maps are not legible. Therefore, links are provided to high resolution versions of the maps and figures where this is the case, e.g. Figure 51. In addition, Figure 40 is unreadable and should be replaced by a table and Figure 41 should be complemented by a table of actual use of the connections. Figure 52 includes a project between Denmark and Poland (project 166, under consideration for year 2030), but this project is not included in the Figure 5-2 in the Communitywide TYNDP report. It is not quite clear how cross-border projects are selected for Figure 5-2 to have pan-European significance. |  | Readability will be improved, and the situation with the named projects will be checked.
Eurelectric |  |  | Project 111 (3rd AC Finland-Sweden north) is further delayed, although this border is currently highly congested towards Finland, and the investment could seem beneficial for both power transit from northern Scandinavia to Baltics and Poland, export of increasing RES generation in northern Sweden and Norway, and for security of supply in Finland. It could also reduce investment needs internally in Sweden (project 126 and projects 93/895 and 104/398). Thus another fast evaluation of project 111 should be prioritized (and the connecting Finnish internal project 96) as the current internal Finnish grid reinforcement (project 64) is commissioned in 2016. |  | It is true that the border is quite congested right at the moment. Project benefits are assessed with TOOT methodology, which means that when assessing it has been assumed that the other projects have already been commissioned. It has not been assessed, whether a project diminishes a need for other projects. The benefits are assessed in a future situation, not in a current situation. The project has a positive effect especially for Finnish security of the system. It has been prioritised after Swedish internal connections due to large number of planned projects in Sweden.

## NS
Respondent Organization | Initial | Proposed | Comment | Confidentiality | ENTSO-E answer
Element Power | B3 RES integration Vision 2 & 3 |  | in Vision 2&3 Project 106 Ireland GB Interconnector has 110-470GWh of RES wheres Greenwire Project 185 has 5.1 to 8.8GWh of RES. How is this when both interconnect the same markets? | Non-confidential | ENTSO-E has updated the table of projects for the final TYNDP report
NorthConnect KS | [Ch.11.1, Project 190] Comment on the SEW: the results for NorthConnect (Norway-Scotland) is the same as for project 110 NSN (Norway-England), this because Great Britain in the analysis is modelled as one node. In practice there would have been price-differences between England and Scotland, making the values different for the two projects. Additional NorthConnect is planned realized after NSN, which will make this project NorthConnect less valuable. | Comment on the SEW: the results for NorthConnect (Norway-Scotland) is the same as for project 110 NSN (Norway-England), this because Great Britain in the analysis is modelled as one node. In practice there would have been price-differences between England and Scotland, making the values different for the two projects. | The statement that NorthConnect is less valuable than NSN needs to be removed. In relation to project lifetimes, NorthConnect will be operational very soon after NSN and remain operational over more or less the same time period. From a pan European socioeconomic view, Entsoe-E's TYNDP should consider the total value of capacity, not assign value to interconnectors on the basis of which comes first. In addition, Entsoe-E acknowledges that the different connection points between NSN and NorthConnect are not represented in the modelling, and thereby possible differences in prices (and value) are not represented. Different connection points would reduce the limiting effect of value that one interconnector has on the other. Furthermore, other new TYNDP interconnector projects will strengthen the indirect connection between Norway and southern GB through the Continent. Analysis conducted for NorthConnect by RedPoint Energy and Thema Consulting Group indicates a greater socioeconomic value of connecting to Scotland rather than England, based on an assumption that Scotland will have a larger proportion of wind power production. All in all, the argument of stating that NorthConnect is less valuable than NSN is far too strong, given the limitations of Entsoe-E's modelling. One could even argue that the value of RES integration of NorthConnect is higher than that of NSN, as connection to Scotland facilitates the wind power investments potential by connection to hydro energy storage areas, but again, this difference is not reflected in Entso-E's modelling either. Finally, the cable length of NorthConnect is shorter than NSN, reducing the investment cost. | Non-confidential | The report is amended accordingly.
Element Power | B3 RES integration Vision 2 & 3 |  | in Vision 2&3 Project 106 Ireland GB Interconnector has 110-470GWh of RES wheres Greenwire Project 185 has 5.1 to 8.8GWh of RES. How is this when both interconnect the same markets? | Non-confidential | ENTSO-E has updated the table of projects for the final TYNDP report
Agder Energi | Page 153: Comment on the SEW: the results for NorthConnect (Norway-Scotland) is the same as for project 110 NSN (Norway-England), this because Great Britain in the analysis is modelled as one node. In practice there would have been price-differences between England and Scotland, making the values different for the two projects. Additional NorthConnect is planned realized after NSN, which will make this project NorthConnect less valuable. | Comment on the SEW: the results for NorthConnect (Norway-Scotland) is the same as for project 110 NSN (Norway-England), this because Great Britain in the analysis is modelled as one node. In practice there would have been price-differences between England and Scotland, making the values different for the two projects. | The statement that NorthConnect is less valuable than NSN needs to be removed. In relation to project lifetimes, NorthConnect will be operational very soon after NSN and remain operational over more or less the same time period. From a pan European socioeconomic view, Entsoe-E's TYNDP should consider the total value of capacity, not assign value to interconnectors on the basis of which comes first. The chosen methodology (TOOT) is based on this approach. In addition, Entsoe-E acknowledges that the different connection points between NSN and NorthConnect are not represented in the modelling, and thereby possible differences in prices (and value) are not represented. Different connection points would reduce the limiting effect of value that one interconnector has on the other. Furthermore, other new TYNDP interconnector projects will strengthen the indirect connection between Norway and southern GB through the Continent. All in all, the argument of stating that NorthConnect is less valuable than NSN is far too strong, given the limitations of Entsoe-E's modelling. One could even argue that the value of RES integration of NorthConnect is higher than that of NSN, as connection to Scotland facilitates the wind power investments potential by connection to hydro energy storage areas, but again, this difference is not reflected in Entso-E's modelling either. Finally, the cable length of NorthConnect is shorter than NSN, reducing the investment cost. | Non-confidential | The report is amended accordingly.
Element Power | Comment on the RES integration: avoided spillage concerns RES in Ireland mostly. | Comment on the RES integration. As well as connecting Ireland and GB, Greenwire provides up to 3GW transmission capacity for RES generation in Ireland connecting to the GB. | More space to explain the Greenwire project would be helpful as it is more complex. Interconnection between GB and Ireland is only part of the project. | Non-confidential | A lot of projects if not all deserve more space, so that a stringent synthesis is required for each of them.
Jonny Hosford | This comment relates to Figure 3.17: Bulk Power flows (5% (green) and 95% percentiles (red))- Vision 1 |  | Figure 3.17 with red and green arrows to depict the 5% lowest and highest flows on each border seems to be of limited use and is not easy to understand. It is stated that this picture “shows that most of the DC interconnections are operating at full power for these percentiles”. Take for example the GB-NO border. Does the 95% percentile (red) arrow at 1400MW mean that for 95% of the year the flow is greater than or equal to 1400MW in the direction from GB to Norway? In fact there are two 1400MW interconnector projects proposed across this boundary (NSN and NorthConnect). Are both these interconnectors thought to be flowing 95% of the time in the direction GB to Norway? Taken together with the other arrows across GB borders, this result would appear to contradict the conclusions elsewhere in the report that GB is expected to be a net importer from Continental Europe / Nordic countries in Vision 1. Furthermore the resolution of the picture is not adequate to make out all the MW figures portrayed. Please could ENTSO-E provide clarification of the correct way to interpret the picture, or preferably provide an alternative presentation such as graphical flow duration curves of the type shown in figure 3.18 for AC boundaries? | Non-confidential | The report is amended accordingly.
Jonny Hosford | This comment relates to Section 4.4 Bulk Power Flows in 2030 |  | With respect to the Visions 1 to 4 it is not clear which transmission reinforcement projects (including interconnectors) have been included in the reference network/market studies. In its assessment of market integration bottlenecks (figure 4.5 page 59) ENTSO-E shows the boundaries related to market integration and the bulk power flows that trigger grid development in 2030 under visions 1 and 4. With respect to the boundary between Great Britain and Continental Europe / Nordic countries, the bulk power flows are shown as amber (4,500 – 10,000MW) in Vision 1 and red (≥ 10,000MW) in Vision 4. In the period up to 2030 there are collectively over 10GW of new interconnection projects proposed between Great Britain and Continental Europe/Nordic countries. For the purposes of its network and market studies does ENTSO-E assume that all of these projects are built in both visions 1 and 4? If so this would tend to imply that in Vision 1 there is likely to be underutilised interconnector capacity (unless ENTSO-E leaves out certain proposed interconnector projects from its reference case), while in Vision 4 there may yet be inadequate installed interconnector capacity (leading to generation curtailment – unless ENTSO-E prescribes additional transmission reinforcement to address the bottlenecks). In order to provide clarity please could ENTSO-E clarify for each of Visions 1 to 4: (1) Which discrete hours of the year have been selected as the representative hours (planning cases) used in network and market studies, and what duration has been ascribed to each to form a representative year? (2) What is the magnitude and direction of cross boundary transfer flows (MW) between Great Britain and its neighbouring countries corresponding to these reference planning cases? (3) Which TYNDP projects are included / excluded from these reference planning cases? (4) Please could ENTSO-E put an upper bound on the target capacity currently expressed as >10,000MW; (5) Where transmission capacity is still inadequate across this boundary please could ENTSO-E indicate (at least conceptually) the nature and location of transmission reinforcement that would be required to address the bottlenecks – for example are more interconnectors required or is the bottleneck associated with other types of constraint such as voltage / stability? | Non-confidential | 1) The market simulations are made for each hour of a whole year, i.e. 8760 hours. The selection of planning cases for the network studies was made based on an in debth analysis, which is described in section 2.4 of the RegIP RGNS 2) The flow and direction of the flows between Great Britain and its neighbours depends on the visions and planning cases investigated. Very generally, the net flows in vision 1 and 2 are from Continental Europe to Great Britain, whildst for vision 3 and 4 the net power flows are from Great Britain to Continental Europe. 3) We used the TOOT methodology – which means, ALL projects are included in the reference case, and the project which is investigated is taken out. Indicators are based on difference between these two simulations. See description in chap-ter… 4) "Beyond 10000" is 10000-15000 MW in our computations, but for Vision 4 where assessing the upper bound is still a pending issue for some borders, and can be much higher. Hence the chosen legend. 5) Vision 4 proved to be more ambitious than expected, the adressment of this is foreseen in the next release of the RgIPs by Summer 2015.
Jonny Hosford | This is a general comment in relation to how the "C1 Estimated Cost" parameter is resported in the project specific assessment tables |  | Where investment items are grouped together to form a clustered project, it would be more helpful/transparent if estimated investment costs for each item were quoted separately rather than a single investment cost representing the sum of all investment items in the cluster. | Non-confidential | Cost figures are displayed according the the CBA methodology. Displaying costs per investment is an option for the next TYNDPs, but the issue proved tricky with legal issues complexifying the matter.
Jonny Hosford | Project 110: Norway - Great Britain. We propose the insertion of the following additional text into the "Additional Comments" section on page 151. | Comment on Security of Supply: This interconnector provides significant diversity benefits of access to increased and different sources of generation which can be used by the respective System Operators at times of normal market operating conditions and at times of system stress. The project will effectively double the capacity of hydro power connected to the National Grid TSO and simultaneously more than double the capacity of thermal generation connected to the Statnett TSO. The project also provides hedging benefit in the event that the significant new investments in generation capacity expected in accordance with the SOAF (and which are essential for security of supply – particularly in Great Britain) are either delayed or not forthcoming. Further system security and market benefits are expected through facilitation of cross-border trade in ancillary services. | This project is expected to provide significant security of supply benefits which are not currently scored under the current ENTSO-E methodology. In order to provide recognition of such benefits we propose insertion of the attached "Comment on Security of Supply". | Non-confidential | The report is amended accordingly.
Jonny Hosford | Project 110: Norway - Great Britain. |  | Please update the indicative location of this project on the map because it is currently inaccurate. The intended cable landing point at the GB side is in the vicinity of Cambois, which is some 300km north of the currently depicted location which appears to be in the vicinity of Skegness. In the first table on page 150 please correct the spelling of Blythe which should read Blyth. | Non-confidential | This is a good point, but the graph only it indicates an area for possible connection. The substations are not yet finally decided. A comment is added to the project description.
Jonny Hosford | This project investigates a connection between Idomlund (Denmark West) and Great Britain by two parallel 700MW HVDC subsea cables and related substations on both ends. | This project, known as Viking Link and under development by National Grid Interconnector Holdings Limited and Energinet.dk, investigates a connection of up to 1400MW between Denmark West and Great Britain by two parallel up to 700MW HVDC subsea cables and related substations on both ends. | The purpose of this proposed change to the first sentence of the project description on page 158 is to recognise (i) the project name Viking Link, (ii) the co-developer National Grid Interconnector Holdings Limited, and (iii) the capacity "up to" 1400MW reflects that the optimal capacity for this project has yet to be determined. | Non-confidential | The report is amended accordingly.
Jonny Hosford | Project 167: DKW-GB. We propose the insertion of the following additional text into the "Additional Comments" section on page 159. | Comment on GB and DK Connections: Since the time of the original project assessment for TYNDP, the project has received a connection offer from the GB national TSO for a grid connection at Bicker Fenn substation, with a capacity of 1000MW and a connection date in late 2020. The project proponents are now work to this timescale. In Denmark the connection point has been set to Revsing substation. | The purpose of this proposed insertion in the "Additional Comments" section on page 159 is to reflect the current status of development of this project with respect to connection locations and expected date of commissioning. | Non-confidential | The report is amended accordingly.
Energy Vally Foundation |  |  | These are the comments of the North Sea commission on the Ten-Year Network Development Plan 2014, its Executive Summary and the Regional Investment Plan 2014 for the North Sea Region | Non-confidential | -
Energy Vally Foundation | Large-scale meshed interconnector structures based on a broader regional coordination is not seen at this stage as a pre-requisite to accommodate the expected offshore RES in the different Visions, even when these Visions includes a substantial increased off-shore wind generation. | Large-scale meshed interconnector structures based on a broader regional coordination is not seen at this stage as a pre-requisite to accommodate the expected offshore RES in the different Visions, even when these Visions includes a substantial increased off-shore wind generation. If however, offshore wind capacity would increase to a level above 100 GW in 2030, a meshed and more coordinated transmission network solution (rather than a radial one) could be required. This would also mean a need for a coordinated policy with respect to the North Sea grid. | 0.4, page 8 After 2nd paragraph Additional text | Non-confidential | Section 0.4 of the report has been completed with the following § : "If however offshore wind develops as in Vision 4, offshore HVDC hubs will be required, combining the 2 functions of wind power harvesting and interconnection.
Energy Vally Foundation | However, ENTSO-E strongly believes that these proposed new interconnectors should be seen as main facilitators of RES- and market integration and therefore will become part of an offshore grid in the future anyway. | However, ENTSO-E strongly believes that these proposed new interconnectors should be seen as main facilitators of RES- and market integration and therefore will become part of an offshore grid in the future anyway. A specially interesting option in this regard could be what is sometimes labelled as green decommissioning, i.e. to combine the dismantling of the about 600 North Sea oil and gas platforms with the opportunity to convert part of these into energy chemical conversion and storage installations. | 0.4, page 9 After 1st paragraph Additional text | Non-confidential | The option is interesting, but has not been considered explicitly in the background analyses. The text of the executive summary is hence kept as it is.
Energy Vally Foundation | Germany has the largest investment portfolio, followed by Great Britain, France, Norway and Denmark. | Germany has the largest investment portfolio, followed by Great Britain, France, Norway and Denmark. Although part of the financing is indicated to be potentially covered by congestion rents and grid-tariffs, proposals have to be developed how financial coverage for the remainder can be secured. | 0.5, page 9 After 1st paragraph Additional text | Non-confidential | The reference is already made in chapter 6.4., where it is stated that the investments are to be financed through congestion rents and/or grid-tariffs. Also the TYNDP report on chapter 5.4 links to the financial challenges to be overcome.
Energy Vally Foundation | One must also notice that the supporting schemes are limited to the Project of Common Interest whereas there are many significant national transmission projects which are crucial to the achievement of a reliable supply to European consumers. | One must also notice that the supporting schemes are limited to the Project of Common Interest whereas there are many significant national transmission projects which are crucial to the achievement of a reliable supply to European consumers. Finally, a more integrated energy policy of the North Sea countries – in order to avoid future extra costs resulting from a lack of coordination - would be useful and welcomed. | 0.6, page 11 After 2nd paragraph Additional text | Non-confidential | The report is amended accordingly.
Energy Vally Foundation | A boundary may be fixed (e.g. a border between states or bidding areas), or vary from one horizon or scenario to another. | A boundary may be fixed (e.g. a border between states or bidding areas), or vary from one horizon or scenario to another. Although this CBA approach offers considerable assessment benefits, it also has its limitations. The current CBA approach does not cover the impact: on other energy sources such as gas and heat and their synergy and business potential; on energy market competition and arbitrage potential; on the precise access conditions of RES to the energy market; on the overall storage potential; on the scope for decentralized energy production; etc. The CBA methodology used is a useful tool, but cannot provide the whole picture for determining the societal relevance of specific grid investments. Another shortcoming is the fact that the methodology applied does not assess shadow costs of not carrying out specific activities. Clear examples of the latter are precautionary measures in grid design and investments to better enable future RES access to the grid. There is increasing evidence in research literature that limited extra anticipatory investment enabling future renewable capacity to be linked may generate considerable savings as compared to investments that do not include such provisions, and are later on confronted with much higher additional costs if RES activities actually takes place. Because such shadow costs can only be assessed with more advanced modelling tools than the ones implemented in the report, conclusions with regard to the need for such anticipatory measures may be biased (i.e. underrated). | 2.2.2, page 24 After 1st paragraph Additional text | Non-confidential | These questions had been discussed when developing the CBA methodology for TYNDP2016. The final version methodology will be published in november 2014. It will be revised on regular basis. The purpose of the CBA is to investigate infrastructure projects under different expected future conditions. These futures span from conservative assumptions to very ambitions visions, thus a comparison between "BAU" and ... can be made. The purpose is not to evaluate different production portfolios. ENTSO-E is aware of the opportunities that anticipatory investments would offer, but today there is not a harmonized European approach yet.
Energy Vally Foundation | A market model for Iceland was added in order to be able to assess a cable project from GB to Iceland. | A market model for Iceland was added in order to be able to assess a cable project from GB to Iceland. Additionally, a dedicated analysis not covering the area of the North Sea’s countries in total, but the North Sea itself and its coastal regions only could be of considerable help for future energy grid, production and storage planning. | 2.3.1, page 26 After 2nd paragraph, Additional text | Non-confidential | The North Seas have been investigated as part of the Regional Studies. An additional chapter focusing on the waters and coastal areas themselves is added.
Energy Vally Foundation | In terms of CO2 prices it has assumed high (93 Euro/t) but at the same time low primary energy prices. | In terms of CO2 prices it has assumed high (93 Euro/t) but at the same time low primary energy prices. The North Sea Commission has the following general comments to the visions developed: • Links with other energy grids are missing: too little attention has been paid in the plans, analyses and visions, to the potential integration of the power grid with the grid for other energy carriers, such as gases and heat. Especially by the rapid increase of renewables, notably the intermittent ones, wind and solar, the interest in energy conversion has grown rapidly. That is why currently serious research has started up to analyse the contribution to the overall energy system of chemical conversion of energy and energy storage. Examples of technologies that could well seriously develop further are power-to-gas and liquids (electrolysis; methanation; production of biomethanol; etc.) as well as various applications of hydrogen in transportation, chemical applications and otherwise. The optimality of such new technologies could be enhanced in so far as they would support the business cases of intermittent renewable power production units, provide a cost effective backup system with a relatively low cost transport and storage capacities, and contribute to grid balancing. To the extent that such technologies might develop on a large scale in the period up to 2030, such development could well have a serious impact on power grid optimality. The Commission therefore would have appreciated if such technology would have been included in the analyses more explicitly. A specially interesting option in this regard could be what is sometimes labelled as green decommissioning, i.e. to combine the dismantling of the about 600 North Sea oil and gas platforms with the opportunity to convert part of these into energy chemical conversion and storage installations. • The role of decentralized energy systems in the visions: in the visions and analyses more extensive attention could have been given to the development of decentralized or quasi-decentralized energy systems. There seems to be a clear trend towards decentralized power production and energy conversion within Europe, and also to local grid connections with local balancing and storage. It has yet to be seen to what extent this trend will continue when subsidy schemes for renewables will become less supportive and capacity based tariffs would gain strength, but nevertheless this trend seems to be strong for the time being. It therefore would have been advisable to more explicitly include this factor in the four visions, because it will clearly have a serious potential impact on future grid requirement both nationally and in terms of interconnectors. A related issue is why vision 4 “Green Revolution” assumes the highest electricity demand relevant for the TSO’s of all four visions, whereas probably many would expect the green revolution to typically imply considerable extension of decentralized capacity. | 3.1, page 32 After 1st paragraph Additional text | Non-confidential | The comment relates to the scenario building, and can be investigated for the TYNDP 2016. Power to heat and power to gas are options comparable to power storage for the power system. ENTSO-E and ENTSO-G are working on a common methodology to articulate gas and power issues. Such development are complementary (but not a pre-requisite) to the development of means required to further investigate dynamic phenomena addressed here.
Energy Vally Foundation | Interconnection with Great Britain also has an important role in helping to reduce the total European CO2-emissions. | Interconnection with Great Britain also has an important role in helping to reduce the total European CO2-emissions. Additionally, it would be interesting to elaborate what role hydro can play in storing energy thereby contributing to a better balancing, to analyse what the business case of such North Sea interconnectors could be and to investigate how the Norwegian energy storage facility could contribute to the overall North Sea area balancing conditions and market integration. More generally it would be interesting to provide a clear vision on the potential of a North Sea power grid, i.e. a AC/DC grid across the North Sea linking the various North Sea member states. | 3.4.3, page 50 After 4th paragraph Additional text | Non-confidential | The proposals you made have to a big extent been investigated in the Regional Investment Plan North Sea, but not explicitly presented. Investigations included pumping power in Norway, especially in Vision 4. Thus the assessment of the infrastructure considers increased use of Norwegian hydro power. For more information, please consult the page of the Long term network development stakeholders group (or join them!). Regarding the offshore infrastructure, an additional chapter has been added.
Energy Vally Foundation | The TSOs welcome the Regulation EC 347/2013 which has been established to help facilitate permitting of projects which are of significant European interest. | The TSOs welcome the Regulation EC 347/2013 which has been established to help facilitate permitting of projects which are of significant European interest. The risk that grid development may not be delivered in time due to lengthy permit granting procedures or problems of public acceptance should be addressed. This issue is already illustrated by the fact that some quarter of the TYNDP 2012 projects is already delayed. It is likely that such concerns may grow in the course of time as the general public becomes increasingly critical and activist towards new energy related activity. If so, the overall number of some 350 investment plans as presented in the report could benefit from a somewhat more extensive estimate of the risks of delay, and ideas how to try to deal with that. The fast tracking procedure foreseen in Regulation 347/2009 may be a step in the right direction, but is limited to PCIs only. | 5.2, page 62 After 4th paragraph Additional text | Non-confidential | The concern is adressed in general in §9 of the TYNDP report (with the present summary in the executive summary); and specifically to every investment in the assessment sheets.
Energy Vally Foundation | ‒ A compressed air energy Storage in Larne with an annual capacity of 550 GWh. | ‒ A compressed air energy Storage in Larne with an annual capacity of 550 GWh. An additional project that could be added to the list and is favoured by the Northsea Commission is the development of an Energy Island with different functions such as pumped hydroelectric storage (trading, balancing, reducing congestion) and maintenance port for wind turbines. Also other functions could probably be added such as biomass production and LNG. | 6.2.4, page 70 After 2nd paragraph Additional text | Non-confidential | The way of implementing new projects into the TYNDP and Regional Plans has to follow the procedures specified in the regulation 347/2013. New projects like this would presumably be treated as Third Party project, i.e. the promoter must supply data for assessment to ENTSO-E, who assesses the project applying the same methodology as for all other projects.
Energy Vally Foundation | Looking at a possible development, all kind of today’s solutions will be part of a later meshed solution. | Looking at a possible development, all kind of today’s solutions will be part of a later meshed solution. The North Sea Commission feels that more in depth analyses would be required with respect to the offshore versus onshore extension of renewable capacities during the period until 2030. In the report an extensive comparison has been made between the four ENTSO-E visions and the two NSCOGI scenarios with respect to the energy system on and around the North Sea (paragraph 11.3). The report illustrates that in general the NSCOGI scenario assumptions seem to lie in between those employed in the ENTSO-E visions. Also the report indicates that the ENTSO-E analyses have been aligned with those of NSCOGI. This probably explains why ENTSO-E shares NSCOGI’s conclusion that “large scale meshed interconnector structures based on a broader regional coordination is not seen at this stage as a prerequisite to accommodate the expected offshore RES in the different visions, even when these visions include a substantial increased offshore wind generation” (page 8). What however is not fully clear from the report is what ENTSO-E expects to be in its various visions the development of offshore wind especially in the period 2020-2030. NSCOGI in its R-scenario assumes an extension of variable RES installed capacity in that period of 79 GW, of which only 13 GW would consist of offshore wind, thus raising Northern Seas’ offshore wind capacity from 42 GW in 2020 to 55 GW in 2030. NSCOGI dramatically changes this picture in its RES+-scenario where offshore wind capacity increases to 117 GW in 2030. Obviously this significantly supports a meshed and more coordinated transmission network solution (rather than a radial one). In other words how rapidly offshore wind will grow in the next few decades will have a serious impact on the need for policy and other coordination with respect to the North Sea grid. From the report it is not clear where ENTSO-E stands in this regard, nor if ENTSO-E agrees with the NSCOGI conclusion that a new offshore grid study would not lead to fundamental new findings (compared to the one published in winter 2012). This is the more so as that (NSCOGI) study was based on national views during mid 2011, i.e. before France decided to reduce its nuclear power capacity, Germany and Britain reduced their expectations with respect to gas fired capacities, or the Netherlands launched its ‘Energie Akkoord’, to extend offshore wind capacity and reduce coal based capacity, etc. | 11.3.2, page 333 After 2nd paragraph below figure Additional text | Non-confidential | This comment is in line with ENTSO-E conclusions. The Regional Investment Plan North Sea has been amended with the addition of a new chapter, elaborating a bit more on the issues mentioned in your comment.
Consortium |  |  | Important improvements have been made from the TYNDP 2012 process in order to analyse the system as a whole and to determine transmission needs from a European perspective. However, investment planning in the TYNDP still mainly relies on national perspectives. Concerning loss variations, it must be noted that the main driver for transmission projects is currently the higher need for power transfer over long distances, which increases losses. Thereby, the socio-economic welfare of the entire system can be increased even with higher thermal losses. Variation in losses is therefore not a relevant benefit indicator per se. Furthermore, the monetisation of these variations in thermal losses is already accounted in the total cost of generation. | Non-confidential | The project identification in the frame of the RegIPs and TYNDP was built on four visions, which had been developed based on strict rules which had also been consulted by stakeholders. There were two visions being built by a “bottom-up” approach, where national TSOs supplied data according to rules given by the CBA methodology. Two other visions were strictly built “top-down”, meaning by Pan-European view on future developments. ENTSO-E is aware of the challenges concerning loss calculation and its information value. When transporting over longer distances, losses may increase but on the other hand other benefits of the project might balance this out in the overall value of the project. In order to be transparent the values are presented separately in the project assessment, and double counting is avoided (see CBA methodology.) The project identification in the frame of the RegIPs and TYNDP was built on four visions, which had been developed based on strict rules which had also been consulted by stakeholders. There were two visions being built by a “bot-tom-up” approach, where national TSOs supplied data according to rules given by the CBA methodology. Two other visions were strictly built “top-down”, meaning by Pan-European view on future developments. ENTSO-E is aware of the challenges concerning loss calculation and its infor-mation value. When transporting over longer distances, losses may increase but on the other hand other benefits of the project might balance this out in the overall value of the project. In order to be transparent the values are presented separately in the project assessment, and double counting is avoided (see CBA methodology.)
Consortium |  |  | In the conclusions, (p.92 of the Regional Investment plan - North Sea Region), it is stated that "Large-scale meshed interconnector structures based on a broader regional coordination is not seen at this stage as a pre-requisite to accommodate the expected offshore RES in the different Visions". However, it is recognised that "new interconnectors should be seen as main facilitators of RES- and market integration and therefore will become part of an offshore grid in the future anyway". When the Business-as-Usual, i.e. investments in offshore infrastructure with very limited coordination (at most three countries) continues, it is very likely that the future offshore grid will be suboptimal. This can be avoided by developing a common vision for the future offshore grid, that will result in an optimal offshore grid from a European perspective. Investments in offshore infrastructure are then coordinated by all North Sea Region countries and are integrated in the global vision of the future offshore grid. We think that such a vision for the future offshore grid is currently missing in the TYNDP. It could be addressed by including in the TYNDP the concept of meshed offshore grid that has been analysed in the study carried out for DG Energy “Benefits of a Meshed Offshore Grid in the Northern Seas Region” (to be downloaded on the website of the EC at http://ec.europa.eu/energy/infrastructure/studies/ten_e_en.htm) In the current version of the TYNDP, without this coordinated meshed offshore grid, important price differences remain between the Nordic countries and Continental Europe for all the different visions in the TYNDP (even considering planned interconnection projects). This suggests that further increases of interconnection capacity between these areas could significantly increase the European social welfare. The TYNDP must in the end demonstrate that the proposed projects actually give the highest social-economic welfare for Europe and that no other/alternative projects would provide a higher social-economic welfare. Otherwise the project portfolio has to be adapted. ENTSO-E must play an important analytical and advisory role using the top-down approach in order to ensure consistency between the national plans and even more importantly point out projects of European interest; even those with limited national interests or even negative national interests. | Non-confidential | This comment is in line with ENTSO-E conclusions. A new section of RegIP RGNS has been implemented, elaborating more in detail on the issues you mention in your comment. The visualization of the offshore grid infrastructure has been improved. We acknowledge that some price differences still exist. However, it might not be beneficial to completely level out the differences, as it might be too expensive to build the last MW infrastructure. ENTSO-E did test the robustness of the project portfolio against the four visions. For the realization of Vision 4 more investments will be needed, whilst at the same time it might well be the case that not all proposed investmens show a sufficient indication on their necessity for all visions, particularly with respect to Visions 1 and 2.
Element Power | Table 2.2. Size of the Regional Group North Sea’s Grid Model | n/a | No of PSTs should be shown. | Non-confidential | We have chosen only to present the very rough overview describing the size of the model rather than giving too many details which might increase confusion instead of enlighten the reader.
Element Power | Figure 4.1 Illustration of Net Transfer Capacities in NS region (2013) | n/a | Some blue arrows in atlantic ocean beyond outer Hebredies seem to be misplaced? | Non-confidential | ENTSO-E has updated the map and arrows have been deleted.
Element Power | Figure 4.2 Map with the main bottlenecks in the North Sea region in 2030 | n/a | It is not clear direction of bottlenecks. | Non-confidential | The location of the bottleneck is the most important information alerting where action is required. The basic motivation appears also essential. The map is hence limited to displaying the above information. More is provided later in the report, with the magnitude of the flows to begin with. With more volatile flows in the coming decades, both directions are usually at stake, with few exceptions (esp. major plant connection issues). The regional investment plans describes more deeply the main bottlenecks and the projects assessments sheets provide the details about GTC magnitude and direction.
Element Power | Figure 4.2 Map with the main bottlenecks in the North Sea region in 2030 | n/a | Why are some bottlenecks marked as lines and some as ovals? | Non-confidential | The boundary is either closed or open: the connection of a specific power plant or the supply of a specific area at risk is usually marked as a closed line, as connection or transmission support can be imagined a priori from all directions. Bottlenecks in the market usually do not isolate completely (360°) a region but solely prevent power flows to cross a certain section.
Element Power | Figure 4.2 Map with the main bottlenecks in the North Sea region in 2030 | n/a | Doesn't show severity or significance of constraints. | Non-confidential | This is correct. The severity information is given in figures 4-4 and 4-5
Element Power | Figure 4.2 Map with the main bottlenecks in the North Sea region in 2030 | n/a | Security of supply affects an area and is not a line. | Non-confidential | The line represents a bottleneck, caused by potential high power flows, that threathen SoS in the Dublin area, hence, a line as been drawn.
Element Power | Comment on the CBA assessment: cost figures have not been provided to ENTSO-E. | n/a | Cost figure can be provided on request | Non-confidential | This offer comes too late for the TYNDP14 process but is wecome for the TYNDP16 process.
Element Power | Commissioning dates 2017 and 2018 |  | Commissining dates are being revised and can be updated on request | Non-confidential | This offer comes too late for the TYNDP14 process but is wecome for the TYNDP16 process.
Eurelectric |  |  | It might be more of a curiosity, but when comparing the calculations of emissions in the different visions they seem to be different for Norway in the North Sea and Baltic Sea plans. In the North Sea plan it also seems for some reason to be an emission increase for Norway in vision 4. There might be a good explanation for this or there may be mistakes in the calculations or input data. |  | ENTSO-E has updated all the regional reports respectively and tuned the final versions.
Eurelectric |  |  | For the ICs between Norway and UK there are two projects presented; NSI and NorthConnect. Although NorthConnect is shorter than NSI (The TYNDP operates with 650 km for NorthConnect, NorthConnect operates with a possible range of 560 – 650 km) the two projects operate with the same range of investment costs € 1.300 – 3.000 million. Furthermore, the NSI project is planned commissioned before NorthConnect. Hence, in the evaluation the TNDP anticipates a lower SEW for NorthConnect project. While ENTSO-E seemingly has a policy of not ranking projects in the TYNDP, it is actually done in the comments of specific projects. In this case the non-TSO project NorthConnect is implicitly ranked lower. ENTSO-E should either rank projects properly and transparently or not at all. |  | Yes, we do investigate the projects based on the same assumptions. The individual descriptions are adapted accordingly in the new edition.
Eurelectric |  |  | Several projects operate with large differences in possible/anticipated investment costs, e.g. NSI and NorthConnect etc. This creates a large uncertainty regarding potential future costs and SEW. The reason for these rather large uncertainties should be explained and if possible reduced. |  | The investment costs have been adapted in the new edition of the reports.

## CCE
Respondent Organization | Initial | Proposed | Comment | ENTSO-E answer
CZ Ministry of Industry and Trade | New features in TYNDP 2014 - Scenarios as four visions for 2030 |  | Although the document “Scenario Outlook & Adequacy Forecast 2014-2030“ works with three scenarios and four Visions, Regional Investment Plan (RgIP) works only with Visions. Visions are specified in the SO&AF as extreme limits. Therefore it is inaccurate to use them as "scenarios" in the usual sense. Notice "Scenarios as four visions for 2030" in "New features in TYNDP 2014" is certainly not a sufficient explanation. | SOAF adresses mid term and long term adequacy (scenarios A, B and 2020 for mid term, and scenarios-visions 1,2,3,4 for long term which represent extreme views on energy sector development in Europe to be conceived as the boundaries defining the space of possible evolutions). RgIPs adress only long term, 2030 time horizon using the four visions as in SOAF.
CZ Ministry of Industry and Trade |  |  | Nowhere is it stated for which parameters is submitted RgIP sufficient (incl. for which Vision). Most projects have the SEW (Social and Economic Welfare) calculated for all four Visions. Does this mean that all projects (with some exceptions) are assumed also for Vision 1 and Vision 2? If this is true, we donot recommend to implement for the Vision 1 and 2 projects, where SEW and other parameters are low compared to the cost. The exceptions are projects that have SEW only for Vision 3 and 4, for example. "133 Project: Longterm German RES". | In principle all projects have been assesed for all four visions with the exception of few projects, in visions 3 and 4, related to the expected huge RES penetration.
CZ Ministry of Industry and Trade |  |  | The vision and the associated calculations are used to confirm the eligibility of each project, respectively linked projects. The procedure should be the opposite, i.e. to identify projects necessary for specific future values in scenarios (see e.g. scenarios in “Scenario Outlook & Adequacy Forecast 2014-2030“), or for limit values in Visions.
CZ Ministry of Industry and Trade |  |  | What is a "market simulation tool"? The term occurs only once and only in RgIP? We think that there is a problem with the terminology coordination and incomplete abbreviations placing (e.g. PEMMDB, but in the list of abbreviations is PEMD) in the whole package of TYNDP documents. This complicates the reading and understanding of documents significantly. | Market simulation tools are used to assess the yearly performance of power systems taking into account load variations, RES and generation mix. In this way commercial (usually cross-border but in specific cases also internal) yearly power flows can be assessed and compared with the transmission capacity of anticipated network. Mentioned terminology inconsistencies will be corrected.
CZ Ministry of Industry and Trade | Through network studies a system adequacy is evaluated and |  | The introductory paragraph of chapter "2.3 Market and Network Studies" is unfinished. | Will be corrected.
CZ Ministry of Industry and Trade | Each country for market study purpose is modelled as one single node (all generation and load data being aggregated to this single node), assuming that there is no internal constraint within the country |  | We point out that it is difficult to use such assumptions for modelling of the system. This situation does not reflect the reality in the EU.
CZ Ministry of Industry and Trade |  |  | As in other documents of TYNDP package, terms are often used without explanation of their meaning or content - e.g. "the basic indicators of secure and reliable network operation”. | Will be corrected.
Eurelectric |  |  | Impact of the German energy transition: Development in the whole CEE region is considerably dependent on the energy transition in Germany, both in terms of growth in the share of production from RES and decommissioning of nuclear power plants and the related development of transmission network in the north-south and northeast-southwest corridor. Due to the fact that one third of projects of European significance is currently delayed to the original schedule, serious concerns arise that it will be difficult to follow Germany's ambitious plans on changing the fuel mix and significantly further increase the share of renewable energy (especially off-shore wind) in the infrastructure area. Given the importance for the entire region, there should be a clear correlation between the ability to connect other sources in northern Germany and preparedness of infrastructure to transfer this production by the internal network to the point of consumption concentrated in the south, without further worsening impacts of loop-flows to neighboring operators. Table 6-1 shows that only in Germany, more than 80% of all capital expenditure in the CEE region (about 50 billion EUR) is to be spent. With regard to delays recorded in all countries of the region where there are expenditures about one to two orders of magnitude lower in comparison with Germany, this plan seems unrealistic in advance. In this context, it is necessary to relativize the scenario 4, which is objectively unattainable without fundamental change in the attitude of Member States to the authorization procedures for construction management. Given the importance of this factor for the wholesale market in the CEE region, we recommend to find a broad approach to take this discussion significantly into account and to develop a bundle of measures by the relevant stakeholders to remove existing barriers and enable required energy flows. That means also measures for the extension of the price area should be considered.
Eurelectric |  |  | Strengthen the interconnection with Hungary: As follows from the analysis of ENTSO-E, another key factor for market development in the CEE region is increasing interconnectivity of Hungary, mainly between Hungary and Slovakia (projects 48 and 54) and also with Romania and Croatia. With regard to the implementation of the market coupling project 4M, any increase in the network transfer capacity (NTC) on the border of Hungary is major improvement and will contribute to increased efficiency of interconnected regional market. It should be a priority for NRAs and TSOs to avoid further delays in the implementation of the projects concerned. | no need
Eurelectric |  |  | The description of the Polish network problems is unclear: The document mentions that the internal problems of the Polish grid cause significant limitations on the total export and import capacities of Poland and that these global constraints are further considered. But the report does not contain any more detailed explanation regarding the Polish system which, for the sake of transparency and significance, should be added. | The right version of description which is included in the text (page 29 of RG CCE Plan) is : "Expected market capacity is a value between two countries. In the case of Poland there are additional restrictions, which are driven by the structure of Polish internal system and the aim to provide maximum capacity for market study. The maximum import and export possibilities are much lower than the sum of all capacities on the Polish borders. Due to this, the import and export capacities were also limited in the market simulations." This is description of the fact that NTC on Polish sychronous border is not the arithmetic sum of NTC values for Polish borders with Germany, Czech Republic and Slovakia taking into account separately. This description has diffrent meaning than mentioned by Eurelectric: "Internal problems of the polish grid cause significant..". There are no internal problems within the Polish grid which cause any significant limitations on the total export and import capacities of Poland (especially in TYNDP 10 year horizon because Polish internal and crossborder investment plans are sufficient in this horizon).

## CSE
Respondent Organization | Initial | Proposed | Comment | Confidentiality | ENTSO-E answer
Eurelectric |  |  | This regional plan describes the investment needs and the associated planned projects for 2030 in the Continental South East (CSE) region, which covers Bosnia-Herzegovina, Bulgaria, Croatia, Greece, Hungary, FYR of Macedonia, Montenegro, Romania, Serbia and Slovenia. Albania and Turkey is also taken into account. It also provides information on monitoring the progress of TYNDP 2012 projects which is valuable for all market participants in the region. The applied holistic view of grid development, combining power transmission issues with environmental and resilience concerns in the TYNDP 2014 contribute for the better appraisal of the projects. The CSE RgIP depicts the insufficient electricity grid connecting South East Europe with Central Europe. The implementation of new projects and the enhancement of cross-border interconnections between the currently divided national systems is vital for the successful implementation of the IEM. |  | ENTSO-E supports this statement which is in line with the TYNDp 2014.
Eurelectric |  |  | We welcome the approach of project assessment in terms of third parties impact in the CSE RgIP, especially the sensitivity analysis of CSE region on Turkey’s electricity exchange balance. An accurate examination of different scenarios for net exporting capacity development of Turkey is quite important for detection potential outages and overloaded interconnectors and therefore it contributes for more comprehensive assessment in the selection process of the most robust and with the highest SEW value network projects in CSE region. This practice will be useful to continue and to extend in the next edition of TYNDP. |  | ENTSO-E acknowleges the support to its approach and will continue delivering this information in future TYNDPs.
Eurelectric |  |  | Reviewing the initiatives under Black Sea Corridor Project in the CSE RgIP, especially Bulgarian ones, all of them are reported as delay due to a lack of funding. The Bulgarian system operator reported financial losses for 2012, 2013 and for the first half of 2014 due to the poor regulated transmission and access fees (two times lower transmission and access fees compared to the period 1.08.2013-31.12.2013 resulted into 4 times higher financial losses for the 2Q 2014 than in 2Q 2013). The impaired company’s credit worthiness accompanied by a prolonged and still not accomplished unbundling procedure of the system operator exposes to a risk and hampers the projects fulfilment no matter how promising and beneficial can be these projects not only for the RES integration in the Black Sea Region but also for the enhancement of internal market integration. This illustration of financial and administrative capacity constraints concerning one of the companies in the region is just an example that the bottom-up approach should be carefully examined and implemented in the CSE region if we want successful projects accomplishment. |  | The ENTSO-E supports this remark. Financiability is one of the main problems when bulding the necessary infrastructure.
Eurelectric |  |  | The legend box in the figures presenting yearly average marginal costs for all four Visions is not easily readable due to a lack of indicating values for different shading of grey. |  | Shades of grey have been implemented and no figure provided as they could be misleading: on average over the year, absolute prices in every country may be close one to another; although hourly price differentials may be high (in one direction at some moments, and in the other direction at other moments). The maps hence display the information that serves the demonstration, highlighting mainly the average absolute price differentials; and giving additionnally with the shades of grey the feeling about which countries are major importers/exporters. The text completes the information indicating the average cost all over Europe.

## SOAF
Respondent Organization | Initial | Proposed | Comment | Confidentiality | ENTSO-E answer
ENDESA |  | - | We welcome the recently published Scenario Outlook and Adequacy Forecast 2014-2030, which provides a reliable overview of generation adequacy at mid and long term horizon. This report is also of particular relevance for the approval of remuneration mechanisms of capacity by the European Commission, since the recently approved Guidelines on State aid for environmental protection and energy 2014-2020 records that "The identification of a generation adequacy problem should be consistent with the generation adequacy analysis regularly carried out by the European Network of Transmission Operators for electricity in accordance with the internal energy market legislation”. |  | The comment is in line with the SOAF report and the proposed methodological improvements for generation adequacy assessment currently under consultation
ENDESA | The scenarios have been prepared jointly with stakeholders during more than 2 years, in the long term network stakeholders group, in workshops and consulted upon. Visions 1 and 3 reflect national energy policy and there consistency at European level is indeed questionnable. Vision 2 and 4 have been built in order to provide a more consistent picture. In this respect, Eurelectric timely, valuable input is welcome for the next TYNDP 2016. | - | Lack of economic sense at TSOs projections. Indeed, the permanence of conventional generation plants that now do not recover costs is at risk and will depend very much on current and future prospects of the market and regulatory framework. If the case is such that squeezed plants finally shut down, the expected generation adequacy will rapidly impoverish, moving away from current expectations. Hence, the economic viability of existing generation fleet is of key importance to take on board at TSOs surveys. In the same way, forecasts for Spain assume that coal-fired plants owners will undertake large investments to be compliant with DEI requirements, which is not realistic in the current situation since utilities have not announced such kind of developments under the current market and regulatory environment. |  | Economic viability of the generation means is essential. Scenarios are however built with different purposes, and hence with different methodologies: scenarios to test adequacy are not built in the same spirit as the Visions, supporting the TYNDP. The Visions are in essence "adequate" with respect to generation (i.e. generation means can cover the expected load, at pan-European level) in order to test in which respect the grid is also appropriately sized.
ENDESA |  | - | TSO input hypothesis shall be supported by an EU methodology. We welcome the public availability of data set used to build up the SOAF. That allows stakeholders to find back SOAF conclusions. Nevertheless in our view, being able to reproduce SOAF conclusions is insufficient as input hypothesis are not well reasoned. Indeed in the case of Spain, recent input data have changed from last year analysis, SOAF 2013-2030, so as conclusions (see previous). However there is no way to understand neither reproduce such hypothesis. An established methodology to calculate and forecast future hypothesis scenarios should be in place. Such methodology should be defined at European level and being common to calculate TSO hypothesis for all EU member states. In addition to SOAF and data set, a comprehensive description of later methodology shall be proposed. |  | The framework and the main references on the base of the scenario building are reported in the document. The methodology and the input used to build the four ENTSO-E 2030 Visions have been publicly consulted. Stakholders' expertise in the scenario building process is key to swiften the construction of economically viable scenarios. The scenarios have been prepared jointly with stakeholders during more than 2 years, in the long term network stakeholders group, in workshops and consulted upon. Visions 1 and 3 reflect national energy policy and there consistency at European level is indeed questionnable. Vision 2 and 4 have been built in order to provide a more consistent picture. In this respect, timely, valuable expertise input from stakeholders is welcome for the next TYNDP 2016.
ENDESA |  | - | SOAF conclusions very much depend on TSO input hypothesis. According to the analysis conducted last year (SOAF 2013-2030), new installed capacity would be required by the end of 2019. Last document (SOAF 2014-2030) postpones the need for new capacity to 2022. See figure on excel attached "Figure 1". |  | Yes, indeed an update of the input hypothesis naturally produces a change in the results.
ENDESA |  | - | Peak demand previsions are too pessimistic. Latest report, SOAF 2014-2030, forecasts by 2020 a peak demand of 43.090MW, that is 3.310MW lower than previous report SOAF 2013-2030. Such expected peak demand is too conservative: it corresponds to the peak demand 15 years ago (2005) and has been already exceeded within the last 5 years. See excel attached "Figure.2" |  | The reference time point considered for the peak load in SOAF does not necessarily correspond to the national peak demand. Also, the forecasts are updated yearly according to the expected future trends of the demand.
ENDESA |  | - | Gas projections foresee no CCGT closures despite their critical situation. Gas projections in the latest report, SOAF 2014-2030, assume the retention of existing CCGTs fleet. That means, the risk that nowadays most combined cycles do not recover costs is not considered. The report of the CNMC 5/12/2012 shows that costs recovery via market is even zero in about 5000 MW. See excel attached "Figure 3". Therefore, in the absence of a mothballing mechanism, 5000 MW will probably shut down deteriorating the margin to cover system demand. |  | Whenever there is no official communication of decommissioning, it is considered that the CCGT units will be available for security of supply reasons.
ENDESA |  | - | Coal projections assume 4.2 GW to undertake investments to comply with the Industrial Emissions Directive (IED) . Coal plants that do not carry out investments to comply with the Industrial Emissions Directive (IED) are subject to the limitation of 17500 utilization hours and obliged to close not later than 31 December 2023. That means that, in the absence of IED investments, the coal fleet will progressively shut down as they do reach the 17500 maximum operating hours. By 2024, at the latest, there will be 0GW generation of coal. ENTSO-E in its latest report, SOAF 2014-2030, forecasts 9,8GW of coal capacity by 2020 and 4,2GW by 2025. Therefore, ENTSO-E assumes that 4,2GW of coal plants will carry out the IED investments to be operational in 2025 and beyond. |  | Concerning the decommissioning of the power plants due to IED, the general approach taken by the TSO was not to take them out without an official communication, especially for adequacy consideration. Some of the coal plants have been considered as decommissioned in the 2030 horizon due to other reasons; as soon as a decision about the future of these plants is taken, it will be considered in the forecasts.
ENDESA |  | - | If IED investments fail, new firm capacity would be needed in 2019. Excel attached "Figure. 4" shows how RC-ARM evolves if, contrary to what ENTSO-E has assumed in its prospective 2014-2030, no investments to comply with IED are made (red line). In this case, the system would experience a loss of firm capacity from 2019 onwards, due to the gradual closure of coal plants as they reach the 17500 utilization hours. In this case new firm capacity would be needed in 2019 to cover demand, three years before ENTSOE prospective. |  | Yes this evolution path is possible under these assumptions. Concerning the decommissioning of the power plants due to IED, the general approach taken by the TSO was not to take them out without an official communication, especially for adequacy consideration.
ENDESA |  | - | Is the ENTSO-E’s hypothesis on IED investments realistic? Current market conditions and regulatory uncertainty make the IED investments very unlikely. The forward price for calendar years 2015-2017 is at 49 €/MWh. Meanwhile, variable costs of combined cycles at current gas prices are around 70 €/MWh. The variable costs of coal plants are between 45 €/MWh and 55 €/MWh, in all cases, including recently introduced taxes on electricity and fuel (Law 15/2012). This means insufficient or even negative margins to recover fixed costs for operation and maintenance and investment. According to the transposition of the Industrial Emissions Directive, the decision to undertake the IED investments should be taken within one year: before October 1st, 2015, the owners of these facilities need to communicate the Government whether they invest or take the limitation of 17500 hours. This means that the power plant owner cannot delay their IED investment decisions while waiting for better market conditions. This situation makes ENTSO-E hypothesis on coal IED investments completely unrealistic. Only the quick implementation and approval by DGCOMP of a capacity remuneration scheme could ensure that a certain amount of coal capacity carries out the IED investment. |  | Concerning the decommissioning of the power plants due to IED, the general approach taken by the TSO was not to take them out without an official communication, especially for adequacy consideration.
Jonny Hosford | It is proposed that the existing description of "Generation Adequacy" on page 97 is amended (or substituted) with the proposed version here. | The Electricity Act 1989 requires OFGEM to prepare an Electricity Capacity Assessment report by 1 September each year. In recent years OFGEM’s Electricity Capacity Assessment report has shown trends of decreasing de-rated capacity margins and increasing loss of load expectation – with the tightest margin forecast for winter 2015/16. The decreasing trend has directed the attention of policy makers towards actions that improve the security of supply outlook. Since the time of the 2013 report a number of new measures have been introduced to reduce the risk to customer disconnections. These include: (i) the Government has set the level of adequacy for the electricity system in Great Britain by defining a Reliability Standard of 3 hours/year loss of load expectation; (ii) OFGEM has approved new tools (new Balancing Services) that National Grid Electricity Transmission can use to help balance the system when margins are tight. The total volume of New Balancing Services that NGET intends to procure ranges from 330MW to 1800MW over the coming winters 2014/15 to 2017/18; (iii) the Government has set out plans to introduce the Capacity Market (as part of Electricity Market Reform) to reduce risks to security of supply in the medium term and beyond. | The initial version of the Generation Adequacy description on Page 97 does not fully reflect the way Great Britain addresses the question of Electricity Capacity adequacy planning and recent developments in this area which are highly relevant. This commentary should be updated to fully reflect the current state of play as described in the "Proposed Version" |  | The SOAF methodology is currently under revision on the base of ACER questions. Both the methodology and definitions will be updated according to the new approach.
Jonny Hosford | It is proposed that the following additional text is inserted in the "Interconnection Capacity" section. | Interconnectors are beneficial for security of supply in general. They allow access to more generation sources that can be used under normal market operating conditions and at times of system stress. They give the GB market extra options, providing services such as energy and reserves balancing, frequency response and black start. They may also reduce the cost of electricity throughout the year and transfer excess renewable generation between countries in a future with high penetration of intermittent generation. [footnote: see OFGEM Electricity Capacity Assessment Report 2014, Page 20] The direction and size of interconnector flows can have a significant impact upon adequacy forecasting. For example according to analysis by OFGEM [See OFGEM Electricity Capacity Assessment Report 2014], the difference between “no imports” and “full imports” (+3GW import to GB from mainland Europe) would be a significant reduction of up to 8 hours/year loss of load expectation. The large divergent trend in RC-ARM between scenarios A and B reflects the extent to which GB adequacy is dependent upon new investments in generation capacity (over 20GW new generation capacity assumed to be connected between now and the year 2025). To the extent such new generation investments may be delayed or not forthcoming, then access to generating capacity in neighbouring countries via existing and new interconnector capacity could have an important hedging benefit for Great Britain security of supply. | The commentary in relation to "Interconnection Capacity" should be expanded as shown in the "Proposed Version" to further explain the impact that such interconnection can have upon security of supply for Great Britain. The proposed text is consistent with the position expressed by OFGEM [see OFGEM Electricity Capacity Assessment Resport 2014] and chimes with the expectations of stakeholders with respect to improved methodology for modelling cross border exchanges in adequacy assessment exercises [see ENTSO-E Target Methodology for Adequacy Assessment - Consultation material July 2014]. |  | We share the point on the important role of interconnectors in security of supply, specially for weakly interconnected countries. The SOAF methodology is currently under revision on the base of ACER questions. Both the methodology and definitions will be updated according to the new approach.
Jonny Hosford | This comment pertains to the SOAF 2014-2030 Dataset suite of spreadsheets |  | It is not clear from the suite of spreadsheets in the SOAF 2014-2030 Dataset as to which interconnector projects (or even which country to country import/export capacities) have been assumed for the purposes of the Scenarios B & EU2020 and for the Visions 1 to 4. This frustrates attempts to establish a joined up understanding between SOAF and TYNDP. For example in ScV4.xlsx the Import/Export capacity for Great Britain is shown as 8.59GW. However, GB already has over 4GW interconnector capacity and the draft TYNDP includes proposed additional interconnector projects to GB with an aggregate new capacity in excess of 10GW. Hence it would appear that ENTSO-E has included some but not all of the new projects. Please could ENTSO-E clarify its approach to this area of analysis and clarify what physical capacities have been assumed between GB and each of its neighbouring countries for the purposes of its network and market modelling Scenarios B, EU2020 and Visions 1 to 4. |  | SOAF adresses simultaneous aggregated import/export capacity, while TYNDP is dealing with specific projects. However, data consistency and description will be improved in the next TYNDP package.
CZ Ministry of Industry and Trade | Conservative Scenario or Scenario A This scenario is not used to further specify grid development as part of the Ten Year Network Development Plan |  | The document identifies three scenarios and four visions (see also our Comment at RgIP). For Scenario A it is literally written: “This scenario is not used to further specify grid development as part of the Ten Year Network Development Plan.“ Although at the “Best Estimate Scenario or Scenario B“ is written “This scenario is an important assumption to further specify grid development in the Ten Year Network Development Plan“, both TYNDP and RgIP work only with four Visions. The explanation is needed. |  | Section 7 in the SOAF document has been ammended according to the comment.
CZ Ministry of Industry and Trade |  |  | One scenario used in TYNDP should include so-called Best Estimate so that it can define the exchanges of electric energy in the most likely scenario based on projections national targets, i.e. not only in extreme scenarios. |  | The four Visions approach was agreed in the scenario consultation process to be the best way to handle long term uncertainties. The purpose of the multiscenario approach used in the TNDP 2014 is to test the grid and the network reinforcements in very different situations in order to cover all possible frameworks.
CZ Ministry of Industry and Trade |  |  | As in other documents of TYNDP package, terms are often used without explanation of their meaning or content - e.g. "energy indicators”. |  | The term "energy indicators" refers RES penetration, CO2 reduction and such other indicators. A comprehensive list of acronyms is reported in the document.