## all_comments
ID | Document version | Chapter | Article | Paragraph | Subparagraph | Submission date | Respondent Fullname | Respondent Organization | Status | Initial | Proposed | Comment | Start line of commented text | End line of commented text | Type of Comment | Nature of Comment | Level of detail of Comment | Confidentiality | Confidentiality2 | File name
0005-e495-853f-cabf-bec9 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 19:51:12 | Roland Tual | SEDC | final | Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs | [8 empty] | confidential
0005-6fb5-0072-d181-5815 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:47 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | 2. Each TSO shall activate Limited Frequency Sensitive Mode before activation of the automatic Low Frequency Demand Disconnection scheme, provided the rate of change of Frequency allows the TSO to do so. | 2. Each TSO shall make sure that Limited Frequency Sensitive Mode will be activated before activation of the automatic Low Frequency Demand Disconnection scheme, provided the rate of change of Frequency allows the TSO to do so. | Paragraph 2 establises that each TSO shall activate Limited Frequency Sensitive Mode before activation of the automatic Low Frequency Demand Disconnection scheme. As both of them are automatic, clarification on this is needed. |  |  | technical |  |  |  | Non-confidential
0005-6f79-2710-cc66-4a18 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-09 09:59:57 | Dr. Michael Wunnerlich | BDEW | final |  | Please find our comments in the BDEW position paper on the ENTSO-E "Draft Network Code on Emergency and Restoration" (NC ER) | Please find our comments in the BDEW position paper on the ENTSO-E "Draft Network Code on Emergency and Restoration" (NC ER) |  |  | technical |  |  |  | Non-confidential | 0005-6f79-2710-cc66-4a18-BDEW-on-NC-NC-ER_20141208.pdf
0005-e4bd-9dfc-81b5-ce82 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-05 15:37:05 | Elisabetta Bourla |  | final | see attached file | see attached file | see attached file |  |  | technical |  |  |  | Non-confidential | 0005-e4bd-9dfc-81b5-ce82-Edison Response NC E&R.pdf
0005-4869-c3e0-cf28-530f | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:47 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 Article 21. | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 and Article 21. Any amendment will be subject to consultation. | where on review a need to amend the System Defence or Restoration Plans is determined, then any amendment must be subject to consultation – provision should be included reflecting this. |  |  | technical |  |  |  | Non-confidential
0005-bd85-12eb-6f29-c3ee | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-04 09:13:21 | Steve Wilkin | ELEXON Limited | final |  | See general comment | With the addition of Chapter 4 on market interactions, this is now a hybrid operational/market Network Code. Because of this the governance arrangements for a "pure" operational code will not be apppropriate. Ideally Chapter 4 should be moved into the respective parts of the market codes depending on which market is being suspended and restored. For example, the Network Code on Electricity Balancing should cover the suspension and restoration of balancing markets, and the CACM Guideline should cover the suspension and restoration of single day-ahead coupling, etc. But given that the CACM Guidelines are almost complete, we suggest that Chapter 4 alone should fall under the governance of a special stakeholder group with market expertise. |  |  | technical |  |  |  | Non-confidential
0005-4891-01cc-3e51-c912 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-05 10:14:00 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final |  | A new Article is proposed, to clarify the question, who has to bear the costs of necessarry measures for significant grid users and power Generation owners who are not in the regulated System. | As in other Network Codes new obligations for DSO and for existing and new power plants as well as significant grid users are stated, without any determination, who will bear the costs for the necessary measures. The consequences will be, that NRA set out different national rules which will distort the competition in the European union. Therefor clear guidance should be given, who is obligated to bear the costs. |  |  | legal |  |  |  | Non-confidential
0005-e4bd-d63b-6ec5-e301 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-04 09:15:32 | Steve Wilkin | ELEXON Limited | final | Recital (4) This Network Code on Emergency and Restoration was drafted aiming at setting out clear and objective requirements for TSOs, DSOs and Significant Grid Users in order to contribute to nondiscrimination,effective competition and the efficient functioning of the internal electricitymarket and to ensure system security. | Recital (4) This Network Code on Emergency and Restoration was drafted aiming at setting out clear and objective requirements for TSOs, DSOs, Significant Grid Users and other affected parties in order to contribute to nondiscrimination,effective competition and the efficient functioning of the internal electricitymarket and to ensure system security. | The stakeholders impacted by this Network Code are not limited to TSOs, DSOs and Significant Grid Users, due to the inclusion of Chapter 4. Market participants and other participants (for example, Balance Responsible Parties and any settlement administrators) will also be impacted by market suspension and restoration. |  |  | technical |  |  |  | Non-confidential
0005-2159-75de-cf8e-35a9 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:49 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | the measures do not endanger the Operational Security of the neighbouring Transmission Systems. | the measures do not endanger the Operational Security of the neighbouring Transmission Systems, DSO networks or Grid Users. | Endangering of DSO networks and Grid Users shall also be prevented. | [6 empty] | Non-confidential
0005-9675-75c0-d180-15cc | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:48 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | [NOTE FOR THE PUBLIC CONSULTATION: this article aims at stating the requirements from other NC that apply in Emergency and/or Restoration States. It has to be further elaborated.] For example: | Work out this article before Public Consultation! | The article is not available for the Public Consultation. All relevant information should be included in the document. This is a formal public consultation on the code and a consultation can be organised in an appropriate manner only when all information is available for stakeholders. | [6 empty] | Non-confidential
0005-e4d1-75de-d24a-d0ae | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:51 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | new clause | e) the measures do not lead to damages on the assets of Grid Users or Sysgtem Operators. | Add new subparagraph. The principle that also assets of grid users and System Operators shall not be damaged. | [6 empty] | Non-confidential
0005-48a5-4eb0-d0b8-deef | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:50 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10. | [6 empty] | Non-confidential
0005-bdad-d36e-d54e-d3ca | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 23:56:21 | Gunnar Kaestle | Clausthal University of Technology | final | Introduction: (7) promises harmonised requirements, but it is unclear how this can be reached if member states chose indidual solutions. | remove paragraph 7, page 3 of the introduction. | harmonised requirements need the same settings within the same synchronous zone, national implementations are contradictionary to harmonisation which is crucial for frequency issues, cf. with article 14 and [NC RfG] article 8. |  |  | legal |  |  |  | Non-confidential
0005-9689-8560-cf8e-c583 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:53 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | new clause | f) the measures are suitable for the purpose foreseen. | Add new subparagraph. | [6 empty] | Non-confidential
0005-4891-5e50-d180-290c | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:52 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10. | [6 empty] | Non-confidential
0005-9689-8560-cff0-71ec | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:54 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10. | [6 empty] | Non-confidential
0005-6fb5-85a9-a04c-ab38 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-07 12:51:40 | Herve MELJAC | EUR | final |  |  | Feeding Nuclear Power Plant auxiliaries is critical for nuclear safety. According to IAEA recommendations, the grid is considered to be the preferred source for power. Emergency and restoration arrangements should take into account specific NPP needs where applicable. The EUR is confident that Article 8.2.d. and 20.2.b. allow System Defence Plan and Restoration Plan designs to take into account the specificity of NPP needs if NPPs are listed as high priority SGUs (as mentioned in the spporting document) although no explicit mention of nuclear safety is made in the proposed document. |  |  | legal |  |  |  | Non-confidential
0005-487d-ac51-7e52-53cf | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:52 | Rothermann Philippe |  | final |  |  | Please add an article that enables the TSO to force a power plant to participate in system restoration. For example: Switzerland operates an open market. What happens if a power plant does not want to participate? | [6 empty] | Non-confidential
0005-2181-9cb2-cf8d-6a7b | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:48 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | maximum inaccuracy of Frequency measurements on Low Frequency Demand Disconnection relays (maximum inaccuracy); | maximum inaccuracy of the complete (sensor, transmission, calculation, analysis, protection relay) Frequency measurements on Low Frequency Demand Disconnection relays (maximum inaccuracy); | It is completely unclear if the whole measurement (sensor, transmission, calculation, analysis, protection function) is meant or only a subpart of the system. It is also unclear how the inaccuracy is to be determined. Please specify exactly what is meant or delete the value. | [6 empty] | Non-confidential
0005-bdd5-7627-a3d0-118c | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-07 12:51:40 | Herve MELJAC | EUR | final | This comment relates to the general provisions (before the table of contents), bullet point 7: This Network Code provide | This Network Code provides | Typo |  |  | legal |  |  |  | Non-confidential
0005-bdd5-27be-d055-3c82 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:50 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Frequency range in which Energy Storage shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | Frequency range in which Energy Storage (in demand mode) shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | Only in demand mode never in generation mode | [6 empty] | Non-confidential
0005-4869-8542-d180-e941 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:49 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Each TSO shall test parts of its Restoration Plan based on computer simulation, in coordination with DSO and Significant Grid Users identified in the Restoration plan, at least every five years. The TSO shall define these simulation tests in a dedicated testing procedure covering at least: | Each TSO shall test the critical parts of its Restoration Plan based on computer simulation, in coordination with DSO and Significant Grid Users identified in the Restoration plan, at least every five years. The TSO shall define these simulation tests in a dedicated testing procedure covering at least: | The TSO shall identify the critical aspects of the Plan and ensure testing of those parts. | [6 empty] | Non-confidential
0005-969d-9ccd-2fcc-d479 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 18:18:37 | Thomas Willson |  | final | The Network Code ER refers to the same classification of generating plants (A-B-C-D) introduced in NC RfG. In an Emergency or Restoration an operational strategy is to have intentional islands and avoiding a complete blackout. | Rethink the ABCD classification introduced in NC RfG and reused in other NCs. ACER's requirement was to use the voltage level. A=LV, B=MV, C=HV, D=EHV or similar seems to be more appropriate. Generating plants along a line of a specific voltage level will behave the same with this approach. | Electrical islands within an electrical power system or horizontal system splits (eg. wider frequency ranges for distribution networks) have boundaries at breakers - usually at substations. |  |  | technical |  |  |  | Non-confidential
0005-4855-c3c1-7eb6-4a13 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:53 | Rothermann Philippe |  | final |  |  | There should be an exception for river power plants. If the river is in flood, operational actions on the power plant will lead to increased restrictions on the flow of water in the river. In flood situations, these power plants should primarily ensure the hydrologycal safety and secondly the the reliability of the electrical system. In national laws, it is surely priorised like that. We recommend the exclusion of nuclear power plants from automatic high frequency control scheme because the restart of these power plants takes a lot of time. During the Night this power is needed and there is no solar power. | [6 empty] | Non-confidential
0005-e4bd-8560-d1e5-4c85 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:52 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | The automatic Low Frequency Demand Disconnection scheme of the System Defence Plan shall have the following parameters: | The automatic Low Frequency Demand Disconnection scheme of the System Defence Plan shall have the following parameters respecting all related NCs (NC RfG, NC DC, NC HVDC): | This shall avoid an undermining of the provisions of other Network Codes. | [6 empty] | Non-confidential
0005-6fb5-d362-d1e4-f934 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:51 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Each TSO shall review its Restoration Plan to assess its effectiveness, at least every 5 years. | To assess its effectiveness, each TSO shall review its Restoration Plan at least every year and before implementation of any modernisation of equipment or grid structure having impact on the System Restoration. | It cannot be true that the TSO can change his grid structure or equipment and wait 5 years before reviewing the System Restoration Plan! | [6 empty] | Non-confidential
0005-e4bd-c3fe-cf8d-6311 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:54 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Table 1 - figures missing. | - | The document states that the figures are under review. The figures should obviously respond to security requirements of the European power systems, but should also be coherent with existing capabilities of equipment and should therefore be justified through a cost benefit analysis. The figures that will be considered should avoid costly retrofits of existing low frequency demand disconnection schemes implemented by DSOs in several European countries. Notwithstanding the economic justification, the considered accuracy on frequency measurement and the overall performance of the proposed scheme should not be a technical burden to reach. The Working Group 3 of the TC8X of CENELEC (TC8X-WG3) has recently produced technical specifications (EN 50549-1 & EN 5049-2) and a standard (EN 50438) on requirements for generators connected to the distribution system. Amongst others, these technical specifications and standards specify the requirement proposed by ENTSOE in the NC RfG to reduce active power generated in case of high frequency. While completing this work, it appeared that no suitable standard is currently available for frequency measurement on electrical networks. The IEC 61000-4-30 standard is considered insufficient with regard to the measurement of frequency during dynamic behaviour of power systems. Therefore TC8X-WG3 is willing to launch the drafting of such a standard. If approved by CENELEC the drafting work for a standard on frequency measurement on electrical networks will probably require the collaboration of various technical Committees of CENELEC as well as, possibly, TSOs, DSOs and manufacturer experts. Without such approach, it seems therefore difficult to define the expected technical performances of LFDD in the NC ER. ENTSO-E mentioned that they are launching a study to confirm the parameters of the LFDD scheme. DSOs would be interested in being informed on the assumptions/conclusions of such study. | [6 empty] | Non-confidential
0005-6fb5-5e6e-cf28-c319 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:53 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | When the TSO identifies the need to adapt the Restoration Plan, it shall amend its Restoration Plan and implement these amendments in accordance with Article 21. | When the TSO identifies the need to adapt the Restoration Plan, it shall amend its Restoration Plan and implement these amendments in accordance with Article 21. Any amendment will be subject to consultation. | where on review a need to amend the System Defence or Restoration Plans is determined, then any amendment must be subject to consultation – provision should be included reflecting this. | [6 empty] | Non-confidential
0005-6f65-c3ec-d5b2-1a7a | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 23:56:22 | Gunnar Kaestle | Clausthal University of Technology | final | Term: Resynchronisation | Add: ..by converging the frequencies of the two Synchronised Regions and connecting them at the Resynchronisation Point | Prior to connection it is recommened to converge the frequencies of the two Regions. |  |  | technical |  |  |  | Non-confidential
0005-6f8d-5e50-d0b9-f1b3 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:47 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design a Restoration Plan, in coordination and agreement with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | This Plan shall not only be consulted but also be agreed by all involved parties. | [6 empty] | Non-confidential
0005-2195-4ece-cf8c-c016 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:54 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | ENTSO-E shall establish and regularly convene a stakeholder advisory group which shall represent the views of stakeholders to ENTSO-E. The stakeholder advisory group shall include a broad representation of relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder advisory group as observers. | ENTSO-E shall establish and regularly convene a stakeholder committee which shall represent the views of stakeholders to ENTSO-E. The stakeholder committee shall include a broad representation of DSOs, Generators and relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder committee as observers. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. DSOs play a special role in this NC, and should therefore be mentioned seperately and not under the umbrella of the 'relevant' stakeholders. | [6 empty] | Non-confidential
0005-48a5-103c-d35a-4eb8 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 23:56:22 | Gunnar Kaestle | Clausthal University of Technology | final | Term: Synchronised Region | Change Term from "Synchronised Region" to "Un-Synchronised Region" | Term sounds inappropriate as the two regions are not synchronised but rather have to be synchronised in the future ("Region to be synchronised with another regigion"). The definition says "*not* synchronised with the rest of the Synchronous Area". |  |  | technical |  |  |  | Non-confidential
0005-e4d1-75a2-d056-b374 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:51 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | (a) Existing and New Power Generating Modules of type B, C and D according to the criteria defined in Article 3(6) of [NC RfG]; | (a) Existing Power Generating Modules of type B, C, D and New Power Generating Modules of type A, B, C and D according to the criteria defined in Article 3(6) of [NC RfG]; | Within the scope of the Network Code, Significant Grid Users are defined as: Existing and New Power Generating Modules of type B, C and D according to the criteria defined in Article 3(6) of [NC RfG]; But when reading the NC, it seems as if it also applies to type A Power Generation Modules. So, why these are not included in the previous definition? | [6 empty] | Non-confidential
0005-e4bd-9cb2-d181-6bab | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:49 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | characteristics of its Network. | characteristics of the Network in its control area. | Also DSO networks inside his control area must be considered. | [6 empty] | Non-confidential
0005-6f8d-007e-d2f6-4e76 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 23:56:22 | Gunnar Kaestle | Clausthal University of Technology | final | Definition of Significant Grid User | Ponder about the relevance of power generating modules of type A: either they are relevant and then they should be introduced in the definiton of a significant grid user, or they are not relevant, then the term Significant Grid User will work fine without the addition of type A generators in the later following NC ER text. | In the text of the NC ER, the use of the term Significant Grid User is almost in each occurance complemented by type A Generating Modules. |  |  | technical |  |  |  | Non-confidential
0005-e4bd-75a2-d056-7ef1 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:53 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | HVDC Systems and DC-connected Power Park Modules. | Existing and new HVDC Systems and DC-connected Power Park Modules. | Make this part in line with a and b to prevent discrimination | [6 empty] | Non-confidential
0005-6fb5-c3c1-7dee-3d2e | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:54 | Rothermann Philippe |  | final |  |  | The system defence plan and the restoration plan are periodically controlled and adapted. But after a disturbance in the power grid, the plans should also be verified and adapted if necessary. | [6 empty] | Non-confidential
0005-4855-00ae-d11d-33cc | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:51 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | the measures are economically efficient; and | the measures are over all economically efficient for all participants; | The concept of an “economically efficient" restoration is ambiguous, as it has to be put in the context of the time it takes to fully restore the service. It should not only be economically efficient for the TSO! It could be applicable to the provision of black-start capabilities or any other preventive action, but it is not clear how the concept applies to the actual restoration actions. | [6 empty] | Non-confidential
0005-4869-9cfa-d4ea-9d29 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 23:56:23 | Gunnar Kaestle | Clausthal University of Technology | final | The Network Code ER refers to the same classification of generating plants (A-B-C-D) introduced in NC RfG. In an Emergency or Restoration an operational strategy is to have intentional islands and avoiding a complete blackout. | Rethink the ABCD classification introduced in NC RfG and reused in other NCs. ACER's requirement was to use the voltage level. A=LV, B=MV, C=HV, D=EHV or similar seems to be more appropriate. Generating plants along a line of a specific voltage level will behave the same with this approach. | Electrical islands within an electrical power system or horizontal system splits (eg. wider frequency ranges for distribution networks) have boundaries at breakers - usually at substations. |  |  | technical |  |  |  | Non-confidential
0005-2145-ad7e-e4ea-7f78 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:39:14 | Markus Hemmer | EnBW | final | Secure Transmission System operation can be made possible only if there is an obligation for the TSOs, Distribution System Operators (DSOs) and Significant Grid Users to cooperate and to meet the relevant minimum technical requirements for the operation of the interconnected Transmission Systems as one entity. | Secure Transmission System operation can be made possible only if there is an obligation for the TSOs, Distribution System Operators (DSOs) and Significant Grid Users to cooperate and to meet the relevant minimum technical requirements, agreed by each party, for the operation of the interconnected Transmission Systems as one entity. | This minimal technical requirements can not be determined by one party for others, e.g. Grid Operators to facilities of Power Generators. The needs and feasabilities of this assets is best known to their owners. With the obligation to cooperate it is ensured that the Power Generation Facility Owners will do their best to ensure a Secure System Operation. | [6 empty] | Non-confidential
0005-e4bd-4ea1-4c4c-527c | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 20:11:07 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | Obligations under this Code should be proportionate and the burden towards actors involved in the electricity market should be balanced in order not to hinder the participation of those actors. The ACER framework guidelines indicate that “network codes shall be elaborated in such a way not to be detrimental to innovation in electric power system operation, maintenance and control” . Demand response is explicitly mentioned as a “trend to be taken into account”. The requirements (cf. comments hereafter) of the draft nework code on emergency and restoration, if applicable to residential consumers, not only deter demand response but also put at risk the integration of innovative technologies necessary to deploy demand response services. ACER framework guidelines for this Code further specify that: “Emergency prevention and restoration plans shall, besides technical needs – consider cost-benefit issues on macroeconomic and market level”, and that “System protection shall limit the consequences of operational disturbances to a minimum”. If residential consumers participating in demand response are characterised as significant grid users by TSOs in the elaboration of their system defence plan as it appears to be possible in the current version of the draft Code, the development of demand response will be jeopardised as constraints will overwhelm advantages, which will cause important consequences with a diminution of the amount of flexibility resources and a drastic reduction of market opportunities. |  |  | legal |  |  |  | Non-confidential
0005-e4bd-1030-d0b9-df50 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:53 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; c) the minimum necessary measures are activated and d) the measures are suitable for foreseeable purposes. | Add the suitability for foreseeable purposes. | [6 empty] | Non-confidential
0005-bdc1-28cc-e35a-1130 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:39:19 | Markus Hemmer | EnBW | final |  | In chapter 4 should be an article that assures the economical compensation of all costs for all involved parties (e.g. loss of market, loss of EOH of assets, fuel costs,…) | The named costs shall be assessed and compensated by NRAs. Otherwise this may lead to discrimination for Stakeholders in an Disturbed area. | [6 empty] | Non-confidential
0005-e4d1-27be-d056-9b56 | V1.0 for Public consultation version | 0 | 0 | - | - | 2014-12-08 16:38:48 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | the minimum necessary measures are activated; and | the necessary measures with minimum impact on society and overall economy are activated; and | the minimum has to be defined to make this statement binding | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-2124 | V1.0 for Public consultation version | 0 | 0 |  |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | General comment- timescales | See the justification. | The Code lacks clear timescales for development and review of the System Defence and Restoration Plans. |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-2125 | V1.0 for Public consultation version | 0 | 0 |  |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | General comment- appeals and derogations | See the justification. | There is no route to appeal or seek a derogation from a decision under the Code, in particular given that some requirements are potentially onerous, unworkable and disproportionate. |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-2126 | V1.0 for Public consultation version | 0 | 0 |  |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | General comment- practical issues | See the justification. | It is not clear how the plans would work with a large quantity of domestic generation and demand which may be in scope. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2127 | V1.0 for Public consultation version | 0 | 0 |  |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | General comment- Type A generators | See the justification. | Requirements on Type A generators are potentially onerous, unworkable and disproportionate. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2128 | V1.0 for Public consultation version | 0 | 0 |  |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | General comment- compliance | See the justification. | The compliance process and the timescales are not justified and will be potentially costly to comply with. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2247 | V1.0 for Public consultation version | 0 | 0 |  |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs | concerned articles 12.3, 12.4, 17.2, 17.3, 19.1. | Duplication of communication channels: in several parts, the code mentions that SGU will receive orders directly from TSOs or indirectly through DSOs. This will often imply duplication of communication channels for consumers. If a consumer is connected to the DSO network, communication should be given trough DSOs: they necessarily are going to have a channel with their users, and could canalize everything for the TSO. In addition TSO giving an order without DSO noticing may create a contradictory action (for example TSO giving and order to decrease demand and DSO disconnecting the lines). Even there is a duplication of communication channels for members in an aggregation: article 37.1.b opens the door for the TSO communication ‘directly or through an aggregator’, what physically requires two channels for them. All the communication channels are already set in NC OS so should not be regulated here again. (The current possible cost of this duplication is €4 billion according to DSOs)
0005-e495-5e7a-d54d-2263 | V1.0 for Public consultation version | 0 | 0 |  |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Chapter 6 |  | How will automatic systems be tested ?
0005-e495-5e7a-d54d-2264 | V1.0 for Public consultation version | 0 | 0 |  |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Chapter 6 |  | There is a lot in the code about testing but what about the training ?
0005-e495-5e7a-d54d-2362 | V1.0 for Public consultation version | 0 | General comment |  |  | 2014-12-08 22:31 | Michael Wilch | RWE | final | - | no specific text proposal. | The NC ER does not provide for derogation mechanisms as it is the case in some other NCs. The derogations mechanisms in the NC RfG and NC DC might not be sufficient to cover possible derogations in this NC. Implementation of measures (for the defence plan and restoration plan) might put overshooting burden to single DSOs or SGUs. A derogation would be a proper solution to handle this problem. The National framework in the MS cannot guarantee derogations, since the NC will be published as a Regulation and will be of higher legal hierarchy. Pursuing ordinary legal avenues in case of disputes does not seem appropriate, as it would delay the finalisation of the Defense Plan/Restoration Plan for years. |  |  | Legal
0005-e495-5e7a-d54d-2363 | V1.0 for Public consultation version | 0 | General comment |  |  | 2014-12-08 22:31 | Michael Wilch | RWE | final | - | no specific text proposal. | All compliance tests should be harmonized throughout all network codes. |  |  | Legal
0005-e495-5e7a-d54d-2129 | V1.0 for Public consultation version | 0 | Recitals | Recitital 4 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | This Network Code on Emergency and Restoration was drafted aiming at setting out clear and objective requirement for TSOs, DSOs and Significant Grid Users in order to contribute to non-discrimination, effective competition and the efficient functioning of the internal electricity market. | This Network Code on Emergency and Restoration was drafted aiming at setting out clear and objective requirements for TSOs, DSOs, Significant Grid Users and other market participants, in order to contribute to non-discrimination, effective competition and the efficient functionnning of the internal market. | The stakeholders impacted by this Network Code are not limited to TSOs, DSOs and Significant Grid Users, due to the inclusion of Chapter 4 (which we understand will be consulted on shortly). Market participants and other participants (for example, Balance Responsible Parties and any settlement administrators) will also be impacted by market suspension and restoration. |  |  | Technical | Editorial
0005-e495-5e7a-d54d-2268 | V1.0 for Public consultation version | 0 | Whereas | 6 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | This network code foresees the establishment by each TSO of a System defense Plan and of a restoration Plan through a three steps approach: … | This network code foreeses the establishment by each TSO, in coordination with DSOs, SGUs and neighbouring TSOs of a System defense Plan and of a restoration Plan through a three steps approach … | The establishment of Defense Plan and Restoration Plan is the TSO's responsibility. However, it shall be done in coordination with stakeholders which will be involved and specifically the DSOs. |  |  | Technical
0005-bd86-7d73-93be-f0c5 | V1.0 for Public consultation version | 1 | 1 | 1 | - | 2014-11-28 14:32:37 | jb test | University of Duisburg-Essen | final | test | test | test | [6 empty] | Non-confidential
0005-e4a9-785d-711d-7436 | V1.0 for Public consultation version | 1 | 1 | 2 | - | 2014-12-04 09:16:38 | Steve Wilkin | ELEXON Limited | final | The provisions of this Network Code shall not apply to the Transmission System or parts of the Transmission System of a Member State which is not operating synchronously with or which is temporarily disconnected from the rest of the Synchronous Area provided it is not the consequence of a Disturbance. | See comment. | It is not clear to us what this paragraph means. Therefore it has an uncertain impact, as far as we are concerned on the market arrangements. Could this requirement please be clarified. For example, would market suspension (Chapter 4) not apply to those parts temporarily disconnected? This would seem perverse if the rest of the market (bidding zone) were suspended and indeed may be particularly difficult to implement if the part disconnected does not align with a bidding zone. |  |  | technical |  |  |  | Non-confidential
0005-bdc1-00ae-cf8e-b73e | V1.0 for Public consultation version | 1 | 1 | 2 | - | 2014-12-08 16:38:49 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | The provisions of this Network Code shall not apply to the Transmission System or parts of the Transmission System of a Member State which is not operating synchronously with or which is temporarily disconnected from the rest of the Synchronous Area provided it is not the consequence of a Disturbance. | The provisions of this Network Code shall not apply to the Transmission System and all underlying Distribution Sytems or parts of the Transmission System and all underlying Dsitribution Systems operating synchronously with or which is temporarily disconnected from the rest of the Synchronous Area provided it is not the consequence of a Disturbance. | If the provisions do not apply to the Transmission System, it seems obvious that they do not apply to all Distribution Systems connected to that Transmission System and equally not apply to all underlying Distribution Systems. |  |  | technical |  |  |  | Non-confidential
0005-968a-569e-e9c7-17ca | V1.0 for Public consultation version | 1 | 1 | 2 | - | 2014-11-28 15:51:10 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The provisions of this Network Code shall not apply to the Transmission System or parts of the Transmission System of a Member State which is not operating synchronously with or which is temporarily disconnected from the rest of the Synchronous Area provided it is not the consequence of a Disturbance. | The provisions of this Network Code shall not apply to the Transmission System and all underlying Distribution Sytems or parts of the Transmission System and all underlying Dsitribution Systems operating synchronously with or which is temporarily disconnected from the rest of the Synchronous Area provided it is not the consequence of a Disturbance. | If the provisions do not apply to the Transmission System, it seems obvious that they do not apply to all Distribution Systems connected to that Transmission System and equally not apply to all underlying Distribution Systems. |  |  | technical |  |  |  | Non-confidential
0005-e495-c3ce-d67a-b539 | V1.0 for Public consultation version | 1 | 1 | 2 | - | 2014-12-08 23:56:21 | Gunnar Kaestle | Clausthal University of Technology | final | 1(2) excludes Transmission Systems which are not operating synchronously with the rest of the Synchronous Area | Please be more precisely with the wording. | What is the case with transmission systems in GB and IE: They are not operating synchronously with the rest of the Synchronous Area (of CE). |  |  | legal |  |  |  | Non-confidential
0005-bdad-376a-d35a-d188 | V1.0 for Public consultation version | 1 | 1 | 2 | - | 2014-12-08 23:56:21 | Gunnar Kaestle | Clausthal University of Technology | final | This network code shall not apply to Aland Island | Remove the sentence on Aland Islands. | Unclear why this islanded network is mentioned, is it because of the peculiar electrical situation or being an autonomous region? In how many other Network Codes are the Aland islands especially mentioned? |  |  | legal |  |  |  | Non-confidential
0005-bdd5-27bb-3224-6f70 | V1.0 for Public consultation version | 1 | 1 | 2 | - | 2014-12-08 18:18:37 | Thomas Willson |  | final | 1(2) excludes Transmission Systems which are not operating synchronously with the rest of the Synchronous Area | Please be more precise with the wording. | What is the case with the TSO in GB and IE: They are not operating synchronously with the rest of the Synchronous Area (of CE). |  |  | legal |  |  |  | Non-confidential
0005-bdad-373e-0e46-2c88 | V1.0 for Public consultation version | 1 | 1 | 2 | - | 2014-12-08 17:09:25 | Paul Doyle | ESB Generation & Wholesale Markets | final | The provisions of this Network Code shall not apply to the Transmission System or parts of the Transmission System of a Member State which is not operating synchronously with or which is temporarily disconnected from the rest of the Synchronous Area provided it is not the consequence of a Disturbance. | The provisions of this Network Code shall not apply to the Transmission System and all underlying Distribution Sytems or parts of the Transmission System and all underlying Dsitribution Systems operating synchronously with or which is temporarily disconnected from the rest of the Synchronous Area provided it is not the consequence of a Disturbance. | If the provisions do not apply to the Transmission System, it seems obvious that they do not apply to all Distribution Systems connected to that Transmission System and equally not apply to all underlying Distribution Systems. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2269 | V1.0 for Public consultation version | 1 | 1 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | The provisions of this Network Code shall not apply to the Transmission System or parts of the Transmission System of a Member State which is not operating synchronously with or which is temporarily disconnected from the rest of the Synchronous Area provided it is not the consequence of a Disturbance. | The provisions of this Network Code shall not apply to the Transmission System and all connected and underlying Distribution Systems or parts of the Transmission System and all connected and underlying Dsitribution Systems operating synchronously with or which is temporarily disconnected from the rest of the Synchronous Area provided it is not the consequence of a Disturbance. | If the provisions do not apply to the Transmission System, it seems obvious that they do not apply to all Distribution Systems connected to that Transmission System and equally not apply to all underlying Distribution Systems. |  |  | Technical
0005-e495-5e7a-d54d-1953 | V1.0 for Public consultation version | 1 | 1 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The provisions of this Network Code shall not apply to the Transmission System or parts of the Transmission System of a Member State which is not operating synchronously with or which is temporarily disconnected from the rest of the Synchronous Area provided it is not the consequence of a Disturbance. | The provisions of this Network Code shall not apply to the Transmission System and all underlying Distribution Sytems or parts of the Transmission System and all underlying Dsitribution Systems operating synchronously with or which is temporarily disconnected from the rest of the Synchronous Area provided it is not the consequence of a Disturbance. | If the provisions do not apply to the Transmission System, it seems obvious that they do not apply to all Distribution Systems connected to that Transmission System and equally not apply to all underlying Distribution Systems.
0005-e495-5e7a-d54d-2130 | V1.0 for Public consultation version | 1 | 1 | 2 |  | 2014-12-08 21:33 | Wilch | RWE | final | The provisions of this Network Code shall not apply to the Transmission System or parts of the Transmission System of a Member State which is not operating synchronously with or which is temporarily disconnected from the rest of the Synchronous Area provided it is not the consequence of a Disturbance. |  | 3 general comments here: (1) this provision is not clear and its wording seems to be different from the one used in the NC OS. What does "temporarily" mean- is it 1 second, 1 minute, 1 day, 1 week? (2) Also, does it mean that if the disconnection is a result of Disturbance, the Code applies? (3) Please note that according to the EMR tool, Disturbance is defined in the Operational Handbook which has no legal value towards third-parties. Therefore, a definition of Disturbance should be inserted. |  |  | Technical | Fundamental
0005-2181-372e-d616-e07f | V1.0 for Public consultation version | 1 | 1 | 3 | - | 2014-12-08 23:56:21 | Gunnar Kaestle | Clausthal University of Technology | final | term: "power system" & "system" | Change both terms into "electrical power systems" | According to the International Electrotechnical Vocabulary (ref 601-01-02), the precise term is "electrical power system" |  |  | legal |  |  |  | Non-confidential
0005-6fa1-39dd-711c-8431 | V1.0 for Public consultation version | 1 | 1 | 4 | - | 2014-12-04 09:17:44 | Steve Wilkin | ELEXON Limited | final | In Member States where more than one TSO exists, this Network Code shall apply to all TSOs within that Member State. Where a TSO does not have a function relevant to one or some obligations under this Network Code, Member States may under the national regulatory regime provide that the responsibility to comply with one or some obligations under this Network Code is assigned to one or more different TSO(s). In case of such assignment, the Network Code shall apply accordingly to the TSO(s) to which responsibilities have been assigned. | In Member States where more than one TSO exists, this Network Code shall apply to all TSOs within that Member State. Where a TSO does not have a function relevant to one or some obligations under this Network Code, Member States may under the national regulatory regime provide that the responsibility to comply with one or some obligations under this Network Code is assigned to one or more different TSO(s). In case of such assignment, the Network Code shall apply accordingly to the TSO(s) to which responsibilities have been assigned. For the avoidance of doubt this Article is without prejudice to the Network Code on Electricity Balancing where it permits delegation or assignment of TSO functions to third parties. Where relevant, such third parties may then be required to undertake some of the functions set out in Chapter 4 of this Network Code. | Chapter 4 applies to markets and therefore to market operators such as NEMOs, but also those third parties to whom responsibilty has been delegated or assigned pursuant to Article 9 of the most recent public draft of the Network Code on Electricity Balancing. |  |  | technical |  |  |  | Non-confidential
0005-96c5-5e6e-d182-75bb | V1.0 for Public consultation version | 1 | 1 | 6 | - | 2014-12-08 16:38:55 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | For the purpose of this Network Code, the classification of Existing Power Generating Modules and Existing Demand Facilities pursuant to Article 1(5) of [NC OS] shall apply. The Significant Grid Users within the scope of this Network Code shall be: (a) Existing and New Power Generating Modules of type B, C and D according to the criteria defined in Article 3(6) of [NC RfG]; (b) Existing and New Transmission Connected Demand Facilities according to the criteria defined in Article 5 and Article 8 of [NC DC] and all Existing and New Transmission Connected Closed Distribution Networks; (c) Significant Demand Facilities, Closed Distribution Networks and Aggregators according to the [NC DC], in the case where they provide Demand Side Response directly to the TSO; (d) Redispatching Aggregators and Providers of Active Power Reserve according to the [NC LFCR]; and (e) HVDC Systems and DC-connected Power Park Modules. | For the purpose of this Network Code, the classification of Existing Power Generating Modules and Existing Demand Facilities pursuant to Article 1(5) of [NC OS] shall apply. Within the scope of this Network Code the definition of Significant Grid Users pursuant to Articel 1(5) of [NC OS] shall apply. | The definition in the NC ER is non consistent with the one in NC OS (the paragraph '(e) HVDC Systems and DC-connected Power Park Modules' has been added. Since the NC OS is the umbrella code, the definition has to be adapted in the NC OS, and not in the NC ER. Definiton should not be repeated. Delete sub paragraphs a, b, c, d and e. |  |  | technical |  |  |  | Non-confidential
0005-48a5-9cce-0de2-b0b7 | V1.0 for Public consultation version | 1 | 1 | 6 | - | 2014-12-08 17:09:28 | Paul Doyle | ESB Generation & Wholesale Markets | final | For the purpose of this Network Code, the classification of Existing Power Generating Modules and Existing Demand Facilities pursuant to Article 1(5) of [NC OS] shall apply. The Significant Grid Users within the scope of this Network Code shall be: (a) Existing and New Power Generating Modules of type B, C and D according to the criteria defined in Article 3(6) of [NC RfG]; (b) Existing and New Transmission Connected Demand Facilities according to the criteria defined in Article 5 and Article 8 of [NC DC] and all Existing and New Transmission Connected Closed Distribution Networks; (c) Significant Demand Facilities, Closed Distribution Networks and Aggregators according to the [NC DC], in the case where they provide Demand Side Response directly to the TSO; (d) Redispatching Aggregators and Providers of Active Power Reserve according to the [NC LFCR]; and (e) HVDC Systems and DC-connected Power Park Modules. | For the purpose of this Network Code, the classification of Existing Power Generating Modules and Existing Demand Facilities pursuant to Article 1(5) of [NC OS] shall apply. Within the scope of this Network Code the definition of Significant Grid Users pursuant to Articel 1(5) of [NC OS] shall apply. | The definition in the NC ER is non consistent with the one in NC OS (the paragraph '(e) HVDC Systems and DC-connected Power Park Modules' has been added. Since the NC OS is the umbrella code, the definition has to be adapted in the NC OS, and not in the NC ER. Definiton should not be repeated. Delete sub paragraphs a, b, c, d and e. |  |  | legal |  |  |  | Non-confidential
0005-bdae-cb92-ea2b-c860 | V1.0 for Public consultation version | 1 | 1 | 6 | - | 2014-11-28 15:51:11 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | HVDC Systems and DC-connected Power Park Modules. | Existing and new HVDC Systems and DC-connected Power Park Modules. | Make this part in line with a and b to prevent discrimination |  |  | legal |  |  |  | Non-confidential
0005-96b1-4ead-c993-4ebd | V1.0 for Public consultation version | 1 | 1 | 6 | - | 2014-12-08 19:51:12 | Roland Tual | SEDC | final | Existing and New Transmission Connected Demand Facilities according to the criteria defined in Article 5 and Article 8 of [NC DC] and all Existing and New Transmission Connected Closed Distribution Networks | [8 empty] | confidential
0005-bdc2-3f10-e70b-9962 | V1.0 for Public consultation version | 1 | 1 | 6 | - | 2014-11-28 15:51:11 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | For the purpose of this Network Code, the classification of Existing Power Generating Modules and Existing Demand Facilities pursuant to Article 1(5) of [NC OS] shall apply. The Significant Grid Users within the scope of this Network Code shall be: (a) Existing and New Power Generating Modules of type B, C and D according to the criteria defined in Article 3(6) of [NC RfG]; (b) Existing and New Transmission Connected Demand Facilities according to the criteria defined in Article 5 and Article 8 of [NC DC] and all Existing and New Transmission Connected Closed Distribution Networks; (c) Significant Demand Facilities, Closed Distribution Networks and Aggregators according to the [NC DC], in the case where they provide Demand Side Response directly to the TSO; (d) Redispatching Aggregators and Providers of Active Power Reserve according to the [NC LFCR]; and (e) HVDC Systems and DC-connected Power Park Modules. | For the purpose of this Network Code, the classification of Existing Power Generating Modules and Existing Demand Facilities pursuant to Article 1(5) of [NC OS] shall apply. Within the scope of this Network Code the definition of Significant Grid Users pursuant to Articel 1(5) of [NC OS] shall apply. | The definition in the NC ER is non consistent with the one in NC OS (the paragraph '(e) HVDC Systems and DC-connected Power Park Modules' has been added. Since the NC OS is the umbrella code, the definition has to be adapted in the NC OS, and not in the NC ER. Definiton should not be repeated. Delete sub paragraphs a, b, c, d and e. |  |  | legal |  |  |  | Non-confidential
0005-6fa1-2915-25ef-3d32 | V1.0 for Public consultation version | 1 | 1 | 6 | - | 2014-12-08 17:01:11 | Jasmina PIERRE | EdF | final | 6. […] The Significant Grid Users within the scope of this Network Code shall be: […] e) HVDC Systems and DC-connected Power Park Modules. | 6. […] The Significant Grid Users within the scope of this Network Code shall be: […] e) Existing and New HVDC Systems and DC-connected Power Park Modules. | Need for consistency with Power Generating Modules (article 1.6.a) and Demand facilities (article 1.6.b) |  |  | technical |  |  |  | Non-confidential
0005-4869-9cce-0bee-5d1f | V1.0 for Public consultation version | 1 | 1 | 6 | - | 2014-12-08 17:09:27 | Paul Doyle | ESB Generation & Wholesale Markets | final | HVDC Systems and DC-connected Power Park Modules. | Existing and new HVDC Systems and DC-connected Power Park Modules. | Make this part in line with a and b to prevent discrimination |  |  | legal |  |  |  | Non-confidential
0005-bdad-75ed-4b20-1454 | V1.0 for Public consultation version | 1 | 1 | 6 | - | 2014-12-08 20:11:07 | European Committee of Domestic Equipment Manufacturers |  | final |  | Exclude residential consumers from the scope of this network code | Considering that a residential consumer per se is connected exclusively to the lowest voltage network, that its consumption and generation potentials are marginal in comparison with the other actors of the electricity system, and that cases of emergency and blackout are deemed by essence to be exceptional, the burden of the preventive requirements described in the present draft Code shall not apply to any residential consumer. A household per se does not have a significant impact on system cross-border performance, and shall therefore be explicitly excluded from the scope of this Network Code. Moreover, households shall not be treated as any other actor of the grid. As end-users they are the reason of being of the electricity system and should be encouraged and not penalised to participate more actively for a flexible energy system by providing demand response. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2270 | V1.0 for Public consultation version | 1 | 1 | 6 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | For the purpose of this Network Code, the classification of Existing Power Generating Modules and Existing Demand Facilities pursuant to Article 1(5) of [NC OS] shall apply. The Significant Grid Users within the scope of this Network Code shall be: (a) Existing and New Power Generating Modules of type B, C and D according to the criteria defined in Article 3(6) of [NC RfG]; (b) Existing and New Transmission Connected Demand Facilities according to the criteria defined in Article 5 and Article 8 of [NC DC] and all Existing and New Transmission Connected Closed Distribution Networks; (c) Significant Demand Facilities, Closed Distribution Networks and Aggregators according to the [NC DC], in the case where they provide Demand Side Response directly to the TSO; (d) Redispatching Aggregators and Providers of Active Power Reserve according to the [NC LFCR]; and (e) HVDC Systems and DC-connected Power Park Modules. | For the purpose of this Network Code, the classification of Existing Power Generating Modules and Existing Demand Facilities pursuant to Article 1(5) of [NC OS] shall apply. Within the scope of this Network Code the definition of Significant Grid Users pursuant to Articel 1(5) of [NC OS] shall apply. (a) Existing and New Power Generating Modules of type B, C and D according to the criteria defined in Article 3(6) of [NC RfG]; (b) Existing and New Transmission Connected Demand Facilities according to the criteria defined in Article 5 and Article 8 of [NC DC] and all Existing and New Transmission Connected Closed Distribution Networks; (c) Significant Demand Facilities, Closed Distribution Networks and Aggregators according to the [NC DC], in the case where they provide Demand Side Response directly to the TSO; (d) Redispatching Aggregators and Providers of Active Power Reserve according to the [NC LFCR]; and (e) HVDC Systems and DC-connected Power Park Modules. | The definition in the NC ER is non consistent with the one in NC OS (the paragraph '(e) HVDC Systems and DC-connected Power Park Modules' has been added. Since the NC OS is the umbrella code, the definition has to adapted in the NC OS, and not in the NC ER. Definiton should not be repeated. |  |  | Legal
0005-e495-5e7a-d54d-1954 | V1.0 for Public consultation version | 1 | 1 | 6 | a | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | (a) Existing and New Power Generating Modules of type B, C and D according to the criteria defined in Article 3(6) of [NC RfG]; | (a) Existing Power Generating Modules of type B, C, D and New Power Generating Modules of type A, B, C and D according to the criteria defined in Article 3(6) of [NC RfG]; | Within the scope of the Network Code, Significant Grid Users are defined as: Existing and New Power Generating Modules of type B, C and D according to the criteria defined in Article 3(6) of [NC RfG]; But when reading the NC, it seems as if it also applies to type A Power Generation Modules. So, why these are not included in the previous definition?
0005-e495-5e7a-d54d-1955 | V1.0 for Public consultation version | 1 | 1 | 6 | e | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | HVDC Systems and DC-connected Power Park Modules. | Existing and new HVDC Systems and DC-connected Power Park Modules. | Make this part in line with a and b to prevent discrimination
0005-e495-5e7a-d54d-1956 | V1.0 for Public consultation version | 1 | 1 | 6 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | For the purpose of this Network Code, the classification of Existing Power Generating Modules and Existing Demand Facilities pursuant to Article 1(5) of [NC OS] shall apply. The Significant Grid Users within the scope of this Network Code shall be: (a) Existing and New Power Generating Modules of type B, C and D according to the criteria defined in Article 3(6) of [NC RfG]; (b) Existing and New Transmission Connected Demand Facilities according to the criteria defined in Article 5 and Article 8 of [NC DC] and all Existing and New Transmission Connected Closed Distribution Networks; (c) Significant Demand Facilities, Closed Distribution Networks and Aggregators according to the [NC DC], in the case where they provide Demand Side Response directly to the TSO; (d) Redispatching Aggregators and Providers of Active Power Reserve according to the [NC LFCR]; and (e) HVDC Systems and DC-connected Power Park Modules. | For the purpose of this Network Code, the classification of Existing Power Generating Modules and Existing Demand Facilities pursuant to Article 1(5) of [NC OS] shall apply. Within the scope of this Network Code the definition of Significant Grid Users pursuant to Articel 1(5) of [NC OS] shall apply. | The definition in the NC ER is non consistent with the one in NC OS (the paragraph '(e) HVDC Systems and DC-connected Power Park Modules' has been added. Since the NC OS is the umbrella code, the definition has to be adapted in the NC OS, and not in the NC ER. Definiton should not be repeated. Delete sub paragraphs a, b, c, d and e.
0005-e495-5e7a-d54d-2131 | V1.0 for Public consultation version | 1 | 1 | 6 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | The Significant Grid Users within the scope of this Network Code shall be: | See the justification. | It remains a fundamental problem for stakeholders where the term 'Significant Grid User' varies, in some cases, by Code, whilst there are numerous cross references to other Network Codes in the NC ER itself. For example, just in Article 1(6) there are references to the NC OS, LFCR, RfG and DCC which all have different definitions of SGU...so which one applies here? |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1714 | V1.0 for Public consultation version | 1 | 1 | 6 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | The Significant Grid Users within the scope of this Network Code shall be: | Xyz | It remains a fundamental problem for stakeholders where the term ‘Significant Grid User’ varies, in some cases, by Code, whilst there are numerous cross references to other Network Codes in this NC E&R document. For example, just in the Art 1 (6) there are references to the NC OS, NC LFCR, NC RfG and NC DC which have different definitions of SGU….so which applies here??!!
0005-e4a9-373d-31c0-d8c6 | V1.0 for Public consultation version | 1 | 1 | - | - | 2014-12-08 18:20:21 | Thomas Willson |  | final | General | remove paragraph 7, page 3 of the introduction. | Introduction: (7) promises harmonised requirements, but it is unclear how this can be reached if member states chose individual solutions. |  |  | legal |  |  |  | Non-confidential
0005-6fa1-8711-2333-b926 | V1.0 for Public consultation version | 1 | 1 | - | - | 2014-12-08 17:01:11 | Jasmina PIERRE | EdF | final | - | - | General comments |  |  | technical |  |  |  | Non-confidential | 0005-6fa1-8711-2333-b926-2014 12 08 - ENTSOE - NC Emergerncy and Restoration - EDF Response - vf.pdf
0005-bdd5-75db-30f8-18ee | V1.0 for Public consultation version | 1 | 1 | - | - | 2014-12-08 18:20:39 | Thomas Willson |  | final | General | Add paragraph to Article 1 to this effect | It should be stated that in periods of overfrequency, renewable energy sources should not be discriminated against when shedding generation |  |  | legal |  |  |  | Non-confidential
0005-2195-4e90-0d1a-45a4 | V1.0 for Public consultation version | 1 | 1 | - | - | 2014-12-08 17:09:30 | Paul Doyle | ESB Generation & Wholesale Markets | final | - |  | The NC ER does not provide for derogation mechanism as it is the case in other NCs. Implementation of measures (for the defence plan and restoration plan) might put overshooting burden to single DSOs or SGUs. A derogation would be a proper solution to handle this problem. |  |  | legal |  |  |  | Non-confidential
0005-4891-373e-0cb6-165d | V1.0 for Public consultation version | 1 | 1 | - | - | 2014-12-08 17:09:32 | Paul Doyle | ESB Generation & Wholesale Markets | final | - |  | General remark on the information exchange between grid operators and Grid Users. "No duplication of information channels, no direct orders/communication bypassing the DSO." |  |  | technical |  |  |  | Non-confidential
0005-96c5-ac8c-0cb6-bcc1 | V1.0 for Public consultation version | 1 | 1 | - | - | 2014-12-08 17:09:33 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power | Each TSO shall be entitled to disconnect new Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power | No communication channels are installed for the majority of Type A & type B PGMs. This would mean a violation of the basic principle: RfG is only for NEW installations |  |  | technical |  |  |  | Non-confidential
0005-2196-db6e-e76f-2286 | V1.0 for Public consultation version | 1 | 1 | - | - | 2014-11-28 15:51:12 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | - |  | The NC ER does not provide for derogation mechanism as it is the case in other NCs. Implementation of measures (for the defence plan and restoration plan) might put overshooting burden to single DSOs or SGUs. A derogation would be a proper solution to handle this problem. |  |  | legal |  |  |  | Non-confidential
0005-bd86-b45e-e89b-71f5 | V1.0 for Public consultation version | 1 | 1 | - | - | 2014-11-28 15:51:13 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | - |  | General remark on the information exchange between grid operators and Grid Users. "No duplication of information channels, no direct orders/communication bypassing the DSO." |  |  | technical |  |  |  | Non-confidential
0005-969e-7dae-e837-d3a7 | V1.0 for Public consultation version | 1 | 1 | - | - | 2014-11-28 15:51:14 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power | Each TSO shall be entitled to disconnect new Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power | No communication channels are installed for the majority of Type A & type B PGMs. This would mean a violation of the basic principle: RfG is only for NEW installations |  |  | technical |  |  |  | Non-confidential
0005-e4d1-01a2-9170-6317 | V1.0 for Public consultation version | 1 | 1 | - | - | 2014-12-05 11:33:48 | Agnieszka Panek |  | final | General comment |  | General remark on the information exchange between TSOs and Grid Users which are connected to the distribution network should be led via DSOs. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-1957 | V1.0 for Public consultation version | 1 | 1 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | - |  | The NC ER does not provide for derogation mechanism as it is the case in other NCs. Implementation of measures (for the defence plan and restoration plan) might put overshooting burden to single DSOs or SGUs. A derogation would be a proper solution to handle this problem.
0005-e495-5e7a-d54d-1958 | V1.0 for Public consultation version | 1 | 1 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | - |  | General remark on the information exchange between grid operators and Grid Users. "No duplication of information channels, no direct orders/communication bypassing the DSO."
0005-e495-5e7a-d54d-1959 | V1.0 for Public consultation version | 1 | 1 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power | Each TSO shall be entitled to disconnect new Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power | No communication channels are installed for the majority of Type A & type B PGMs. This would mean a violation of the basic principle: RfG is only for new installations
0005-e495-5e7a-d54d-1713 | V1.0 for Public consultation version | 1 | 1 |  |  | 2014-12-08 13:31 | Garth Graham | SSE | final | [whereas (3)] This Network Code on Emergency and Restoration was drafted aiming at setting out clear and objective requirements for TSOs, DSOs and Significant Grid Users in order to contribute to… | [whereas (3)] This Network Code on Emergency and Restoration was drafted aiming at setting out clear and objective requirements for TSOs, DSOs, MARKET PARTICIPANTS, NEMOS and Significant Grid Users in order to contribute to…. | The obligations in the Code do not only apply to those listed in whereas (3) but also to market participants who would be affected by any market suspension etc., under Chapter 4.
0005-bdc1-5f7c-e5b2-e9f4 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 16:41:59 | Markus Hemmer | EnBW | final | Synchronised Region means a subpart of a Synchronous Area covered by interconnected TSOs with a common System Frequency not synchronised with the rest of the Synchronous Area; and | Please complete this sentence | see above |  |  | legal |  |  |  | Non-confidential
0005-9675-c590-a1cd-1911 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-04 13:51:20 | Dekinderen Eric | Genrator company | final | Missing definiton : NEMO | NEMO : Nominated Electricity Market Operators | Missing definiton |  |  | technical |  |  |  | Non-confidential
0005-4855-c590-a3c1-96cb | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-04 13:53:34 | Dekinderen Eric | Genrator company | final | Missing definiton : On load tap changer blocking scheme (see Art 16) | To add | To add |  |  | technical |  |  |  | Non-confidential
0005-e4aa-3f2e-e7d3-c702 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-11-28 15:52:13 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Missing definiton : NEMO | add definition | Nominated Electricity Market Operator |  |  | technical |  |  |  | Non-confidential
0005-6f8d-103f-4a58-916a | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 20:11:08 | European Committee of Domestic Equipment Manufacturers |  | final |  | Add a clear definition of significant grid user | There should be a clear definition of how a significant grid user is characterised in this Code in order to understand the impact of its requirements on actors in the market. In its framework guidelines ACER notably requires that “minimum standards shall be defined for each type of significant grid user and shall take into account the voltage level at the grid user’s connection point. The Network Code shall specify the criteria and methodology for the definition of significant grid users. These shall be based on a predefined set of parameters which measure the degree of their impact on cross-border system performance via control area’s security of supply”. The draft Network Code under public consultation fails to comply with the above conditions. |  |  | legal |  |  |  | Non-confidential
0005-6f8d-d39c-0f71-3918 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 17:15:54 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year |  | Backup is not defined and not mentioned in Art. 38 |  |  | technical |  |  |  | Non-confidential
0005-6fb5-104b-2fcc-64eb | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 18:18:38 | Thomas Willson |  | final | introduction: Article 2 of Commission Regulations establishing Network Codes shall apply. | A solution may be that a common glossary, which will be amended regularily in case a new NC with new terminology is needed, is put into force as a special NC only on Terminology. Then, NC codes with a similar area can refer to the same terminology and avoid misinterpretation of the legal text. | It's unclear how Terms and Definitions in other Network Codes, which have so far not entered into force, can be refered to. |  |  | legal |  |  |  | Non-confidential
0005-968a-2f70-e8ff-4a0d | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-11-28 15:52:13 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Missing definiton : On load tap changer blocking scheme (see Art 16) | add definition | Add definition of On load tap changer blocking scheme. |  |  | technical |  |  |  | Non-confidential
0005-486a-3f2e-e89b-5206 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-11-28 15:52:14 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Missing definition: Frequency Leader | Frequency Leader means the TSO managing Frequency within a Synchronised Region in order to restore System Frequency back to Nominal Frequency | Add definition of Frequency Leader |  |  | technical |  |  |  | Non-confidential
0005-e4d2-b422-e70b-d86a | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-11-28 15:52:15 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year |  | Backup is not defined and not mentioned in Art. 38 |  |  | technical |  |  |  | Non-confidential
0005-e4e5-86d5-26b7-3a0e | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 17:01:12 | Jasmina PIERRE | EdF | final | (new) | "System Defence Plan" needs to be defined. | "System Defence Plan" needs to be defined, as "Restoration Plan" already is. |  |  | technical |  |  |  | Non-confidential
0005-969d-375c-0d1a-53fe | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 17:09:34 | Paul Doyle | ESB Generation & Wholesale Markets | final | Bottom-up Re-energisation Strategy means a strategy that does not require the assistance from other TSOs to re-energise part of the system of a TSO; | Bottom-up Re-energisation Strategy means a strategy that does not require the assistance from other TSOs to re-energise (part of) the system of a TSO; | Also valid in case of re-energisation of the complete system . |  |  | technical |  |  |  | Non-confidential
0005-4869-277f-31c0-657c | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 18:18:37 | Thomas Willson |  | final | introduction: Article 2 of Commission Regulations establishing Network Codes shall apply. | A solution may be that a common glossary, which will be amended regularily in case a new NC with new terminology is needed, is put into force as a special NC only on Terminology. Then, NC codes with a similar area can refer to the same terminology and avoid misinterpretation of the legal text. | It's unclear how Terms and Definitions in other Network Codes, which have so far not entered into force, can be refered to. |  |  | legal |  |  |  | Non-confidential
0005-6f65-102e-0d1a-497c | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 17:09:36 | Paul Doyle | ESB Generation & Wholesale Markets | final | Resynchronisation means synchronising two Synchronised Regions by connecting the two Synchronised Regions at the Resynchronisation Point; | Resynchronisation means bringing two Synchronised Regions into synchronous operation and connecting them at the Resynchronisation Point; | Synchronisation is more than blind connecting asynchronous areas! Resynchronisation must be covered by a dedicated procedure. |  |  | technical |  |  |  | Non-confidential
0005-6f79-c40a-d486-9b72 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 23:56:22 | Gunnar Kaestle | Clausthal University of Technology | final | introduction: Article 2 of Commission Regulations establishing Network Codes shall apply. | A solution may be that a common glossary, which will be amended regularily in case a new NC with new terminology is needed, is put into force as a special NC only on Terminology. Then, NC codes with a similar area can refer to the same terminology and avoid misinterpretation of the legal text. | It's unclear how Terms and Definitions in other Network Codes, which have so far not entered into force, can be refered to. |  |  | legal |  |  |  | Non-confidential
0005-4855-102e-0e46-6574 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 17:09:37 | Paul Doyle | ESB Generation & Wholesale Markets | final | Resynchronisation Point means the substation used to connect two Synchronised Regions by closing circuit-breakers; | Resynchronisation Point means the substation where a circuit-breaker is being closed to connect two Synchronised Regions at the moment of resynchronisation; | Also other substations are used but not meanth in this definition. |  |  | technical |  |  |  | Non-confidential
0005-bdc1-c3ec-d486-fede | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 23:56:22 | Gunnar Kaestle | Clausthal University of Technology | final | Term: Demand | Introduce the correct term "load". (compare with reference load) | Described is the residual load (load-generation). The following pairs match: Supply & Demand (macroeconomics), Production & Consumption (microeconomics), Generator & Load (technical terms for electrical souces and sinks) |  |  | technical |  |  |  | Non-confidential
0005-2146-0860-e70b-ed6d | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-11-28 15:51:15 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Bottom-up Re-energisation Strategy means a strategy that does not require the assistance from other TSOs to re-energise part of the system of a TSO; | Bottom-up Re-energisation Strategy means a strategy that does not require the assistance from other TSOs to re-energise (part of) the system of a TSO; | Also valid in case of re-energisation of the complete system . |  |  | technical |  |  |  | Non-confidential
0005-9689-8540-0de2-5b2c | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 17:15:43 | Paul Doyle | ESB Generation & Wholesale Markets | final | Top-down Re-energisation Strategy means a strategy that requires the assistance of other TSOs to re-energise part of the system of a TSO. | Top-down Re-energisation Strategy means a strategy that requires the assistance of other TSOs to re-energise (part of) the system of a TSO. | Also valid in case of re-energisation of the complete system . |  |  | technical |  |  |  | Non-confidential
0005-2181-c5f6-1337-b1e6 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-03 11:09:21 | AXPO Group |  | final | Energy Storage means a device being used for storage of electrical energy and that can be used to balance the system, e.g. water pumped-storage or batteries; | Energy Storage means a device being used for storage of electrical energy and that can be used to balance the system, e.g. batteries; | Regarding Energy Storage: Water isn't a device. It can store potential energy, not electrical energy. |  |  | technical |  |  |  | Non-confidential
0005-bd9a-5680-e89b-f385 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-11-28 15:51:16 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Resynchronisation means synchronising two Synchronised Regions by connecting the two Synchronised Regions at the Resynchronisation Point; | Resynchronisation means bringing two Synchronised Regions into synchronous operation and connecting them at the Resynchronisation Point; | Synchronisation is more than blind connecting asynchronous areas! Resynchronisation must be covered by a dedicated procedure. |  |  | technical |  |  |  | Non-confidential
0005-bd99-373e-0f72-aec3 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 17:15:45 | Paul Doyle | ESB Generation & Wholesale Markets | final | Energy Storage means a device being used for storage of electrical energy and that can be used to balance the system, e.g. water pumped-storage or batteries; | Energy Storage means a device being used for storage of electrical energy or other energy and that can be used to balance the system, e.g. water pumped-storage or batteries; | Water isn't a device. It can store potential energy, not electrical energy. |  |  | technical |  |  |  | Non-confidential
0005-9675-3938-1143-6cfc | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-03 11:09:21 | AXPO Group |  | final | Missing definition | System Defence plan means the summary of all technical and organisational measures to be untertaken to keep the system in Normal State; | Restoration Plan has a definition. Add also a definition for System Defence plan. |  |  | technical |  |  |  | Non-confidential
0005-215a-6620-e963-bc49 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-11-28 15:51:17 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Resynchronisation Point means the substation used to connect two Synchronised Regions by closing circuit-breakers; | Resynchronisation Point means the substation where a circuit-breaker is being closed to connect two Synchronised Regions at the moment of resynchronisation; | Also other substations are used but not meanth in this definition. |  |  | technical |  |  |  | Non-confidential
0005-6fa1-104c-0d1a-f812 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 17:15:47 | Paul Doyle | ESB Generation & Wholesale Markets | final | missing text | Restoration Plan has a definition. Add also a definition for System Defence plan. | Integrity of Article 2 |  |  | technical |  |  |  | Non-confidential
0005-9676-6602-e76f-49bb | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-11-28 15:52:10 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Top-down Re-energisation Strategy means a strategy that requires the assistance of other TSOs to re-energise part of the system of a TSO. | Top-down Re-energisation Strategy means a strategy that requires the assistance of other TSOs to re-energise (part of) the system of a TSO. | Also valid in case of re-energisation of the complete system . |  |  | technical |  |  |  | Non-confidential
0005-2181-ac50-0cb6-2b25 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 17:15:49 | Paul Doyle | ESB Generation & Wholesale Markets | final | Missing definiton : NEMO | add definition | Nominated Electricity Market Operator |  |  | technical |  |  |  | Non-confidential
0005-216e-cb92-e963-4c98 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-11-28 15:52:11 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Energy Storage means a device being used for storage of electrical energy and that can be used to balance the system, e.g. water pumped-storage or batteries; | Energy Storage means a device being used for storage of electrical energy or other energy and that can be used to balance the system, e.g. water pumped-storage or batteries; | Water isn't a device. It can store potential energy, not electrical energy. |  |  | technical |  |  |  | Non-confidential
0005-bdc1-27bc-0f0e-47a8 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 17:15:51 | Paul Doyle | ESB Generation & Wholesale Markets | final | Missing definiton : On load tap changer blocking scheme (see Art 16) | add definition | Add definition of On load tap changer blocking scheme. |  |  | technical |  |  |  | Non-confidential
0005-e4a9-c4ee-e54e-9172 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 16:39:15 | Markus Hemmer | EnBW | final | Frequency Leader means the TSO managing Frequency within a Synchronised Region in order to restore System Frequency back to Nominal Frequency | Please explain or make clear the differnce between "Frequency leader" and " Frequency Governor" wich are normally part of thermal or hydro Power Plants. | E.g. in island condition while system restoration the frequency is managed by them and not by the TSO, the TSO has no physical facility to manage the frequency. | [6 empty] | Non-confidential
0005-e4aa-cbb0-e76f-1086 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-11-28 15:52:12 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | missing text | Restoration Plan has a definition. Add also a definition for System Defence plan. | Integrity of Article 2 |  |  | technical |  |  |  | Non-confidential
0005-bdd5-855e-0ea9-f246 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 17:15:52 | Paul Doyle | ESB Generation & Wholesale Markets | final | Missing definition: Frequency Leader | Frequency Leader means the TSO managing Frequency within a Synchronised Region in order to restore System Frequency back to Nominal Frequency | Add definition of Frequency Leader |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2271 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Demand means the netted value of Active Power seen from a given point of the system, computed as (load – generation), generally expressed in kilowatts (kW) or megawatts (MW), at a given instant or averaged over any designated interval of time; | no text proposal. | The definition of Demand is different from the one in the ENTSO-E Glossary: " Demand is the rate at which electric power is delivered to or by a system or part of a system, generally expressed in kilowatts (kW) or megawatts (MW), at a given instant or averaged over any designated interval of time. Demand should not be confused with load (a load is usually a device). " Demand in the NC ER is defined as an equation (demand = load - generation); this is not the case for the definition in the glossary. |  |  | Legal
0005-e495-5e7a-d54d-2272 | V1.0 for Public consultation version | 1 | 2 | - | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Synchronised Region means a subpart of a Synchronous Area covered by interconnected TSOs with a common System Frequency not synchronised with the rest of the Synchronous Area; | Synchronised Region means a subpart of a Synchronous Area covered by interconnected TSOs with a common System Frequency not synchronised with the rest of the Synchronous Area; | The part that has been deleted is already in the definition of a Synchronous area in the NC OS. No need to repeat this here. |  |  | Legal
0005-e495-5e7a-d54d-1960 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Bottom-up Re-energisation Strategy means a strategy that does not require the assistance from other TSOs to re-energise part of the system of a TSO; | Bottom-up Re-energisation Strategy means a strategy that does not require the assistance from other TSOs to re-energise (part of) the system of a TSO; | Also valid in case of re-energisation of the complete system .
0005-e495-5e7a-d54d-1961 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Resynchronisation means synchronising two Synchronised Regions by connecting the two Synchronised Regions at the Resynchronisation Point; | Resynchronisation means bringing two Synchronised Regions into synchronous operation and connecting them at the Resynchronisation Point; | Synchronisation is more than blind connecting asynchronous areas. Resynchronisation must be covered by a dedicated procedure.
0005-e495-5e7a-d54d-1962 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Resynchronisation Point means the substation used to connect two Synchronised Regions by closing circuit-breakers; | Resynchronisation Point means the substation where a circuit-breaker is being closed to connect two Synchronised Regions at the moment of resynchronisation; | Also other substations are used but not meanth in this definition.
0005-e495-5e7a-d54d-1963 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Top-down Re-energisation Strategy means a strategy that requires the assistance of other TSOs to re-energise part of the system of a TSO. | Top-down Re-energisation Strategy means a strategy that requires the assistance of other TSOs to re-energise (part of) the system of a TSO. | Also valid in case of re-energisation of the complete system .
0005-e495-5e7a-d54d-1964 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Energy Storage means a device being used for storage of electrical energy and that can be used to balance the system, e.g. water pumped-storage or batteries; | Energy Storage means a device being used for storage of electrical energy or other energy and that can be used to balance the system, e.g. water pumped-storage or batteries; | Water isn't a device. It can store potential energy, not electrical energy.
0005-e495-5e7a-d54d-1965 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | missing text | Restoration Plan has a definition. Add also a definition for System Defence plan. | Integrity of Article 2
0005-e495-5e7a-d54d-1966 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Missing definiton : NEMO | add definition | Nominated Electricity Market Operator
0005-e495-5e7a-d54d-1967 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Missing definiton : On load tap changer blocking scheme (see Art 16) | add definition | Add definition of On load tap changer blocking scheme.
0005-e495-5e7a-d54d-1968 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Missing definition: Frequency Leader | Frequency Leader means the TSO managing Frequency within a Synchronised Region in order to restore System Frequency back to Nominal Frequency | Add definition of Frequency Leader
0005-e495-5e7a-d54d-1969 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year |  | Backup is not defined and not mentioned in Art. 38
0005-e495-5e7a-d54d-1970 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final |  | The definitions should cover: Normal state Alert Emergency Restoration Blackout | These definition may be in other NCs, but they should be replicated here for clarity, as these state definitions are at the core of the procedures.
0005-e495-5e7a-d54d-1971 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final |  | Add definitions. | General Comment to articles 12,13 y 14: It is not clear the borderline between Normal and Alert state frequency control procedures (LFC&R NC), and Emergency frequency control procedures (E&R NC). When there is an Emergency State, Normal and Alert state frequency control procedures should apply?, or should they be suspended?. If there is an Emergency state, and Normal and Alert state frequency control procedures are keeped, they could interfere with the activated TSO Emergency procedure.
0005-e495-5e7a-d54d-2132 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 21:33 | AG | RWE | final | Bottom-up Re-energisation Strategy means a strategy that does not require the assistance from other TSOs to re-energise part of the system of a TSO; | Bottom-up Re-energisation Strategy means a strategy that does not require the assistance from other TSOs to re-energise (part of) the system of a TSO; | Also valid in case of re-energisation of the complete system . |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2133 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Demand means the netted value of Active Power seen from a given point of the system, computed as (load generation), generally expressed in kilowatts (kW) or megawatts (MW), ata given instant or averaged over any designated interval of time. | See the justification. | Given there is no Network Code definition of Demand (the only one that exists currently in the metadata repository refers to a definition in the Operational Handbook which is not opposable to third parties) is this to be the definition used throughout the Network Codes, and if so is it compatibe with those NCs that preceded it?
0005-e495-5e7a-d54d-2134 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 21:33 | AG | RWE | final | Resynchronisation means synchronising two Synchronised Regions by connecting the two Synchronised Regions at the Resynchronisation Point; | Resynchronisation means bringing two Synchronised Regions into synchronous operation and connecting them at the Resynchronisation Point; | Synchronisation is more than blind connecting asynchronous areas. Resynchronisation must be covered by a dedicated procedure. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2135 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 21:33 | AG | RWE | final | Resynchronisation Point means the substation used to connect two Synchronised Regions by closing circuit-breakers; | Resynchronisation Point means the substation where a circuit-breaker is being closed to connect two Synchronised Regions at the moment of resynchronisation; | Also other substations are used but not meanth in this definition. |  |  | Technical | Editorial
0005-e495-5e7a-d54d-2136 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 21:33 | AG | RWE | final | Top-down Re-energisation Strategy means a strategy that requires the assistance of other TSOs to re-energise part of the system of a TSO. | Top-down Re-energisation Strategy means a strategy that requires the assistance of other TSOs to re-energise (part of) the system of a TSO. | Also valid in case of re-energisation of the complete system . |  |  | Technical | Editorial
0005-e495-5e7a-d54d-2137 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 21:33 | Koch | AXPO | final | Energy Storage means a device being used for storage of electrical energy and that can be used to balance the system, e.g. water pumped-storage or batteries; | Energy Storage means a device being used for storage of electrical energy or other energy and that can be used to balance the system, e.g. water pumped-storage or batteries; | Water isn't a device. It can store potential energy, not electrical energy. Also the definition put in the metadata repository is different: "A device being used for storage of electrical energy that can be used to balance the system". Which one is correct? |  |  | Technical | Editorial
0005-e495-5e7a-d54d-2138 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 21:33 | Koch | AXPO | final | Restoration Plan means the summary of all technical and organisational measures to be undertaken to restore the system back to Normal State | Restoration Plan means the document containing all of the technical and organisational measures to be undertaken to restore the system back to Normal State | Restoration plan cannot be a 'summary'. If that's the case, what is the document where the details are contained? |  |  | Technical | Editorial
0005-e495-5e7a-d54d-2139 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 21:33 | EDK | GFS | final | Missing definiton : On load tap changer blocking scheme (see Art 16) | Add definition | Add definition of On load tap changer blocking scheme. |  |  | Technical | Editorial
0005-e495-5e7a-d54d-2140 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 21:33 | Eberhard | ENBW | final | Missing definition: Frequency Leader | Frequency Leader means the TSO managing Frequency within a Synchronised Region in order to restore System Frequency back to Nominal Frequency | Add definition of Frequency Leader | E.g. in island condition while system restoration the frequency is managed by them and not by the TSO, the TSO has no physical facility to manage the frequency. |  | Technical | Editorial
0005-e495-5e7a-d54d-2141 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 21:33 | EDK | GFS | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year |  | Backup is not defined and not mentioned in Article 38 |  |  | Technical | Editorial
0005-e495-5e7a-d54d-1715 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Demand means the netted value of Active Power seen from a given point of the system, computed as (load – generation), generally expressed in kilowatts (kW) or megawatts (MW), at a given instant or averaged over any designated interval of time; | Xyz | Given that there is no Network Code definition of Demand (the only one that exists currently in the metadata repository refers to a definition in the Operational Handbook which has no legal basis and is therefore unacceptable) is this to be the definition used throughout the Network Codes, and if so is it compatible with those that NCs preceded it?
0005-e495-5e7a-d54d-1716 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Energy Storage means a device being used for storage of electrical energy and that can be used to balance the system, e.g. water pumped-storage or batteries; | xyz | The definition in the metadata repository is different – “ A device being used for storage of electrical energy and that can be used to balance the system”. Whish is correct?
0005-e495-5e7a-d54d-1719 | V1.0 for Public consultation version | 1 | 2 |  |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Restoration Plan means the summary of all technical and organisational measures to be undertaken to restore the system back to Normal State; | Restoration Plan means the DOCUMENT CONTAINING summary of all OF THE technical and organisational measures to be undertaken to restore the system back to Normal State; | If the Restoration Plan is a ‘summary’ document then where are the details contained? What is the second (detailed) document called and where is its legal vires and governance set out?
0005-96b1-d37d-c867-180e | V1.0 for Public consultation version | 1 | 3 | 1 | - | 2014-12-08 19:51:13 | Roland Tual | SEDC | final | When defining terms and conditions or actions necessary to ensure Operational Security pursuant to this Network Code, a TSO shall act in accordance with the principles of transparency, proportionality and non-discrimination and shall take into account at least the following: a) characteristics of the system; b) operational conditions; and c) efficiency. | [8 empty] | confidential
0005-e4d1-ac8c-0bed-977e | V1.0 for Public consultation version | 1 | 3 | 3 | - | 2014-12-08 17:15:56 | Paul Doyle | ESB Generation & Wholesale Markets | final | c) efficiency | Over all cost efficiency for all participannts. | Define efficiency (cost for TSO, Energy efficiency, fast recovery etc?). It must consider all participants |  |  | legal |  |  |  | Non-confidential
0005-bd85-9cec-0de1-164a | V1.0 for Public consultation version | 1 | 3 | 3 | - | 2014-12-08 17:15:57 | Paul Doyle | ESB Generation & Wholesale Markets | final | When defining terms and conditions or actions necessary to ensure Operational Security | Delete | This article belongs to the NC OS. Add it there! |  |  | legal |  |  |  | Non-confidential
0005-6f8e-cb92-e89b-e9a4 | V1.0 for Public consultation version | 1 | 3 | 3 | - | 2014-11-28 15:52:16 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | c) efficiency | Over all cost efficiency for all participannts. | Define efficiency (cost for TSO, Energy efficiency, fast recovery etc?). It must consider all participants |  |  | legal |  |  |  | Non-confidential
0005-969e-181e-e8ff-bcf1 | V1.0 for Public consultation version | 1 | 3 | 3 | - | 2014-11-28 15:52:17 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | When defining terms and conditions or actions necessary to ensure Operational Security | Delete | This article belongs to the NC OS. Add it there! |  |  | legal |  |  |  | Non-confidential
0005-6f65-c555-2397-3458 | V1.0 for Public consultation version | 1 | 3 | 3 | - | 2014-12-08 17:01:12 | Jasmina PIERRE | EdF | final | 3. When defining terms and conditions or actions necessary to ensure Operational Security pursuant to this Network Code, a TSO shall act in accordance with the principles of transparency, proportionality and non-discrimination and shall take into account at least the following: a) characteristics of the system; b) operational conditions; and c) efficiency. | 3. When defining terms and conditions or actions necessary to ensure Operational Security pursuant to this Network Code, a TSO shall act in accordance with the principles of transparency, proportionality and non-discrimination and shall take into account at least the following: a) characteristics of the system; b) operational conditions; and c) overall cost efficiency. | TSOs should be incentivize to pursue cost overall efficiency. When some markets activities are to be suspended, the resulting requested actions for grids users are no longer driven by market-based mechanisms but still need to pursue a “cost-efficient” dispatch, i.e. actions that will minimize global impacts for the system including grid users. |  |  | technical |  |  |  | Non-confidential
0005-2159-5e4f-29f0-e18e | V1.0 for Public consultation version | 1 | 3 | 3 | - | 2014-12-08 16:38:47 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | c) efficiency | Over all cost efficiency for all participannts. | Define efficiency (cost for TSO, Energy efficiency, fast recovery etc?). It must consider all participants | [6 empty] | Non-confidential
0005-9689-279f-2a54-1d09 | V1.0 for Public consultation version | 1 | 3 | 3 | - | 2014-12-08 16:38:49 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | When defining terms and conditions or actions necessary to ensure Operational Security | Copy this article into NC OS. | This article belongs to the NC OS. Add it also there! | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-1972 | V1.0 for Public consultation version | 1 | 3 | 3 | c | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | c) efficiency | Over all cost efficiency for all participannts. | Define efficiency (cost for TSO, Energy efficiency, fast recovery etc?). It must consider all participants
0005-e495-5e7a-d54d-1973 | V1.0 for Public consultation version | 1 | 3 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | When defining terms and conditions or actions necessary to ensure Operational Security | Copy this article into NC OS. | This article belongs to the NC OS. Add it also there!
0005-e495-5e7a-d54d-2142 | V1.0 for Public consultation version | 1 | 3 |  |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | See the wording of the whole Article 3- general comment | To be moved to the recitals. | This Article does not contain any specific obligation but will be used for the interpretation purposes. Hence, it should be moved to the recitals. More importantly- the front/ end of this Code should be aligned with the other Codes/ Guidelines, in particular the latest vesrion of CACM. |  |  | Legal | Editorial
0005-2181-6000-a03d-3be3 | V1.0 for Public consultation version | 1 | 4 | 1 | - | 2014-12-04 13:54:29 | Dekinderen Eric | Genrator company | final | The costs related to the obligations referred to in this Network Code which have to be borne by regulated Network Operators shall be assessed by National Regulatory Authorities. | NA | Why only "regulated" network operators? Which ones are excluded??? |  |  | technical |  |  |  | Non-confidential
0005-bd85-75dc-0d19-a325 | V1.0 for Public consultation version | 1 | 4 | 1 | - | 2014-12-08 17:15:59 | Paul Doyle | ESB Generation & Wholesale Markets | final | The costs related to the obligations referred to in this Network Code which have to be borne by regulated Network Operators shall be assessed by National Regulatory Authorities. | The costs related to the obligations referred to in this Network Code shall be assessed by National Regulatory Authorities. | During restoration phase, customers have to bear the costs of consumed energy. It must be recognised that there are other costs than just Network Operator costs. Also these costs must be addressed. |  |  | legal |  |  |  | Non-confidential
0005-6f79-acd7-a114-537a | V1.0 for Public consultation version | 1 | 4 | 1 | - | 2014-12-07 12:51:40 | Herve MELJAC | EUR | final | The costs related to the obligations referred to in this Network Code which have to be borne by regulated Network Operators shall be assessed by National Regulatory Authorities. | The costs related to the obligations referred to in this Network Code which have to be borne by regulated Network Operators and Significant Grid Users shall be assessed by National Regulatory Authorities. | Costs incurred to SGUs by this Code should be borne by requesting TSOs, which in turn would recover this cost through their regulated tarif. This would avoid any competition distortion caused by Emergency and Restoration arrangements, and would incentivise TSOs to optimise E&R arrangements. The potential for competition distortion can be explained as such... Let's assume two SGUs, SGU1 and SGU2, who are competitors on the market, both connected to the same TSO grid. The TSO, which decides of the restoration arrangements and defence plan, may decide that SGU1 has to participate to these arrangements and not SGU2. Hence SGU1 suffers extra costs compared to SGU2, because of the TSO decision. If SGU1 and SGU2 are left to recover their costs from the market, there is competition distortion. If SGU1 incurred costs are borne by TSO and then recovered through the tarif, the cost of E&R arrangements are evenly split between all grid users, who all benefit from them. Additionally, NRA scrutiny on TSO spendings will incentivise E&R arrangements optimisation. It has to be noted that the question of cost recovery for SGUs is not limited to this article, but has wider implication throughout this Code. |  |  | legal |  |  |  | Non-confidential
0005-e4be-cbb0-e9c7-6d84 | V1.0 for Public consultation version | 1 | 4 | 1 | - | 2014-11-28 15:52:17 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The costs related to the obligations referred to in this Network Code which have to be borne by regulated Network Operators shall be assessed by National Regulatory Authorities. | The costs related to the obligations referred to in this Network Code and the costs referred to the implementation of the System Defence Plan measures and the implementation of Restoration Plan measures shall be assessed by National Regulatory Authorities. | During restoration phase, customers have to bear the costs of consumed energy. It must be recognised that there are other costs than just Network Operator costs. Implementation measures to be carried out by SGUs shall be recovered. All the actions required have to have the corresponding remuneration. Otherwise they cannot be considered. |  |  | legal |  |  |  | Non-confidential
0005-6f65-11c3-2397-4eef | V1.0 for Public consultation version | 1 | 4 | 1 | - | 2014-12-08 17:01:12 | Jasmina PIERRE | EdF | final | The costs related to the obligations referred to in this Network Code which have to be borne by regulated Network Operators shall be assessed by National Regulatory Authorities. | The costs related to the obligations referred to in this Network Code shall be assessed by National Regulatory Authorities. | It is essential that TSOs shall bear all the costs incurred by grid users for (i) the actions/measures carried out upon TSO request; (ii) additional and redundant (voice) communication channels; (iii) measures to ensure the extended (>24h) availability of critical tools and facilities and (iv) for “compliance testing” of equipment and procedures required to ensure reliability of prepared System Defense and Restoration Plans. First, ensuring “cost recovery” for Significant Grid Users identified in the System Defense and restoration Plans contributes to incentivizing TSOs to pursue the objective of overall cost efficiency, in accordance with the principle defined in “general conditions” chapter (article 3.3.c). When the suspension of market activities is required by TSOs, TSOs then act as a central dispatch to maintain and restore the operational parameters within the security limits. The resulting actions requested from grids users are no longer driven by market-based mechanisms but however still need to pursue a “cost-efficient” dispatch, i.e. actions that will minimize global impacts for the system including grid users. Furthermore, ensuring “cost recovery” for Significant Grid Users identified in the System Defense and restoration Plans is also required to prevent from any discrimination between grid users competing on the markets. Some grid users can be identified as part of the System Defense and Restoration Plans, while others will not. All of them should still be able to compete on the same playing field, which implies recognizing and bearing all the costs incurred by grid users when they contribute to System Defense and Restoration Plans implementation. |  |  | technical |  |  |  | Non-confidential
0005-969d-855f-27fc-4a83 | V1.0 for Public consultation version | 1 | 4 | 1 | - | 2014-12-08 16:38:51 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | The costs related to the obligations referred to in this Network Code which have to be borne by regulated Network Operators shall be assessed by National Regulatory Authorities. | The costs related to the obligations referred to in this Network Code and the costs referred to the implementation of the System Defence Plan measures and the implementation of Restoration Plan measures shall be assessed by National Regulatory Authorities. | During restoration phase, customers have to bear the costs of consumed energy. It must be recognised that there are other costs than just Network Operator costs. Implementation measures to be carried out by SGUs shall be recovered. All the actions required have to have the corresponding remuneration. Otherwise they cannot be considered. | [6 empty] | Non-confidential
0005-e4e5-27bb-cabf-cdb8 | V1.0 for Public consultation version | 1 | 4 | 1 | b | 2014-12-08 19:51:13 | Roland Tual | SEDC | final | 1. regulated Network Operators shall be assessed by National Regulatory Authorities. 2.Costs assessed as efficient, reasonable and proportionate shall be recovered as determined by National Regulatory Authorities. | [8 empty] | confidential
0005-e495-5e7a-d54d-1974 | V1.0 for Public consultation version | 1 | 4 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The costs related to the obligations referred to in this Network Code which have to be borne by regulated Network Operators shall be assessed by National Regulatory Authorities. | The costs related to the obligations referred to in this Network Code and the costs referred to the implementation of the System Defence Plan measures and the implementation of Restoration Plan measures shall be assessed by National Regulatory Authorities. | During restoration phase, customers have to bear the costs of consumed energy. It must be recognised that there are other costs than just Network Operator costs. Implementation measures to be carried out by SGUs shall be recovered. All the actions required have to have the corresponding remuneration. Otherwise they cannot be considered.
0005-e495-5e7a-d54d-2239 | V1.0 for Public consultation version | 1 | 4 | 1 |  | 2014-12-08 12:24 | Wolfram Heckmann | Fraunhofer IWES | final | “costs…which have to be borne by regulated Network Operators” |  | The NC also deals with obligations of significant grid users, aggregators, individual generators, how will their costs be covered arising from the obligations? Remuneration by the TSO?
0005-48a5-9e80-a105-b4ad | V1.0 for Public consultation version | 1 | 4 | 3 | - | 2014-12-04 13:56:08 | Dekinderen Eric | Genrator company | final | If requested by National Regulatory Authorities, regulated Network Operators shall ... | If requested by National Regulatory Authorities, Network Operators shall .... | Why only "regulated" network operators? Which ones are excluded??? |  |  | technical |  |  |  | Non-confidential
0005-487d-9e62-a3c1-1e88 | V1.0 for Public consultation version | 1 | 4 | 3 | - | 2014-12-04 13:56:54 | Dekinderen Eric | Genrator company | final | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | "endeavours" is too free |  |  | technical |  |  |  | Non-confidential
0005-bd99-01cc-3b95-e029 | V1.0 for Public consultation version | 1 | 4 | 3 | - | 2014-12-05 10:17:49 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Regulated Network Operators shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | Regulated Network Operators shall, after an impact analyses within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | The request can only be reasonably fulfilled, if the full impact of the changes is known and the necessary system changes are defined - this is not the case at the very beginning of the process. | 1 | 4 | technical |  |  |  | Non-confidential
0005-96b1-ac6f-28c4-7deb | V1.0 for Public consultation version | 1 | 4 | 3 | - | 2014-12-08 16:38:53 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | If requested by National Regulatory Authorities, involved parties shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | In line with change in 4.1. Also parties, not being DSO/TSO shall deliver informations to facilitate the assessment of the costs incurred. | [6 empty] | Non-confidential
0005-e495-ac50-0d7d-3246 | V1.0 for Public consultation version | 1 | 4 | 3 | - | 2014-12-08 17:16:47 | Paul Doyle | ESB Generation & Wholesale Markets | final | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | If requested by National Regulatory Authorities, involved parties shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | In line with change in 4.1. Also parties, not being DSO/TSO shall deliver informations to facilitate the assessment of the costs incurred. |  |  | legal |  |  |  | Non-confidential
0005-216d-5e30-0ea9-68e9 | V1.0 for Public consultation version | 1 | 4 | 3 | - | 2014-12-08 17:16:49 | Paul Doyle | ESB Generation & Wholesale Markets | final | If requested by National Regulatory Authorities, regulated Network Operators shall | If requested by National Regulatory Authorities, Network Operators shall | Why only "regulated" network operators? Which ones are excluded and why should they be excluded? |  |  | legal |  |  |  | Non-confidential
0005-e4e5-ac8c-0f71-e5b3 | V1.0 for Public consultation version | 1 | 4 | 3 | - | 2014-12-08 17:16:51 | Paul Doyle | ESB Generation & Wholesale Markets | final | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | Use best endeavours is unacceptable. |  |  | legal |  |  |  | Non-confidential
0005-969e-5680-e9c7-6569 | V1.0 for Public consultation version | 1 | 4 | 3 | - | 2014-11-28 15:52:34 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | If requested by National Regulatory Authorities, involved parties shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | In line with change in 4.1. Also parties, not being DSO/TSO shall deliver informations to facilitate the assessment of the costs incurred. |  |  | legal |  |  |  | Non-confidential
0005-216d-11c3-24c3-cf89 | V1.0 for Public consultation version | 1 | 4 | 3 | - | 2014-12-08 17:01:13 | Jasmina PIERRE | EdF | final | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | If requested by National Regulatory Authorities, regulated Network Operators and other involved parties shall, within three months of such a request, provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | Parties, not being DSO/TSO shall deliver informations to facilitate the assessment of the costs incurred. "Cost recovery"principle should be ensured, so that "best endeavours" to provide such information is not enough. |  |  | technical |  |  |  | Non-confidential
0005-e4be-cbce-e837-8a66 | V1.0 for Public consultation version | 1 | 4 | 3 | - | 2014-11-28 15:52:35 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | If requested by National Regulatory Authorities, regulated Network Operators shall | If requested by National Regulatory Authorities, Network Operators shall | Why only "regulated" network operators? Which ones are excluded and why should they be excluded? |  |  | legal |  |  |  | Non-confidential
0005-4892-8d12-e9c7-1bf6 | V1.0 for Public consultation version | 1 | 4 | 3 | - | 2014-11-28 15:52:36 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | Use best endeavours is unacceptable. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-1975 | V1.0 for Public consultation version | 1 | 4 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | If requested by National Regulatory Authorities, involved parties shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | In line with change in 4.1. Also parties, not being DSO/TSO shall deliver informations to facilitate the assessment of the costs incurred.
0005-e495-5e7a-d54d-1976 | V1.0 for Public consultation version | 1 | 4 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | If requested by National Regulatory Authorities, regulated Network Operators shall | If requested by National Regulatory Authorities, Network Operators shall | Why only "regulated" network operators? Which ones are excluded and why should they be excluded?
0005-e495-5e7a-d54d-1977 | V1.0 for Public consultation version | 1 | 4 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | The code should include clear requirements on the network operators. It is not adequate to ask them to use "best endeavours" to provide the information.
0005-e495-5e7a-d54d-2143 | V1.0 for Public consultation version | 1 | 4 | 3 |  | 2014-12-08 21:33 | EDK | GFS | final | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, use best endeavours to provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | If requested by National Regulatory Authorities, regulated Network Operators shall, within three months of such a request, provide such additional information as reasonably requested by National Regulatory Authorities to facilitate the assessment of the costs incurred. | The code should include clear requirements on the network operators. It is not adequate to ask them to use "best endeavours" to provide the information. The general provision on cost recovery (Article 72 of CACM) should be used here. |  |  | Legal | Fundamental
0005-6f65-af49-6ec4-2eca | V1.0 for Public consultation version | 1 | 5 | 1 | - | 2014-12-04 09:18:23 | Steve Wilkin | ELEXON Limited | final | When a TSO has to consult other parties under this Network Code, the following process shall apply: a) liaise with the concerned parties; | When a TSO has to consult other parties under this Network Code, the following process shall apply: a) consult publicly with the parties; | As a principle, we suggest that consultations should be public so that any party can choose to respond if it believes it is impacted. |  |  | technical |  |  |  | Non-confidential
0005-e495-c40d-4d77-5bd2 | V1.0 for Public consultation version | 1 | 5 | 1 | - | 2014-12-08 20:11:09 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | The decision-making process described in this Network Code appears to be unbalanced in view of the consequences of the requirements involved, notably concerning the preventive system defence plans. These consultation processes are inappropriate for taking decisions towards residential consumers. Although the TSOs - as they are responsible for the security of the electricity system - shall be given exceptional extended authority in emergency, blackout and restoration situations, there should be a supervision by national regulatory authorities to ensure that the principles of proportionality and social welfare are respected, in particular when such plans have consequences on small residential consumers. |  |  | legal |  |  |  | Non-confidential
0005-4855-602a-120b-c277 | V1.0 for Public consultation version | 1 | 5 | 1 | - | 2014-12-03 11:09:21 | AXPO Group |  | final | Original text of issue 13.10.2014 | see Comment | Consultation means a unilateral decision by a TSO. The wording "consultation" is misleading. This procedure is simply called unilateral decision by the TSO under consideration of other grid participants. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-1720 | V1.0 for Public consultation version | 1 | 5 | 1 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | explain the objective of the consultation / decision that it has to take; | explain the MOTIVATION AND objective of the consultation / decision that it has to take; | The word ‘motivation’ appears in Art 5(2) (b) and so should appear here in (1) (b) as well.
0005-e495-5e7a-d54d-1721 | V1.0 for Public consultation version | 1 | 5 | 1 | E | 2014-12-08 13:31 | Garth Graham | SSE |  | before adopting a decision, indicate to the parties consulted how their observations were taken into consideration, including reasons where observations have not been taken into account. | before SUBMITTING THEIR PROPOSED adopting a decision TO THE NRA(S) FOR APPROVAL, indicate to the parties consulted how their observations were taken into consideration, including reasons where observations have not been taken into account. | All decisions taken by the TSOs that have been consulted upon must be subject to explicit approval from the relevant NRA(s) or ACER.
0005-e495-5e7a-d54d-2248 | V1.0 for Public consultation version | 1 | 5 | 1 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Consultation Process |  | This process requires only that the TSO considers other parties needs and explain their reasons for potentially ignoring these needs. It provides no legal protection whatever for ensuring that these needs are in fact respected, be they social, privacy concerns, cost to the party, social welfare etc. This is inappropriate if small consumers and prosumers are covered by this code.
0005-96b1-5f7c-e616-37ce | V1.0 for Public consultation version | 1 | 5 | 2 | - | 2014-12-08 16:39:15 | Markus Hemmer | EnBW | final | When a TSO has to coordinate with other parties under this Network Code, the following process shall apply: [...] e) make a proposal on actions to be launched by each parties, taking into account the situations and constraints of the concerned parties; f) when the concerned parties agree with the TSO’s proposal, each party, including the TSO, shall launch the actions in line with the proposal agreed; [...] | There should be an additional point between e) and f) that says: "Discuss the proposal with all involved parties" | The discussion should be on "eye level" with the possibility of a compromise for the process. Not only as stated here, of decline or agreement. | [6 empty] | Non-confidential
0005-bd85-373e-0f0d-141f | V1.0 for Public consultation version | 1 | 5 | 2 | - | 2014-12-08 17:16:52 | Paul Doyle | ESB Generation & Wholesale Markets | final | When a TSO has to coordinate with other parties under this Network Code, the following process shall apply: [...] e) make a proposal on actions to be launched by each parties, taking into account the situations and constraints of the concerned parties; f) when the concerned parties agree with the TSO’s proposal, each party, including the TSO, shall launch the actions in line with the proposal agreed; [...] | When a TSO has to coordinate with other parties under this Network Code, the following process shall apply: [...] e) make a proposal on actions to be launched by each parties, taking into account the situations and constraints of the concerned parties; f) Agree the proposal with all involved parties. g) when the concerned parties agree with the TSO’s proposal, each party, including the TSO, shall launch the actions in line with the proposal agreed; [...] | There should be an additional point between e) and f) that says: "Agree the proposal with all involved parties" |  |  | legal |  |  |  | Non-confidential
0005-4855-38d3-258b-6954 | V1.0 for Public consultation version | 1 | 5 | 2 | - | 2014-12-08 17:01:13 | Jasmina PIERRE | EdF | final | When a TSO has to coordinate with other parties under this Network Code, the following process shall apply: [...] e) make a proposal on actions to be launched by each parties, taking into account the situations and constraints of the concerned parties; f) when the concerned parties agree with the TSO’s proposal, each party, including the TSO, shall launch the actions in line with the proposal agreed; [...] | When a TSO has to coordinate with other parties under this Network Code, the following process shall apply: [...] e) make a proposal on actions to be launched by each parties, taking into account the situations and constraints of the concerned parties; f) Discuss the proposal with all involved parties ; g) when the concerned parties agree with the TSO’s proposal, each party, including the TSO, shall launch the actions in line with the proposal agreed; [...] | Both network operators and significant grid users have a common interest in a safe and secure operation of the system and both contribute to it. "Coordination" process should ensure the proposal that will be implemented relies on effective preliminary discussions between all involved parties, |  |  | technical |  |  |  | Non-confidential
0005-4856-17e2-e70b-942a | V1.0 for Public consultation version | 1 | 5 | 2 | - | 2014-11-28 15:52:37 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | When a TSO has to coordinate with other parties under this Network Code, the following process shall apply: [...] e) make a proposal on actions to be launched by each parties, taking into account the situations and constraints of the concerned parties; f) when the concerned parties agree with the TSO’s proposal, each party, including the TSO, shall launch the actions in line with the proposal agreed; [...] | When a TSO has to coordinate with other parties under this Network Code, the following process shall apply: [...] e) make a proposal on actions to be launched by each parties, taking into account the situations and constraints of the concerned parties; f) Agree the proposal with all involved parties. g) when the concerned parties agree with the TSO’s proposal, each party, including the TSO, shall launch the actions in line with the proposal agreed; [...] | There should be an additional point between e) and f) that says: "Agree the proposal with all involved parties" |  |  | legal |  |  |  | Non-confidential
0005-e4bd-391a-12d3-b042 | V1.0 for Public consultation version | 1 | 5 | 2 | - | 2014-12-03 11:09:21 | AXPO Group |  | final | Original text of issue 13.10.2014 | see Comment | Coordination means that the involved parties have to agree to a proposal. This procedure is simply called multilateral decision or mutual agreement by grid members. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-1978 | V1.0 for Public consultation version | 1 | 5 | 2 | f | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | When a TSO has to coordinate with other parties under this Network Code, the following process shall apply: [...] e) make a proposal on actions to be launched by each parties, taking into account the situations and constraints of the concerned parties; f) when the concerned parties agree with the TSO’s proposal, each party, including the TSO, shall launch the actions in line with the proposal agreed; [...] | When a TSO has to coordinate with other parties under this Network Code, the following process shall apply: [...] e) make a proposal on actions to be launched by each parties, taking into account the situations and constraints of the concerned parties; f) Agree the proposal with all involved parties. g) when the concerned parties agree with the TSO’s proposal, each party, including the TSO, shall launch the actions in line with the proposal agreed; [...] | There should be an additional point between e) and f) that says: "Agree the proposal with all involved parties"
0005-e495-5e7a-d54d-1722 | V1.0 for Public consultation version | 1 | 5 | 2 | F | 2014-12-08 13:31 | Garth Graham | SSE |  | when the concerned parties agree with the TSO’s proposal, each party, including the TSO, shall launch the actions in line with the proposal agreed; | when the concerned parties agree with the TSO’s proposal, each party, including the TSO, shall PRIOR TO launchING the actions in line with the proposal agreed SEEK APPROVAL FROM THE NRA(S); | It is unacceptable for parties to agree amongst themselves to embark upon a costly action without NRA(s) approval….. unless those parties do NOT intend to seek the recovery of those costs under Art 4.
0005-e495-5e7a-d54d-2145 | V1.0 for Public consultation version | 1 | 5 | 3 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO shall support any TSO in Emergency, Blackout or Restoration States, upon request, provided it does not endanger its own system. | Each TSO shall support any TSO in Emergency, Blackout or Restoration States, upon request, provided it does not endenger its own system and the costs incurred by the supporting TSO of doing so shall be born by the requesting TSO. | There needs to be a clear reference to cost recovery to avoid the costs of providing support to another TSO in an Emergency, Black Start or Restoration State falling upon consumers in another TSO's area.
0005-e495-5e7a-d54d-1724 | V1.0 for Public consultation version | 1 | 5 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall support any TSO in Emergency, Blackout or Restoration States, upon request, provided it does not endanger its own system. | Each TSO shall support any TSO in Emergency, Blackout or Restoration States, upon request, provided it does not endanger its own system AND THE COSTS INCURRED BY THE SUPPORTING TSO OF DOING SO SHALL BE BORN BY THE REQUESTING TSO. | There needs to be a clear reference to cost recovery to avoid the cost of providing support to another TSO in an Emergency, Black Start or Restoration State falling upon consumers in another TSO’s area.
0005-e495-5e7a-d54d-2144 | V1.0 for Public consultation version | 1 | 5 |  |  | 2014-12-08 21:33 | Eberhard | ENBW | final | See the wording of Article 5- general comment | See the justification. | It is not clear why there is a distinction between the consultation and coordination. This Article should be constructed in the same way as in the other Codes (CACM) in particular. In addition, the term "concerned parties" should be avoided. All the stakeholders (not only "concerned") shall have a right to be consulted. Finally, the NRA approvals are missing. As a general rule (and like in the other Network Codes/ Guidelines), all decisions taken by the TSOs shall be consulted with the stakeholders and approved by the relevant NRAs. | The discussion should be on "eye level" with the possibility of a compromise for the process. Not only as stated here, of decline or agreement. |  | Legal | Fundamental
0005-bd85-100f-c9f7-cfd0 | V1.0 for Public consultation version | 1 | 6 | 1 | - | 2014-12-08 19:51:13 | Roland Tual | SEDC | final | Each TSO ,DSO and Significant Grid User shall preserve the confidentiality of the information and data submitted to them in connection with this Network Code and shall use them exclusively for the purpose they have been submitted in compliance with this Network Code. | [8 empty] | confidential
0005-e495-5e7a-d54d-2273 | V1.0 for Public consultation version | 1 | 6 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO, DSO and Significant Grid User shall preserve the confidentiality of the information and data submitted to them in connection with this Network Code and shall use them exclusively for the purpose they have been submitted in compliance with this Network Code. | Each TSO and Significant Grid User shall preserve the confidentiality of the information and data submitted to them in connection with this Network Code and shall use them exclusively for the purpose they have been submitted in compliance with this Network Code. | Confidentiality obligations for DSOs are redundant to Directive 2003/54/EC (Article 16), which still binds DSOs across Europe. |  |  | Legal
0005-e495-5e7a-d54d-2249 | V1.0 for Public consultation version | 1 | 6 | 1 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each TSO, DSO and Significant Grid User shall preserve the confidentiality of the information and data submitted to them in connection with this Network Code and shall use them exclusively for the purpose they have been submitted in compliance with this Network Code. |  | It is unreasonable to expect a small consumer or prosumer to keep the commands of a TSO a secret. They should not be included here
0005-e495-ac6e-0ea9-2a45 | V1.0 for Public consultation version | 1 | 7 | 1 | - | 2014-12-08 17:16:53 | Paul Doyle | ESB Generation & Wholesale Markets | final | No later than 12 months after entering into force of this Network Code all TSOs shall endeavour to implement a Synchronous Area agreement within a Synchronous Area to ensure that TSOs with no legal obligation to respect this Network Code, belonging to the Synchronous Area, also cooperate to fulfil the requirements. | No later than 12 months after entering into force of this Network Code all TSOs shall implement a Synchronous Area agreement within a Synchronous Area to ensure that TSOs with no legal obligation to respect this Network Code, belonging to the Synchronous Area, also cooperate to fulfil the requirements. | Endeavour only is not sufficient and not acceptable. |  |  | legal |  |  |  | Non-confidential
0005-96c6-b45e-e76f-9f00 | V1.0 for Public consultation version | 1 | 7 | 1 | - | 2014-11-28 15:52:38 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | No later than 12 months after entering into force of this Network Code all TSOs shall endeavour to implement a Synchronous Area agreement within a Synchronous Area to ensure that TSOs with no legal obligation to respect this Network Code, belonging to the Synchronous Area, also cooperate to fulfil the requirements. | No later than 12 months after entering into force of this Network Code all TSOs shall implement a Synchronous Area agreement within a Synchronous Area to ensure that TSOs with no legal obligation to respect this Network Code, belonging to the Synchronous Area, also cooperate to fulfil the requirements. | Endeavour only is not sufficient and not acceptable. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-1979 | V1.0 for Public consultation version | 1 | 7 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | No later than 12 months after entering into force of this Network Code all TSOs shall endeavour to implement a Synchronous Area agreement within a Synchronous Area to ensure that TSOs with no legal obligation to respect this Network Code, belonging to the Synchronous Area, also cooperate to fulfil the requirements. | No later than 12 months after entering into force of this Network Code all TSOs of all EU memberstates shall implement a Synchronous Area agreement within a Synchronous Area to ensure that TSOs with no legal obligation to respect this Network Code, belonging to the Synchronous Area, also cooperate to fulfil the requirements. | The code should include clear requirements on the network operators. "Endeavour" only is not sufficient.
0005-2181-c4ee-e4ea-d833 | V1.0 for Public consultation version | 1 | 7 | 3 | - | 2014-12-08 16:39:15 | Markus Hemmer | EnBW | final | If an agreement according to Article 7(1) cannot be implemented within 12 months after entering into force of this Network Code, the TSO’s operating in a Synchronous Area whose frequency is influenced in a predominant way by Power systems that are not bound by the EU legislation shall nevertheless endeavour to implement a Synchronous Area agreement within their Synchronous Area to ensure that TSOs with no legal obligation to respect this Network Code, belonging to the Synchronous Area, also cooperate to fulfil the requirements. | Delete | TSOs wiith no legal obligation to fullfill this NC cannot be forced to cooperate. What shall the respective TSO do, if this endeavor fails? |  |  | technical |  |  |  | Non-confidential
0005-e4bd-387c-3acd-a911 | V1.0 for Public consultation version | 2 | 8 | 1 | - | 2014-12-05 10:19:08 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | 1. Each TSO shall design a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | 1. Each TSO shall design a System Defence Plan in agreement with DSOs especially according maintenance, protection scheme and network control, for the preservation of the controllability of the grid infrastructure, and consultation with Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | The know how of the DSO should be not only be checked in a conslutation, the system defence plan shopuld beelaborated between TSO and DSO. | 1 | 3 | legal |  |  |  | Non-confidential
0005-48a5-032d-6e60-539f | V1.0 for Public consultation version | 2 | 8 | 1 | - | 2014-12-04 09:19:10 | Steve Wilkin | ELEXON Limited | final | Each TSO shall design a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Each TSO shall design a System Defence Plan in consultation with DSOs, Significant Grid Users, neighbouring TSOs and by public consultation, covering at least the technical and organisational measures specified in Section 2. | As a principle, we suggest that consultations should be public so that any party can choose to respond if it believes it is impacted. |  |  | technical |  |  |  | Non-confidential
0005-4855-855f-8046-2e64 | V1.0 for Public consultation version | 2 | 8 | 1 | - | 2014-12-08 16:38:53 | Rothermann Philippe |  | final | Each TSO shall design a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Each TSO shall design a System Defence Plan in coordination with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Coordination and not only consultation | [6 empty] | Non-confidential
0005-6f65-115c-e54e-996d | V1.0 for Public consultation version | 2 | 8 | 1 | - | 2014-12-08 16:39:15 | Markus Hemmer | EnBW | final | Each TSO shall design a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Each TSO shall design a System Defence Plan in consultation and agreement with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Stakeholders shall not only be consulted. An agreement is essential to such a defence plan. Otherwise there could be requirements which can not be met by stakeholders. | [6 empty] | Non-confidential
0005-2159-6001-2527-c984 | V1.0 for Public consultation version | 2 | 8 | 1 | - | 2014-12-08 17:01:14 | Jasmina PIERRE | EdF | final | Each TSO shall design a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Each TSO shall design a System Defence Plan in coordination with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | The consultation process proposed by ENTSO-E would lead the final decision to TSO without possible recourse from others parties if their constraints are not duly considered. It is essential all the instructions given by the TSO for execution respect the technical constraints and minimize related impacts for grid users. ENTSO-E proposals should be reinforced and foresee a final neutral decision from relevant NRA in case no agreement is reached (reference to coordination process defined in article 5). |  |  | technical |  |  |  | Non-confidential
0005-487d-75dc-0cb5-36bc | V1.0 for Public consultation version | 2 | 8 | 1 | - | 2014-12-08 17:16:55 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall design a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Each TSO shall design a System Defence Plan in coordination with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | It is important for DSOs and significant grid users that there is a mutual agreement (based on mutual understanding and trust) between the DSO, grid user and the TSO on the design of the system defence plan. A consultation does not provide for this agreement (cf. art. 5). |  |  | legal |  |  |  | Non-confidential
0005-bd99-c5f6-1017-c010 | V1.0 for Public consultation version | 2 | 8 | 1 | - | 2014-12-03 11:14:53 | AXPO Group |  | final | Each TSO shall design a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Each TSO shall design a System Defence Plan in coordination with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | The design shall be in coordination, not consultation (as defined in Article 5) with DSO's and others. Measures generate costs. DSO's and others have a cost liability towards regulating authorities. Therefore they need to have the right for participation in decision-making. |  |  | legal |  |  |  | Non-confidential
0005-2196-b422-e837-8d43 | V1.0 for Public consultation version | 2 | 8 | 1 | - | 2014-11-28 15:52:39 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall design a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Each TSO shall design a System Defence Plan in coordination with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | It is important for DSOs and significant grid users that there is a mutual agreement (based on mutual understanding and trust) between the DSO, grid user and the TSO on the design of the system defence plan. A consultation does not provide for this agreement (cf. art. 5). |  |  | legal |  |  |  | Non-confidential
0005-e4e5-5e41-4b1f-c959 | V1.0 for Public consultation version | 2 | 8 | 1 | - | 2014-12-08 20:11:10 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | The decision-making process described in this Network Code appears to be unbalanced in view of the consequences of the requirements involved, notably concerning the preventive system defence plans. These consultation processes are inappropriate for taking decisions towards residential consumers. Although the TSOs - as they are responsible for the security of the electricity system - shall be given exceptional extended authority in emergency, blackout and restoration situations, there should be a supervision by national regulatory authorities to ensure that the principles of proportionality and social welfare are respected, in particular when such plans have consequences on small residential consumers. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2274 | V1.0 for Public consultation version | 2 | 8 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall design a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Each TSO shall design a System Defence Plan in consultation coordination with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | It is important for the DSOs that there is a mutual agreement (based on mutual understanding and trust) between the DSO and the TSO on the design of the system defence plan. A consultation does not provide for this agreement (cf. art. 5). It is not sufficient to only consult on a system defense plan, it must be coordinated between TSOs, DSOs and SGUs to respect the constraints of the overall vertically interconnected system. As the design phase of the plan is a non time-critical issue, exactness rather than speed should rule the process. The NC OS (umbrella code) does not provide the use of consultation instead of coordination. All actions and/or decisions specified in the NC OS in which the DSO is involved are always in coordination with the TSO, so it makes no sense to introduce consultation in the NC ER. ENTSO-E should consider to introduce the definition of 'coordination' (now in art. 5) in the NC OS so that it is valid in all system operation codes. Using "consultation" instead of "coordination" does also contradict the regulations on DSOs in Directive 2003/54/EC (Article 14). |  |  | Technical
0005-e495-5e7a-d54d-1980 | V1.0 for Public consultation version | 2 | 8 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall design a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Each TSO shall design a System Defence Plan in coordination with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | It is important for DSOs and significant grid users that there is a mutual agreement (based on mutual understanding and trust) between the DSO, grid user and the TSO on the design of the system defence plan. A consultation does not provide for this agreement (cf. art. 5).
0005-e495-5e7a-d54d-2147 | V1.0 for Public consultation version | 2 | 8 | 1 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO shall design a System Defence Plan in consultatoon with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Each TSO shall propose a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical, oreganisational measures specified in Section 2, which shall be submitted to NRA(s) for approval. | This is the critical element of the NC ER and it's vital that NRAs approve this. |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-1726 | V1.0 for Public consultation version | 2 | 8 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall design a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2. | Each TSO shall PROPOSE A design OF a System Defence Plan in consultation with DSOs, Significant Grid Users and neighbouring TSOs, covering at least the technical and organisational measures specified in Section 2 WHICH SHALL BE SUBMITTED TO THE NRA(S) FOR APPROVAL. | This is a critical element of the whole NC E&R and its vital that NRAs approve this.
0005-9676-663e-e76f-f669 | V1.0 for Public consultation version | 2 | 8 | 2 | - | 2014-11-28 15:52:40 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | characteristics of its Network. | characteristics of the Networks in its control area. | Also DSO networks must be considered. |  |  | technical |  |  |  | Non-confidential
0005-6f79-85c7-a0b0-ce58 | V1.0 for Public consultation version | 2 | 8 | 2 | - | 2014-12-07 12:51:40 | Herve MELJAC | EUR | final |  | We propose to merge Article 8.2 and 8.4, to make clearer that technical capability of SGUs in the design of System Defence plans. | The current drafting is confusing |  |  | legal |  |  |  | Non-confidential
0005-e4bd-c573-25ef-2349 | V1.0 for Public consultation version | 2 | 8 | 2 | - | 2014-12-08 17:01:14 | Jasmina PIERRE | EdF | final | When designing a System Defence Plan, each TSO shall take into account, at least: […] d) specific needs of the Significant Grid Users listed as high priority Significant Grid Users pursuant to Article 32(10) [NC OS]; and e) characteristics of its Network. | When designing a System Defence Plan, each TSO shall take into account, at least: […] d) specific needs of the Significant Grid Users listed as high priority Significant Grid Users pursuant to Article 32(10) [NC OS]; and e) characteristics of its Network ; and f) technical constraints of the Significant Grids Users. | It is essential all the instructions given by the TSO for execution respect the respective technical constraints and minimize related impacts for grid users. Furthermore, the reference to “high priority Significant Grid Users pursuant to NS OS” needs is essential. Such a disposal should be maintained to ensure, in particular, that defense plan will consider how to restore nuclear power plants without compromising nuclear safety. |  |  | technical |  |  |  | Non-confidential
0005-48a5-857c-0f0d-627d | V1.0 for Public consultation version | 2 | 8 | 2 | - | 2014-12-08 17:16:57 | Paul Doyle | ESB Generation & Wholesale Markets | final | characteristics of its Network. | characteristics of the Networks in its control area. | Also DSO networks must be considered. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-1981 | V1.0 for Public consultation version | 2 | 8 | 2 | e | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | characteristics of its Network. | characteristics of the Networks in its control area. | Also DSO networks must be considered.
0005-e495-5e7a-d54d-2275 | V1.0 for Public consultation version | 2 | 8 | 2 | f | 2014-12-08 22:31 | Michael Wilch | RWE | final | - | characteristics and requirements of underlying Distribution Systems | Paragraph to be added. DSOs play a special role in this NC and should therefore be mentioned explicitly. Respecting the underlying distribution system properly is crucial for the success of any system defence plan. |  |  | Technical
0005-e495-5e7a-d54d-2240 | V1.0 for Public consultation version | 2 | 8 | 2 |  | 2014-12-08 12:24 | Wolfram Heckmann | Fraunhofer IWES | final | “e) characteristics of its Network” |  | The term is very generic, a specification what characteristics are meant would help.
0005-e4a9-d360-0f0d-95d7 | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-12-08 17:17:01 | Paul Doyle | ESB Generation & Wholesale Markets | final | the measures are economically efficient; | the measures are economically efficient for all participants; | It must be clear that the the overall economy is meant, and not one single market participant |  |  | legal |  |  |  | Non-confidential
0005-2159-855e-0c51-ce86 | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-12-08 17:17:02 | Paul Doyle | ESB Generation & Wholesale Markets | final | the minimum necessary measures are activated; and | the necessary measures with minimum impact on society and overall economy are activated; and | the minimum has to be defined to make this statement binding |  |  | legal |  |  |  | Non-confidential
0005-e496-cbce-e7d3-654c | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-11-28 15:52:41 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | In the design of its System Defence Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; | In the design of its System Defence Plan, each TSO shall respect the following principles: a) the impact for all impacted Grid Users is minimal; | Grid Users must be defined in this code or reference made to the code which contains the definition. All impacted Grid Users must be considered. | [6 empty] | Non-confidential
0005-9675-75dc-0e45-7a65 | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-12-08 17:17:31 | Paul Doyle | ESB Generation & Wholesale Markets | final | the measures do not endanger the Operational Security of the neighbouring Transmission Systems. | the measures do not endanger the Operational Security of the neighbouring Transmission Systems, DSO networks or Grid Users. | Endangering of DSO networks and Grid Users shall also be prevented. |  |  | technical |  |  |  | Non-confidential
0005-e4d2-8d12-e9c7-f042 | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-11-28 15:52:42 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | the measures are economically efficient; | the measures are economically efficient for all participants; | It must be clear that the the overall economy is meant, and not one single market participant |  |  | legal |  |  |  | Non-confidential
0005-969d-4ecc-0e45-6e06 | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-12-08 17:17:33 | Paul Doyle | ESB Generation & Wholesale Markets | final | new clause | e) the measures do not lead to damages on the assets of Grid Users or Sysgtem Operators. | Add new subparagraph. The principle that also assets of grid users and System Operators shall not be damaged. |  |  | legal |  |  |  | Non-confidential
0005-968a-0842-e7d3-3f38 | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-11-28 15:52:42 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | the minimum necessary measures are activated; and | the necessary measures with minimum impact on society and overall economy are activated; and | the minimum has to be defined to make this statement binding |  |  | legal |  |  |  | Non-confidential
0005-bd85-c3fc-0d7d-b375 | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-12-08 17:09:24 | Paul Doyle | ESB Generation & Wholesale Markets | final | new clause | f) the measures are suitable for the purpose foreseen. | Add new subparagraph. |  |  | technical |  |  |  | Non-confidential
0005-6fa2-663e-e963-3d7d | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-11-28 15:53:00 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | the measures do not endanger the Operational Security of the neighbouring Transmission Systems. | the measures do not endanger the Operational Security of the neighbouring Transmission Systems, DSO networks or Grid Users. | Endangering of DSO networks and Grid Users shall also be prevented. |  |  | technical |  |  |  | Non-confidential
0005-e4aa-8d12-e963-cdc6 | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-11-28 15:53:01 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | new clause | e) the measures do not lead to damages on the assets of Grid Users or Sysgtem Operators. | Add new subparagraph. The principle that also assets of grid users and System Operators shall not be damaged. |  |  | legal |  |  |  | Non-confidential
0005-6f66-2f8e-e76f-dc4a | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-11-28 15:51:09 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | new clause | f) the measures are suitable for the purpose foreseen. | Add new subparagraph. |  |  | technical |  |  |  | Non-confidential
0005-4869-868c-e422-ef93 | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-12-08 16:39:16 | Markus Hemmer | EnBW | final | the impact for Grid Users is minimal; | the impact for all Grid Users is minimal; | It should be clear, that the impact for ALL Grid Users (PGFs, Demand Facilities,…) is minimal | [6 empty] | Non-confidential
0005-bdad-4fbe-e35a-9fb2 | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-12-08 16:39:16 | Markus Hemmer | EnBW | final | In the design of its System Defence Plan, each TSO shall respect the following principles: […] | 3. In the design of its System Defence Plan, each TSO shall respect the following principles: […] e) the measures do not lead to damages on the assets of Grid Users or Sysgtem Operators. | This point is essential to avoid any harm to assets which could be usefull for the Restoration of the System. Since e.g. TSOs are not anymore concerned with the possibilities and needs of the assets of stakeholders, there is a risk that some requirements ould lead to damages. | [6 empty] | Non-confidential
0005-487d-5fe3-2527-a462 | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-12-08 17:01:15 | Jasmina PIERRE | EdF | final | 3. In the design of its System Defence Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; c) the minimum necessary measures are activated; and d) the measures do not endanger the Operational Security of the neighbouring Transmission Systems. | 3. In the design of its System Defence Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient (cost efficiency including all participants); c) the minimum necessary measures are activated; d) the measures do not endanger the Operational Security of the neighbouring Transmission Systems, Grid Users and DSO networks; and e) the measures do not lead to damages on the assets of Grid Users or System Operators. | It is essential all the instructions given by the TSO for execution respect the technical constraints and minimize related impacts for all involved parties (including Grid users) and pursue "cost overall efficiency". |  |  | technical |  |  |  | Non-confidential
0005-216d-d360-0d19-525a | V1.0 for Public consultation version | 2 | 8 | 3 | - | 2014-12-08 17:16:59 | Paul Doyle | ESB Generation & Wholesale Markets | final | In the design of its System Defence Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; | In the design of its System Defence Plan, each TSO shall respect the following principles: a) the impact for all impacted Grid Users is minimal; | Grid Users must be defined in this code or reference made to the code which contains the definition. All impacted Grid Users must be considered. | [6 empty] | Non-confidential
0005-9689-ae20-a03d-42f3 | V1.0 for Public consultation version | 2 | 8 | 3 | a | 2014-12-04 13:58:06 | Dekinderen Eric | Genrator company | final | In the design of its System Defence Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; | the impact for all Grid Users is minimal; | Which Grid Users ? Only of the TSO or of the TSO and DSO? |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-1982 | V1.0 for Public consultation version | 2 | 8 | 3 | a | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | In the design of its System Defence Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; | In the design of its System Defence Plan, each TSO shall respect the following principles: a) the impact for all impacted Grid Users is minimal; | Grid Users must be defined in this code or reference made to the code which contains the definition. All impacted Grid Users must be considered.
0005-e495-5e7a-d54d-2148 | V1.0 for Public consultation version | 2 | 8 | 3 | a | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | (…) the impact for Grid Users is minimal (…) | (…) the impact for Significant Grid Users is minimal (…) | The reference to just 'Grid Users' is misleading. Should be replaced by 'Significant Grid Users'. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1728 | V1.0 for Public consultation version | 2 | 8 | 3 | A | 2014-12-08 13:31 | Garth Graham | SSE |  | the impact for Grid Users is minimal | the impact for SIGNIFICANT Grid Users is minimal | The reference to just ‘Grid Users’ is misleading as the definition in the metadata repository only refer to the NC HVDC definition – and as that code is limited in its application (to HVDC users) it gives a misleading and inappropriate application if used here.
0005-e495-5e7a-d54d-1983 | V1.0 for Public consultation version | 2 | 8 | 3 | b | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | the measures are economically efficient; | the measures are economically efficient for all participants; | It must be clear that the the overall economy is meant, and not one single market participant
0005-e495-5e7a-d54d-2149 | V1.0 for Public consultation version | 2 | 8 | 3 | b | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | (…) the measures are economically efficient (…) | (…) the measures are economic, efficient, reasonable and proportionate | The terms "reasonable" and "proportionate" appear in Article 4(2) and should be used here as well. |  |  | Technical | Editorial
0005-e495-5e7a-d54d-2276 | V1.0 for Public consultation version | 2 | 8 | 3 | b | 2014-12-08 22:31 | Michael Wilch | RWE | final | the measures are economically efficient; | the measures are economically efficient for the overall economy; | It must be clear that the overall economy is meant, and not one single market participant. |  |  | Legal
0005-e495-5e7a-d54d-1730 | V1.0 for Public consultation version | 2 | 8 | 3 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | the measures are economically efficient | the measures are economically, efficient, REASONABLE AND PROPORTIONATE | The words reasonable and proportionate appears in Art 4(2) and should be used here as well.
0005-e495-5e7a-d54d-1984 | V1.0 for Public consultation version | 2 | 8 | 3 | c | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | the minimum necessary measures are activated; and | the necessary measures with minimum impact on society and overall economy are activated; and | the minimum has to be defined to make this statement binding
0005-e495-5e7a-d54d-2277 | V1.0 for Public consultation version | 2 | 8 | 3 | c | 2014-12-08 22:31 | Michael Wilch | RWE | final | the minimum necessary measures are activated; and | the minimum necessary measures, to manage the situation that can be foreseen and which involves the part of the network related directly to the critical situation, with minimum impact on society and overall economy are activated; and | The 'minimum' has to be defined to make this statement binding. Just also to clarify that the impact of the Defence Plan has to be minimal for the all users and customers connected to the network at transmission and distribution level for all voltage levels. These users are different from the SGUs that are involved in the Defence Plans and have an active role. |  |  | Legal
0005-e495-5e7a-d54d-1985 | V1.0 for Public consultation version | 2 | 8 | 3 | d | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | the measures do not endanger the Operational Security of the neighbouring Transmission Systems. | the measures do not endanger the Operational Security of the neighbouring Transmission Systems, DSO networks or Grid Users. | Endangering of DSO networks and Grid Users shall also be prevented.
0005-e495-5e7a-d54d-2278 | V1.0 for Public consultation version | 2 | 8 | 3 | d | 2014-12-08 22:31 | Michael Wilch | RWE | final | the measures do not endanger the Operational Security of the neighbouring Transmission Systems. | the measures do not endanger the Operational Security of the neighbouring Transmission Systems and of neighbouring Distribution Systems and of Distribution Systems directly connected to the Transmission Systems. | The design of defense plan should not endanger the operational security of DSOs. |  |  | Technical
0005-e495-5e7a-d54d-1986 | V1.0 for Public consultation version | 2 | 8 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | new clause | e) the measures do not lead to damages on the assets of Grid Users or Sysgtem Operators. | Add new subparagraph. The principle that also assets of grid users and System Operators shall not be damaged.
0005-e495-5e7a-d54d-1987 | V1.0 for Public consultation version | 2 | 8 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | new clause | f) the measures are suitable for the purpose foreseen. | Add new subparagraph.
0005-96b1-76c0-3ded-5fe5 | V1.0 for Public consultation version | 2 | 8 | 4 | - | 2014-12-05 10:20:02 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | for Significant Grid Users and new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; | for Significant Grid Users; | Type A Generators are not mentioned in the scope, so in our understanding they cannot be taken into accout, eccept they are significant (article 1, 6.) . | 2 | 3 | technical |  |  |  | Non-confidential
0005-6f79-4ecb-c92f-39c3 | V1.0 for Public consultation version | 2 | 8 | 4 | - | 2014-12-08 19:51:13 | Roland Tual | SEDC | final | In the design of its System Defence Plan, each TSO shall consider the capabilities required: a) for Significant Grid Users and new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in national legislation for Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC] | [8 empty] | confidential
0005-e495-5e7a-d54d-2279 | V1.0 for Public consultation version | 2 | 8 | 4 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | In the design of its System Defence Plan, each TSO shall consider the capabilities required: a) for Significant Grid Users and new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in national legislation for Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | In the design of its System Defence Plan, each TSO shall consider the capabilities required: a) for Significant Grid Users and new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in national legislation for Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | The TSO seems only to consider certain capabilities. What are the criteria to determine whether the TSO will consider certain capabilities or not? DSOs understand the need to consider the behaviour of type A PGMs in the design of the defence plan, but do not see the immediate need for using the capabalities as such. Is this reasonable for type A? DSOs are convinced new type A PGMs should not be part of the NC ER yet, because: * SGU are defined in NC OS, standing alone type A PGMs (as from 800W!) are not significant for the security of the system; * This creates high barriers for the development of DG and RES, in terms of costs (communication channels, smart inverters, testing). Articles 8§3 and 20§3 are very clear however, the design of the defence and the restoration plans needs to be with "minimal impact for Grid Users" and the measures must be "economically efficient". * Since not all new type A PGMs seem to be involved, this might create discrimination of treatment; * Are there studies available that indicate future necessity of type A PGMs for Emergency and Restoration of the electrical system? No CBA is available to justify the use of capabilities of type A PGMs in Emergency and Restoration, let alone for creation of suitable communication infrastructure. Emergency and Restoration is a real time process, the existing communication channels are not suitable for LV mass market.* 95% (and even more) of the outages come from the distribution side. Type A PGMs are never considered by the DSOs in their own restoration processes. * Coordination is key in the ER process; type A PGMs will complicate the restoration process, because the more Grid Users that have to be considered the worse the efficiency of the restoration process - and hence its effectiveness - will be. * ENTSO-E confirmed several times type A PGM capabilities were not going to be used in the near future (5 years). |  |  | Technical
0005-e495-5e7a-d54d-1732 | V1.0 for Public consultation version | 2 | 8 | 4 | A | 2014-12-08 13:31 | Garth Graham | SSE |  | for Significant Grid Users and new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and | for FROM Significant Grid Users and new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and | Typo
0005-969d-76ce-e292-5a06 | V1.0 for Public consultation version | 2 | 8 | 4 | b | 2014-12-08 16:39:16 | Markus Hemmer | EnBW | final | In national legislation for Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | b) in national legislation for Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. or bilateral Contracts | There are many Grid users which have their own contracts with TSOs which requirements they have to fullfil. In national legislation there are usually no requirements named so contracts are a better base for this reason. | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-1734 | V1.0 for Public consultation version | 2 | 8 | 4 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | in national legislation for Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | SET OUT in national legislation for Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | Typo
0005-e495-5e7a-d54d-1988 | V1.0 for Public consultation version | 2 | 8 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | In the design of its System Defence Plan, each TSO shall consider the capabilities required: a) for Significant Grid Users and new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in national legislation for Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | In the design of its System Defence Plan, each TSO shall consider the capabilities required: a) on behalf of Significant Grid Users and new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in national legislation for Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | The TSO seems only to consider certain capabilities. To prevent discrimination, criteria to determine whether the TSO will consider certain capabilities or not must be defined in this code. We understand the need to consider the behaviour of type A PGMs in the design of the defence plan, but do not see the immediate need for using the capabilities as such. Is this reasonable for type A? We are convinced that new type A PGMs should not be part of the NC ER yet, because: * SGU are defined in NC OS, standing alone type A PGMs (as from 800W!) are not significant for the security of the system; * This creates high barriers for the development of DG and RES, in terms of costs (communication channels, smart inverters, testing). Articles 8§3 and 20§3 are very clear however, the design of the defence and the restoration plans needs to be with "minimal impact for Grid Users" and the measures must be "economically efficient". * Since not all new type A PGMs seem to be involved, this might create discrimination of treatment; * Are there studies available that indicate future necessity of type A PGMs for Emergency and Restoration of the electrical system? No CBA is available to justify the use of capabilities of type A PGMs in Emergency and Restoration, let alone for creation of suitable communication infrastructure. Emergency and Restoration is a real time process, the existing communication channels are not suitable for LV mass market.* 95% (and even more) of the outages come from the distribution side. Will DSOs be able to consider all Type A PGMs in their own restoration processes? * Coordination is key in the ER process; type A PGMs will complicate the restoration process, because the more Grid Users that have to be considered the worse the efficiency of the restoration process - and hence its effectiveness - will be. * ENTSO-E confirmed several times type A PGM capabilities were not going to be used in the near future (5 years).
0005-48a5-7752-a105-b6e3 | V1.0 for Public consultation version | 2 | 8 | 5 | - | 2014-12-04 14:01:07 | Dekinderen Eric | Genrator company | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the System Defence Plan. | ???????????????????????? | What are "significant grid users" at a company with several PGMs? Each PGM itself or the central dispatch of this company? |  |  | legal |  |  |  | Non-confidential
0005-6fa1-38f0-a105-4008 | V1.0 for Public consultation version | 2 | 8 | 5 | - | 2014-12-04 14:01:39 | Dekinderen Eric | Genrator company | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the System Defence Plan. |  | What happens if a SGU refuses his role in the System Defence Plan. See provision in Art 38 regarding communication as an example for refusal |  |  | legal |  |  |  | Non-confidential
0005-e495-1130-3acd-38f3 | V1.0 for Public consultation version | 2 | 8 | 5 | - | 2014-12-05 10:20:25 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the System Defence Plan. | Each TSO shall identify the DSOs, Significant Grid Users that have an active role for providing the necessary services in case of activation of the System Defence Plan. | Type A Generators are not mentioned in the scope, so in our understanding they cannot be taken into accout, eccept they are significant (article 1, 6.) . | 1 | 2 | technical |  |  |  | Non-confidential
0005-6f65-0190-3c5d-9bd9 | V1.0 for Public consultation version | 2 | 8 | 5 | - | 2014-12-05 10:21:05 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the System Defence Plan. | Each TSO shall identify the DSOs and Significant Grid Users that have an active role for providing the necessary services in case of activation of the System Defence Plan. Each TSO shall procure all Services necessary to activate the System Defence Plan | According to FWGL FG-2011-E-003 on System Operations, TSOs shall ensure access (contracted or otherwise procured) to sufficient black-start capacities and islanding capabilities to allow for the efficient and fast restoration. | 1 | 3 | legal |  |  |  | Non-confidential
0005-bdd5-77d6-1337-f27f | V1.0 for Public consultation version | 2 | 8 | 5 | - | 2014-12-03 11:17:31 | AXPO Group |  | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the System Defence Plan. | Each TSO shall identify the DSOs and Significant Grid Users that have an active role for providing the necessary services in case of activation of the System Defence Plan. | Not the TSO shall identify new type A Power Generating Modules. That is the job of the DSO. The DSO then reports to the TSO. |  |  | legal |  |  |  | Non-confidential
0005-bdd5-00ac-0bed-e227 | V1.0 for Public consultation version | 2 | 8 | 5 | - | 2014-12-08 17:09:26 | Paul Doyle | ESB Generation & Wholesale Markets | final | new clause | In the event that there is a dispute over the inclusion of a SGU in the System Defence Plan, the NRA shall be asked to decide. | What happens if a SGU refuses his role in the System Defence Plan. See provision in Art 38 regarding communication | [6 empty] | Non-confidential
0005-e4aa-3f10-e70b-f8b7 | V1.0 for Public consultation version | 2 | 8 | 5 | - | 2014-11-28 15:51:09 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | new clause | In the event that there is a dispute over the inclusion of a SGU in the System Defence Plan, the NRA shall be asked to decide. | What happens if a SGU refuses his role in the System Defence Plan. See provision in Art 38 regarding communication | [6 empty] | Non-confidential
0005-2145-5e4d-c8cb-f7d1 | V1.0 for Public consultation version | 2 | 8 | 5 | - | 2014-12-08 19:51:13 | Roland Tual | SEDC | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the System Defence Plan. | [8 empty] | confidential
0005-9689-00ab-c8cb-dadb | V1.0 for Public consultation version | 2 | 8 | 5 | - | 2014-12-08 19:51:14 | Roland Tual | SEDC | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating, Modules that have an active role for providing the necessary services in case of activation of the System Defense Plan | [8 empty] | confidential
0005-9675-ad82-90a8-702c | V1.0 for Public consultation version | 2 | 8 | 5 | - | 2014-12-05 11:33:48 | Agnieszka Panek |  | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the System Defence Plan. | Each TSO shall identify and inform the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the System Defence Plan. | System users should know that they are taken into account at system defence plan. |  |  | technical |  |  |  | Non-confidential
0005-4891-ae03-23fb-2cfb | V1.0 for Public consultation version | 2 | 8 | 5 | - | 2014-12-08 17:01:15 | Jasmina PIERRE | EdF | final | (new) | In the event that there is a dispute over the inclusion of a SGU in the System Defence Plan, the relevant NRA shall be asked to decide. | If the System Defense Plan designed by TSOs do not fully respect constraints from Significant Grid Users that have been identified, the latter may contest this role. In case of dispute, a "resolution" process invloving the relevant NRA should be foreseen. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2280 | V1.0 for Public consultation version | 2 | 8 | 5 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the System Defence Plan. | Based on the economically efficiency requirement of Article 8 §3.b), each TSO shall identify the DSOs and Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the System Defence Plan and involve them in the process. | DSOs are convinced that new type A PGMs should not be part of the NC ER, cf. explanation art. 8§4. TSO must involve all parties that have an active role to play in the Defence Plan. |  |  | Technical
0005-e495-5e7a-d54d-1989 | V1.0 for Public consultation version | 2 | 8 | 5 | b | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | new clause | In the event that there is a dispute over the inclusion of a SGU in the System Defence Plan, the NRA shall be asked to decide. | What happens if a SGU refuses his role in the System Defence Plan. See provision in Art 38 regarding communication
0005-e495-5e7a-d54d-1736 | V1.0 for Public consultation version | 2 | 8 | 5 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the System Defence Plan. | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary PROCURED services in case of activation of the System Defence Plan. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to those services being procured.
0005-96b1-868b-d0c8-48fe | V1.0 for Public consultation version | 2 | 8 | 6 | - | 2014-12-05 17:01:43 | Til Kristian Vrana |  | final | manual Demand disconnection procedure | manual Load disconnection procedure | Demand is the interest in receiving electric energy. It is not a technical device, which can be disconnected. Load can be disconnected. Possibly "net load" could be used here, but not demand. |  |  | technical |  |  |  | Non-confidential
0005-487d-02a6-10df-2d08 | V1.0 for Public consultation version | 2 | 8 | 6 | - | 2014-12-03 11:17:31 | AXPO Group |  | final | Original text of issue 13.10.2014 | see Comment | The automatisation of an extensive plan that consist of many heavily interdependent parameters seems not makeable. Only parts of the whole plan may be suitable for automatisation. Especially an emergency situation cannot be handled by computers alone. Any complex facility like power stations, aeroplanes, industrial plants are ultimately managed by persons. The same applies to a grid. Further the financial expense to implement all requested automatic schemes is immense. The grade of automatisation requested by the article is too high. |  |  | technical |  |  |  | Non-confidential
0005-4869-101e-d3be-7ef2 | V1.0 for Public consultation version | 2 | 8 | 6 | - | 2014-12-08 23:56:23 | Gunnar Kaestle | Clausthal University of Technology | final | i. automatic low frequency control scheme; ii automatic high frequency control scheme | i. automatic over-frequency control scheme; ii automatic under-frequency control scheme | over and under describes a parameter above a certain threshold, where as high and low describes a certain range. High frequency is the ITU designation for the range from 3-30 MHz. An over frequency active power reduction kicks in at a certain threshold (most commonly 50,2 Hz). In this context high and low frequency are the wrong terms. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2281 | V1.0 for Public consultation version | 2 | 8 | 6 | a | 2014-12-08 22:31 | Michael Wilch | RWE | final | System Protection Schemes including at least: i. automatic low Frequency control scheme; ii. automatic high Frequency control scheme; and iii. automatic scheme against Voltage collapse. | System Protection Schemes including at least: i. automatic low Frequency control scheme. | ii. and iii. are new requirements, but do not match existing reality. How will this be economically justified? CBA available? |  |  | Technical
0005-2145-4e9e-d54e-b1f5 | V1.0 for Public consultation version | 2 | 8 | 6 | b | 2014-12-08 23:56:23 | Gunnar Kaestle | Clausthal University of Technology | final | v. manual Demand disconnection procedure | v. manual load shedding procedure | "Demand" is a term that matches to "Supply", both coming from the domain of macroeconomics. "Generator" and "Load" is the terminus technicus for an electrical source or sink of electrical energy. The commonly used term for disconnecting consumers is "load shedding" (see http://www.electropedia.org/iev/iev.nsf/display?openform&ievref=603-04-32). It is strongy not recommended to introduce a new European dialect for technical english, but to reuse the global electrotechnical vocabulary in European legislation to avoid misunderstandings. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-1740 | V1.0 for Public consultation version | 2 | 8 | 6 | B Iv | 2014-12-08 13:31 | Garth Graham | SSE |  | assistance for Active Power procedure; | assistance for Active Power procedure; | Art 8 (6) (b) (i)-(iii) and (v) all refer to a procedure without ‘assistance for’ so why is it used here?
0005-e495-5e7a-d54d-2364 | V1.0 for Public consultation version | 2 | 8 | 6 | b5 | 2014-12-09 09:29 | Dr. Til Kristian Vrana | Sintef | final | manual Demand disconnection procedure | manual Load disconnection procedure | Demand is the interest in receiving electric energy. It is not a technical device, which can be disconnected. Load can be disconnected. Possibly net load could be used here, but not demand.
0005-6f79-8540-0d7d-69c0 | V1.0 for Public consultation version | 2 | 8 | 8 | - | 2014-12-08 17:09:27 | Paul Doyle | ESB Generation & Wholesale Markets | final | b) context triggering the measures of the System Defence Plan; and | b) parameters and limits triggering the measures of the System Defence Plan; and | The term "context" is far too less specific for the purpose |  |  | technical |  |  |  | Non-confidential
0005-9689-8540-0de1-fc17 | V1.0 for Public consultation version | 2 | 8 | 8 | - | 2014-12-08 17:09:29 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall notify the concept of the System Defence Plan to its National Regulatory Authority or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the System Defence Plan. | Each TSO shall notify the concept of the System Defence Plan to its National Regulatory Authority and parties identified in accordance with Article 8.4 or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the System Defence Plan. | Also parties mentioned in Article 8.4 must be informed! |  |  | legal |  |  |  | Non-confidential
0005-e4be-087e-e9c7-1947 | V1.0 for Public consultation version | 2 | 8 | 8 | - | 2014-11-28 15:51:10 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | b) context triggering the measures of the System Defence Plan; and | b) parameters and limits triggering the measures of the System Defence Plan; and | The term "context" is far too less specific for the purpose |  |  | technical |  |  |  | Non-confidential
0005-2146-6620-e963-d2bb | V1.0 for Public consultation version | 2 | 8 | 8 | - | 2014-11-28 15:51:11 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall notify the concept of the System Defence Plan to its National Regulatory Authority or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the System Defence Plan. | Each TSO shall notify the concept of the System Defence Plan to its National Regulatory Authority and parties identified in accordance with Article 8.4 or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the System Defence Plan. | Also parties mentioned in Article 8.4 must be informed! |  |  | legal |  |  |  | Non-confidential
0005-bd85-ac6d-c803-ab02 | V1.0 for Public consultation version | 2 | 8 | 8 | - | 2014-12-08 19:51:14 | Roland Tual | SEDC | final | Each TSO shall notify the concept of the System Defense Plan to its National Regulatory, Authority or, when explicitly foreseen in national law, other relevant national authorities, | [8 empty] | confidential
0005-e495-5e7a-d54d-2282 | V1.0 for Public consultation version | 2 | 8 | 8 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall notify the concept of the System Defence Plan to its National Regulatory Authority or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the System Defence Plan. | Each TSO shall notify the concept of the System Defence Plan to its National Regulatory Authority or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the System Defence Plan. | It seems only logical to notify the complete Defence Plan to the NRA, not only the concept. |  |  | Technical
0005-e495-5e7a-d54d-1990 | V1.0 for Public consultation version | 2 | 8 | 8 | b | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | b) context triggering the measures of the System Defence Plan; and | b) parameters and limits triggering the measures of the System Defence Plan; and | The term "context" is far too less specific for the purpose
0005-e495-5e7a-d54d-2283 | V1.0 for Public consultation version | 2 | 8 | 8 | b | 2014-12-08 22:31 | Michael Wilch | RWE | final | context triggering the measures of the System Defence Plan; and | parameters and limits context triggering the measures of the System Defence Plan; and | The term "context" is far too less specific for the purpose. |  |  | Technical
0005-e495-5e7a-d54d-1744 | V1.0 for Public consultation version | 2 | 8 | 8 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | context triggering the measures of the System Defence Plan; and | context triggering the measures of the System Defence Plan; and | Add in Art 8 (8) (d)
0005-e495-5e7a-d54d-1745 | V1.0 for Public consultation version | 2 | 8 | 8 | C | 2014-12-08 13:31 | Garth Graham | SSE |  | general principle of each measure, explaining how each measure contributes to the objectives of the System Defence Plan. | general principle of each measure, explaining how each measure contributes to the objectives of the System Defence Plan., AND | Add in Art 8 (8) (d)
0005-e495-5e7a-d54d-2284 | V1.0 for Public consultation version | 2 | 8 | 8 | d | 2014-12-08 22:31 | Michael Wilch | RWE | final | - | justification of the economical efficiency of the measures as required in Article 8 §3.b). | Paragraph to be added. The economic efficiency of the decisions made when designing the defense plan must be justified. |  |  | Legal
0005-e495-5e7a-d54d-1746 | V1.0 for Public consultation version | 2 | 8 | 8 | D | 2014-12-08 13:31 | Garth Graham | SSE |  | Xyz | THE DETAILS OF THE MEASURES THE TSO WILL IMPLEMENT ON THEIR SYSTEM ACCORDACNE WITH ARTICLE 9 (1) AND THE MEASEURE THE TSO WILL NOTIFY TO DSO(S) AND / OR SIGNIFICANT GRID USERS IN ACCORDANCEE WITH ARTICLE 9 (2) (A) AND (B). | The measures to be imposed should also set out in the System Defence Plan. If they are NOT to be set out here, then where are they to be set out? Who approves these measures – it must not be the TSO who approves the measure to apply to their own system as this amounts to asking a child to mark their own exam work….it sounds good to those who wish to do it (the TSOs) …but sounds (and is) ridiculous in practice.
0005-e495-5e7a-d54d-1991 | V1.0 for Public consultation version | 2 | 8 | 8 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall notify the concept of the System Defence Plan to its National Regulatory Authority or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the System Defence Plan. | Each TSO shall notify the concept of the System Defence Plan to its National Regulatory Authority and parties identified in accordance with Article 8.4 or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the System Defence Plan. | Also parties mentioned in Article 8.4 must be informed.
0005-e495-5e7a-d54d-2150 | V1.0 for Public consultation version | 2 | 8 | 8 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO shall notify the concept of the System Defence Plan to the National Regulatory Authorities or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to this article and subsequently pursuant to any changes of the concept of the System Defence Plan. The concept of the System defence Plan shall include the following: | Each TSO shall submit the System defence Plan to its National Regulatory Authority or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes to the System Defence Plan. The System Defence Plan shall include: | The System Defence Plan is a key element oof the NC ER and must be subject to explicit NRA approval. External oversight is vital to give confidence to all stakeholders and consumers across the 28 Member States that the System Defence Plan(s) are robust and fit for purpose. |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-2250 | V1.0 for Public consultation version | 2 | 8 | 8 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each TSO shall notify the concept of the System Defense Plan to its National Regulatory, Authority or, when explicitly foreseen in national law, other relevant national authorities, |  | The TSO will only notify national governments what they have already planned concerning national citizens. They do not ask permission. This is unacceptable when customers and small generators are included in national plans. A wider set of considerations must be taken into account than those under the TSO's control.
0005-e495-5e7a-d54d-1742 | V1.0 for Public consultation version | 2 | 8 | 8 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall notify the concept of the System Defence Plan to its National Regulatory Authority or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the System Defence Plan. The concept of the System Defence Plan shall include the following: | Each TSO shall notify the concept of SUBMIT the System Defence Plan to its National Regulatory Authority or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of TO the concept of the System Defence Plan. The concept of the System Defence Plan shall include the following: | The System Defence Plan is a key element of the NC E&R and MUST be subject to explicit NRA approval. If an NRA is unable / unwilling to do this then they should be able to ask ACER to do it on their behalf. It must be remembered that the event, in November 2006, that gave rise to the Network Codes being developed arose from the actions of TSOs and NOT Significant Grid Users. It would therefore be perverse to allow the TSOs alone to write their own homework question, answer it and then mark it. External oversight is vital to give confidence to all stakeholders and consumers across the 28 Member States that the System Defence Plan(s) are robust and fit for purpose.
0005-e495-5e7a-d54d-2146 | V1.0 for Public consultation version | 2 | 8 |  |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | See the wording of Article 8- general comment | See the justification. | It is disappointing that the Code is not a pan-European System Defence Plan/ Restoration Plan, but rather a loosly linked collection of each TSOs national plans. One may ask: what is the added value of a pan-European network code in comparison to the current situation. |  |  | Technical | Fundamental
0005-bdd5-d480-3b95-17bb | V1.0 for Public consultation version | 2 | 9 | 1 | - | 2014-12-05 10:21:40 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each TSO shall make available the measures of its System Defence Plan which are to be implemented on the Transmission System. | Each TSO shall make available the measures of its System Defence Plan which are to be implemented on the Transmission System. Each TSO shall procure the services from the significant grid users necesary to activate the System Defence plan | According to FWGL FG-2011-E-003 on System Operations, TSOs shall ensure access (contracted or otherwise procured) to sufficient black-start capacities and islanding capabilities to allow for the efficient and fast restoration. | 1 | 2 | legal |  |  |  | Non-confidential
0005-9689-4eaf-7f7e-7972 | V1.0 for Public consultation version | 2 | 9 | 1 | - | 2014-12-08 16:38:52 | Rothermann Philippe |  | final |  |  | The TSO should involve the DSO's by planning the measures for the system defence plan, because some measures will take a lot of time to be implemented in the distribution grid. We would prefer to complete the article with a paragraph, which stipulates that the TSO must cooperate with the DSO's. | [6 empty] | Non-confidential
0005-2195-acf5-a04c-3a03 | V1.0 for Public consultation version | 2 | 9 | 1 | - | 2014-12-07 12:51:41 | Herve MELJAC | EUR | final | Each TSO shall make available the measures of its System Defence Plan which are to be implemented on the Transmission System. | Each TSO shall make sure the measures of its System Defence Plan which are to be implemented on the Transmission System are available for use at all time. | Wording not clear. When reading the initial version, the read is tempted to ask "to whom? Where? How?" |  |  | legal |  |  |  | Non-confidential
0005-4891-5e6b-c803-b26e | V1.0 for Public consultation version | 2 | 9 | 1 | - | 2014-12-08 19:51:14 | Roland Tual | SEDC | final | Each TSO shall: a) notify DSOs the measures of the System Defense Plan which are to be implemented, on their installations and/or the installations of Significant Grid Users and new type A, Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | [8 empty] | confidential
0005-e495-5e7a-d54d-2285 | V1.0 for Public consultation version | 2 | 9 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall make available the measures of its System Defence Plan which are to be implemented on the Transmission System. | After consultation of and coordination with all involved parties, each TSO shall make available the measures of its System Defence Plan which are to be implemented on the Transmission System. | The implementation should follow the principles of consultation/coordination stated in Article 5. Please explain what is precisely meant by 'measures'. |  |  | Technical
0005-e495-5e7a-d54d-2252 | V1.0 for Public consultation version | 2 | 9 | 1 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each TSO shall make available the measures of its System Defence Plan which are to be implemented on the Transmission System. |  | Safety and environmental measures should be coordinated with DSO/TSO measures of the defense plan (e.g. flaring)
0005-e495-5e7a-d54d-2253 | V1.0 for Public consultation version | 2 | 9 | 1 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each TSO shall: a) notify DSOs the measures of the System Defense Plan which are to be implemented, on their installations and/or the installations of Significant Grid Users and new type A, Power Generating Modules connected to their Distribution System, including the deadlines for implementation; |  | Again - here we have notification only. A consumer/PV owner will be notified what they have to do by the TSO or by the DSO. This notification simply includes deadlines for compliance. There is no discussion of cost mitigation for example
0005-e495-5e7a-d54d-1747 | V1.0 for Public consultation version | 2 | 9 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall make available the measures of its System Defence Plan which are to be implemented on the Transmission System. | Each TSO shall IMPLEMENT AND make available the measures of its THE System Defence Plan which are to be implemented on the Transmission System IN THE TIMSECALES SPECIFIED BY THE NRA(S). | Given the reference in Art 9 (2) (a) and (b) to DSO and SGUs having to implement the measures its important that the TSOs, likewise, have to implement the measures…after all if they are not ‘implemented’ then they cannot (as suggested with the current wording) be ‘made available’. It is important to recognise that the System Defence Plan it not the TSO’s, so ‘its’ should be replaced by ‘the’.
0005-e495-5e7a-d54d-1748 | V1.0 for Public consultation version | 2 | 9 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall make available the measures of its System Defence Plan which are to be implemented on the Transmission System. | Each TSO shall IMPLEMENT AND make available the measures of its THE System Defence Plan which are to be implemented on the Transmission System IN THE TIMSECALES SPECIFIED BY THE NRA(S). | Measures to be implemented on the transmission system should be specified by the NRA. Given that the TSO is not proposing (in Art 9 (2) (a) or (b) any appeal on the deadlines they set for DSOs or SGUs then they presumably do not require any appeal for a deadline set by the NRA(s)?!
0005-6f79-01ae-3dec-3efb | V1.0 for Public consultation version | 2 | 9 | 2 | - | 2014-12-05 10:24:52 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each TSO shall notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | Each TSO shall elaborate a recommendation for each DSO, based on the consultation(discussion) in Article 8, according the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users connected to their Distribution System, including the deadlines for implementation; | measures should be agreed, the TSO is not a NRA. | 1 | 4 | legal |  |  |  | Non-confidential
0005-e4be-7d72-e8ff-eadf | V1.0 for Public consultation version | 2 | 9 | 2 | - | 2014-11-28 15:51:14 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan, determined in collaboration between the TSO, the DSO and the SGU, which are to be implemented on their installations, including the deadlines for implementation. | The article imposes measures to be implemented on their installations within a certain deadline. It seems a rather unidirectional order coming from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO, DSO and SGU. Notification of the SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). |  |  | technical |  |  |  | Non-confidential
0005-216e-2f52-e89b-9344 | V1.0 for Public consultation version | 2 | 9 | 2 | - | 2014-11-28 15:51:15 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | There are no further implementations necessary. Either the Gri User has to fullfil the requirements of e.g. NC RfG or NC DC or requirements of bilateral contracts or the implementations are already agreed as stated in Article 5(2) of this NC. |  |  | legal |  |  |  | Non-confidential
0005-bdd5-75a0-0d19-e2ef | V1.0 for Public consultation version | 2 | 9 | 2 | - | 2014-12-08 17:09:31 | Paul Doyle | ESB Generation & Wholesale Markets | final | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs directly connected to its Transmission System the measures of the System Defence Plan, determined in collaboration between the TSO, the DSO and the SGU, which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | To conform with the framework of cascading measures, each System Operator shall notify only its own customers. The article imposes measures to be implemented on their installations within a certain deadline. It seems a rather unidirectional order coming from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO, DSO and SGU. |  |  | technical |  |  |  | Non-confidential
0005-4891-d39c-0d19-ec16 | V1.0 for Public consultation version | 2 | 9 | 2 | - | 2014-12-08 17:09:32 | Paul Doyle | ESB Generation & Wholesale Markets | final | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | There are no further installations necessary. Either the Gri User has to fullfil the requirements of e.g. NC RfG or NC DC or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | legal |  |  |  | Non-confidential
0005-96c5-4ecc-0c51-d035 | V1.0 for Public consultation version | 2 | 9 | 2 | - | 2014-12-08 17:09:34 | Paul Doyle | ESB Generation & Wholesale Markets | final | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan, determined in collaboration between the TSO, the DSO and the SGU, which are to be implemented on their installations, including the deadlines for implementation. | The article imposes measures to be implemented on their installations within a certain deadline. It seems a rather unidirectional order coming from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO, DSO and SGU. Notification of the SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). |  |  | technical |  |  |  | Non-confidential
0005-2181-c4f2-9300-e4d5 | V1.0 for Public consultation version | 2 | 9 | 2 | - | 2014-12-05 11:33:48 | Agnieszka Panek |  | final | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | To conform with the framework of cascading measures, each System Operator shall notify only its own customers. The article imposes measures to be implemented on their installations within a certain deadline. |  |  | technical |  |  |  | Non-confidential
0005-969e-2f52-e837-94e9 | V1.0 for Public consultation version | 2 | 9 | 2 | - | 2014-11-28 15:51:12 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs directly connected to its Transmission System the measures of the System Defence Plan, determined in collaboration between the TSO, the DSO and the SGU, which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | To conform with the framework of cascading measures, each System Operator shall notify only its own customers. The article imposes measures to be implemented on their installations within a certain deadline. It seems a rather unidirectional order coming from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO, DSO and SGU. |  |  | technical |  |  |  | Non-confidential
0005-487d-5e4e-0e45-6a14 | V1.0 for Public consultation version | 2 | 9 | 2 | - | 2014-12-08 17:09:35 | Paul Doyle | ESB Generation & Wholesale Markets | final | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | There are no further implementations necessary. Either the Gri User has to fullfil the requirements of e.g. NC RfG or NC DC or requirements of bilateral contracts or the implementations are already agreed as stated in Article 5(2) of this NC. |  |  | legal |  |  |  | Non-confidential
0005-96c5-ad9c-e486-9770 | V1.0 for Public consultation version | 2 | 9 | 2 | - | 2014-12-08 16:39:16 | Markus Hemmer | EnBW | final | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs the measures of the System Defence Plan which of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | There are no further installations necessary. Either the Gri User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. | [6 empty] | Non-confidential
0005-2146-0842-e963-2a54 | V1.0 for Public consultation version | 2 | 9 | 2 | - | 2014-11-28 15:51:13 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | There are no further installations necessary. Either the Gri User has to fullfil the requirements of e.g. NC RfG or NC DC or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2286 | V1.0 for Public consultation version | 2 | 9 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall: a) notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; b) notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | Each TSO shall: a) notify DSOs, directly connected to the Transmission Network, the measures of the System Defence Plan, determined in collaboration between the TSO and the DSO, which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation, agreed upon between TSO, DSOs and NRA; b) notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | The article imposes measures to be implemented on their installations within a certain deadline. It seems a rather uniderictional order coming from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO and the DSO. Notification just to DSOs directly connected to the Transmission Network, to keep within the framework of cascading measures, each System Operator shall notify only underlying SOs. Notification of the SGUs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). This point of view can be resumed in two main points: * unilateral actions from one SO on the network of another SO without coordination could create security problems at local (DSO) level, which could be worse than the problem that was supposed to be solved. * it creates inefficiency (duplication of communication channels). DSOs are convinced that new type A PGMs should not be part of the NC ER, cf. explanation art. 8§4. |  |  | Technical
0005-e495-5e7a-d54d-1992 | V1.0 for Public consultation version | 2 | 9 | 2 | a | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs directly connected to its Transmission System the measures of the System Defence Plan, determined in collaboration between the TSO, the DSO and the SGU, which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | To conform with the framework of cascading measures, each System Operator shall notify only its own customers. The article imposes measures to be implemented on their installations within a certain deadline. It seems a rather unidirectional order coming from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO, DSO and SGU.
0005-e495-5e7a-d54d-1993 | V1.0 for Public consultation version | 2 | 9 | 2 | a | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | There are no further installations necessary. Either the Gri User has to fullfil the requirements of e.g. NC RfG or NC DC or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC.
0005-e495-5e7a-d54d-2151 | V1.0 for Public consultation version | 2 | 9 | 2 | a | 2014-12-08 21:33 | Wilch | RWE | final | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs directly connected to its Transmission System the measures of the System Defence Plan, determined in collaboration between the TSO, the DSO and the SGU, which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | Each System Operator should notify solely its own customers. This article imposes measures to be implemented on their installations within a certain deadline. This order should not come solely from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO, DSO and SGU. | 1 | 4 | Technical | Fundamental
0005-e495-5e7a-d54d-2152 | V1.0 for Public consultation version | 2 | 9 | 2 | a | 2014-12-08 21:33 | Eberhard | EnBW | final | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | There are no further implementation necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or NC DCC or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1749 | V1.0 for Public consultation version | 2 | 9 | 2 | A | 2014-12-08 13:31 | Garth Graham | SSE |  | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs the measures of the System Defence Plan which are to be implemented on their installations and/or TO BE PROCURED FROM the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-96c5-c50c-e616-c2d3 | V1.0 for Public consultation version | 2 | 9 | 2 | b | 2014-12-08 16:39:16 | Markus Hemmer | EnBW | final | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | There are no further implementation necessary. Either the Gri User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the implementations are already agreed as stated in Article 5(2) of this NC. | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-1994 | V1.0 for Public consultation version | 2 | 9 | 2 | b | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan, determined in collaboration between the TSO, the DSO and the SGU, which are to be implemented on their installations, including the deadlines for implementation. | The article imposes measures to be implemented on their installations within a certain deadline. It seems a rather unidirectional order coming from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO, DSO and SGU. Notification of the SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS).
0005-e495-5e7a-d54d-1995 | V1.0 for Public consultation version | 2 | 9 | 2 | b | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | There are no further implementations necessary. Either the Gri User has to fullfil the requirements of e.g. NC RfG or NC DC or requirements of bilateral contracts or the implementations are already agreed as stated in Article 5(2) of this NC.
0005-e495-5e7a-d54d-2153 | V1.0 for Public consultation version | 2 | 9 | 2 | b | 2014-12-08 21:33 | Wilch | RWE | final | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan, determined in collaboration between the TSO, the DSO and the SGU, which are to be implemented on their installations, including the deadlines for implementation. | Each System Operator should notify solely its own customers. This article imposes measures to be implemented on their installations within a certain deadline. This order should not come solely from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO, DSO and SGU. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2154 | V1.0 for Public consultation version | 2 | 9 | 2 | b | 2014-12-08 21:33 | Eberhard | EnBW | final | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | There are no further implementations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or NC DC or requirements of bilateral contracts or the implementations are already agreed as stated in Article 5(2) of this NC. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1751 | V1.0 for Public consultation version | 2 | 9 | 2 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be PROCURED AND implemented on their installations, including the deadlines for implementation. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-1752 | V1.0 for Public consultation version | 2 | 9 | 2 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | notify Significant Grid Users directly connected to its Transmission System the measures of the System Defence Plan which are to be implemented on their installations, including the deadlines for implementation. | ….., including the deadlines for implementation. A SIGNIFICANT GRID USER MAY USE THE DEROGATION AND APPEAL PROCESS SET OUT IN THE NC RFG OR NC DC (AS APPROPRIATE) IF THEY BELIEVE THE SYSTEM DEFENCE PLAN MEASURES PROPOSED BY THE TSO ARE TO ONEROUS. | If the measures are not to be procured then a derogation and appeal process is required whereby SGUs can appeal to the NRA.
0005-9689-4e90-0de1-f47d | V1.0 for Public consultation version | 2 | 9 | 3 | - | 2014-12-08 17:09:38 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify other DSOs, Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation. | To work conform the framework of cascading measures, each System Operator shall notify its own customers incl. Underlayed DSOs. |  |  | technical |  |  |  | Non-confidential
0005-9689-9dde-e486-766f | V1.0 for Public consultation version | 2 | 9 | 3 | - | 2014-12-08 16:39:17 | Markus Hemmer | EnBW | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan , unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | There are no further implementation necessary. Either the Gri User has to fullfil the requirements of NCs of Grid Connection or requirements of bilateral contracts or the implementations are already agreed as stated in Article 5(2) of this NC. | [6 empty] | Non-confidential
0005-487d-c3fc-0de1-153c | V1.0 for Public consultation version | 2 | 9 | 3 | - | 2014-12-08 17:15:44 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | There are no further implementation necessary. Either the Gri User has to fullfil the requirements of NCs of Grid Connection or requirements of bilateral contracts or the implementations are already agreed as stated in Article 5(2) of this NC. |  |  | legal |  |  |  | Non-confidential
0005-96c6-db50-e837-1f65 | V1.0 for Public consultation version | 2 | 9 | 3 | - | 2014-11-28 15:51:16 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation. | Notification of the SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Still the question on how this will be done for new type A PGMs. |  |  | technical |  |  |  | Non-confidential
0005-e4bd-297a-1337-e2af | V1.0 for Public consultation version | 2 | 9 | 3 | - | 2014-12-03 11:14:54 | AXPO Group |  | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | see Comment | To work conform to the framework of cascading measures, each System Operator shall notify its own customers including underlayed DSOs. There is only ONE line of communication. |  |  | legal |  |  |  | Non-confidential
0005-487e-3f2e-e8ff-3abc | V1.0 for Public consultation version | 2 | 9 | 3 | - | 2014-11-28 15:51:17 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify other DSOs, Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation. | To work conform the framework of cascading measures, each System Operator shall notify its own customers incl. Underlayed DSOs. |  |  | technical |  |  |  | Non-confidential
0005-969e-3ef2-e8ff-d8ca | V1.0 for Public consultation version | 2 | 9 | 3 | - | 2014-11-28 15:51:17 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | There are no further implementation necessary. Either the Gri User has to fullfil the requirements of NCs of Grid Connection or requirements of bilateral contracts or the implementations are already agreed as stated in Article 5(2) of this NC. |  |  | legal |  |  |  | Non-confidential
0005-487d-00ac-0f0d-2356 | V1.0 for Public consultation version | 2 | 9 | 3 | - | 2014-12-08 17:09:36 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation. | Notification of the SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Still the question on how this will be done for new type A PGMs. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2287 | V1.0 for Public consultation version | 2 | 9 | 3 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify other DSOs, Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation. , unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Notification of the SGUs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Notification just to DSOs directly connected to the Transmission Network, to keep within the framework of cascading measures, each System Operator shall notify only underlying SOs. DSOs are convinced that new type A PGMs should not be part of the NC ER, cf. explanation art. 8§4. |  |  | Technical
0005-e495-5e7a-d54d-1996 | V1.0 for Public consultation version | 2 | 9 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation. | Notification of the SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Still the question on how this will be done for new type A PGMs.
0005-e495-5e7a-d54d-1997 | V1.0 for Public consultation version | 2 | 9 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify other DSOs, Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation. | To work conform the framework of cascading measures, each System Operator shall notify its own customers incl. Underlayed DSOs.
0005-e495-5e7a-d54d-1998 | V1.0 for Public consultation version | 2 | 9 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | There are no further implementation necessary. Either the Gri User has to fullfil the requirements of NCs of Grid Connection or requirements of bilateral contracts or the implementations are already agreed as stated in Article 5(2) of this NC.
0005-e495-5e7a-d54d-2155 | V1.0 for Public consultation version | 2 | 9 | 3 |  | 2014-12-08 21:33 | Wilch | RWE | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify other DSOs, Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation. | Each System Operator should notify solely its own customers. | 1 | 5 | Technical | Fundamental
0005-e495-5e7a-d54d-2156 | V1.0 for Public consultation version | 2 | 9 | 3 |  | 2014-12-08 21:33 | Eberhard | EnBW | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO already notified the Significant Grid Users and new type A Power Generating Modules. | There are no further implementation necessary. Either the Gri dUser has to fullfil the requirements of NCs of Grid Connection or requirements of bilateral contracts or the implementations are already agreed as stated in Article 5(2) of this NC. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1753 | V1.0 for Public consultation version | 2 | 9 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan which they have to implement on their installations, including the deadlines for implementation, …. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the System Defence Plan TO BE PROCURED FROM THEM which they have to implement on their installations, including the deadlines for implementation, …. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-1755 | V1.0 for Public consultation version | 2 | 9 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | ….including the deadlines for implementation, ….unless | ….including the deadlines for implementation, ….A SIGNIFICANT GRID USER OR NEW TYPE A POWER GENERATING MODULE MAY USE THE DEROGATION AND APPEAL PROCESS SET OUT IN THE NC RFG OR NC DC (AS APPROPRIATE) IF THEY BELIEVE THE SYSTEM DEFENCE PLAN MEASURES PROPOSED BY THE TSO ARE TO ONEROUS., unless | If the measures are not to be procured then a derogation and appeal process is required whereby SGUs can appeal to the NRA.
0005-2195-0190-3b94-5070 | V1.0 for Public consultation version | 2 | 9 | 4 | - | 2014-12-05 10:25:34 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each notified DSO, Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and | Each notified DSO, Significant Grid User shall: a) implement the measuresthat are agreed with the TSO and confirm this implementation to the notifying Network Operator; Costs for DSOs and Significant Grid Users arrising from retrofit measures shall be aproved by the NRA and fefunded by the TSO. | Costs for DSOs and Significant Grid Users arrising from retrofit measures shall be approved by the NRA and refunded by the TSO | 1 | 3 | legal |  |  |  | Non-confidential
0005-e4d1-5061-25ef-493f | V1.0 for Public consultation version | 2 | 9 | 4 | - | 2014-12-08 17:01:16 | Jasmina PIERRE | EdF | final | b) make available the measures implemented on its installations. | To be clarified | It is unclear what "make measures available" means. Available to whom? What exactly? Measurements and signals? |  |  | technical |  |  |  | Non-confidential
0005-6fb5-76ec-e35a-e67a | V1.0 for Public consultation version | 2 | 9 | 4 | - | 2014-12-08 16:39:17 | Markus Hemmer | EnBW | final | implement the measures notified to them and confirm this implementation to the notifying Network Operator; and | delete | The implementation of the measures is not necessary, since there are no additional implementations possible. All possible requirements are stated in NC on Grid Connection or Contracts. | [6 empty] | Non-confidential
0005-216d-8540-0bed-8ca4 | V1.0 for Public consultation version | 2 | 9 | 4 | - | 2014-12-08 17:15:46 | Paul Doyle | ESB Generation & Wholesale Markets | final | implement the measures notified to them and confirm this implementation to the notifying Network Operator; and | delete | The implementation of the measures is not necessary, since there are no additional implementations possible. All possible requirements are stated in NC on Grid Connection or Contracts. |  |  | legal |  |  |  | Non-confidential
0005-4869-9ee6-126f-29db | V1.0 for Public consultation version | 2 | 9 | 4 | - | 2014-12-03 11:14:54 | AXPO Group |  | final | make available the measures implemented on its installations. | see Comment | It is uncelar what "make measures available" means. Available to whom? What exactly? Measurements and signals? |  |  | technical |  |  |  | Non-confidential
0005-48a5-008e-0f71-87c8 | V1.0 for Public consultation version | 2 | 9 | 4 | - | 2014-12-08 17:15:48 | Paul Doyle | ESB Generation & Wholesale Markets | final | b) make available the measures implemented on its installations. |  | It is unclear what "make measures available" means. Available to whom? What exactly? Measurements and signals? |  |  | technical |  |  |  | Non-confidential
0005-2145-373e-0cb5-bbb3 | V1.0 for Public consultation version | 2 | 9 | 4 | - | 2014-12-08 17:15:50 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each notified DSO, Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and b) make available the measures implemented on its installations. |  | How will this be done in practice for new type A PGMs? This sounds unworkable, especially the confirmation. Even if the number of new type A PGMs being part of the defence plan might be limited in the beginning, this number will rise in the future. Furthermore, by only picking out a number of new type A PGMs, there may be a risk of discrimination because of not treating all new type A PGMs in the same way. |  |  | technical |  |  |  | Non-confidential
0005-bdc2-7d72-e7d3-38a1 | V1.0 for Public consultation version | 2 | 9 | 4 | - | 2014-11-28 15:52:10 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | implement the measures notified to them and confirm this implementation to the notifying Network Operator; and | delete | The implementation of the measures is not necessary, since there are no additional implementations possible. All possible requirements are stated in NC on Grid Connection or Contracts. |  |  | legal |  |  |  | Non-confidential
0005-48a6-5680-e9c7-7364 | V1.0 for Public consultation version | 2 | 9 | 4 | - | 2014-11-28 15:52:11 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | b) make available the measures implemented on its installations. |  | It is unclear what "make measures available" means. Available to whom? What exactly? Measurements and signals? |  |  | technical |  |  |  | Non-confidential
0005-486a-8d30-e76f-9db3 | V1.0 for Public consultation version | 2 | 9 | 4 | - | 2014-11-28 15:52:12 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each notified DSO, Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and b) make available the measures implemented on its installations. |  | How will this be done in practice for new type A PGMs? This sounds unworkable, especially the confirmation. Even if the number of new type A PGMs being part of the defence plan might be limited in the beginning, this number will rise in the future. Furthermore, by only picking out a number of new type A PGMs, there may be a risk of discrimination because of not treating all new type A PGMs in the same way. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2288 | V1.0 for Public consultation version | 2 | 9 | 4 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each notified DSO, Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and b) make available the measures implemented on its installations. | Each notified DSO and Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and b) make available the measures implemented on its installations. | How will this be done in practice for new type A PGMs? This sounds unworkable, especially the confirmation. DSOs are convinced that new type A PGMs should not be part of the NC ER, cf. explanation art. 8§4. |  |  | Technical
0005-e495-5e7a-d54d-1999 | V1.0 for Public consultation version | 2 | 9 | 4 | a | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | implement the measures notified to them and confirm this implementation to the notifying Network Operator; and | delete | The implementation of the measures is not necessary, since there are no additional implementations possible. All possible requirements are stated in NC on Grid Connection or Contracts. Measures to imply, implementation deadline and responsabilities shall be part of the contract as a result of the agreement in Article 5.2.
0005-e495-5e7a-d54d-2000 | V1.0 for Public consultation version | 2 | 9 | 4 | b | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | b) make available the measures implemented on its installations. |  | It is unclear what "make measures available" means. Available to whom? What exactly? Measurements and signals?
0005-e495-5e7a-d54d-1757 | V1.0 for Public consultation version | 2 | 9 | 4 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | make available the measures implemented on its installations. | make available the measures implemented on its installations IN ACCORDANCE WITH THE PROCUREMENT ARRANGEMENTS ENTERED INTO WITH THE RELEVANT NETWORK OPERATOR. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-2001 | V1.0 for Public consultation version | 2 | 9 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each notified DSO, Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and b) make available the measures implemented on its installations. |  | How will this be done in practice for new type A PGMs? This sounds unworkable, especially the confirmation. Even if the number of new type A PGMs being part of the defence plan might be limited in the beginning, this number will rise in the future. Furthermore, by only picking out a number of new type A PGMs, there may be a risk of discrimination because of not treating all new type A PGMs in the same way.
0005-e495-5e7a-d54d-2240 | V1.0 for Public consultation version | 2 | 9 | 4 |  | 2014-12-08 12:24 | Wolfram Heckmann | Fraunhofer IWES | final | “b) make available the measures implemented…” |  | How should the availability be provided and verified especially for individual type A Power Generating Modules?
0005-bdc1-9eaa-107b-c239 | V1.0 for Public consultation version | 2 | 9 | - | - | 2014-12-03 11:17:31 | AXPO Group |  | final | missing paragraph | see Comment | Add new paragraph 5: The procurement of all measures defined by the System Defence Plan is NOT clear. How is the TSO going to pay DSO's, SGU's and others for making available all the measurements of the System Defence Plan and the Restoration Plan? |  |  | legal |  |  |  | Non-confidential
0005-6f8d-4eae-0f71-df41 | V1.0 for Public consultation version | 2 | 10 | 1 | - | 2014-12-08 17:15:51 | Paul Doyle | ESB Generation & Wholesale Markets | final | the system is in Emergency State due to at least one deviation from the Operational Security Limits and no Remedial Action is available to restore the system to Normal State; | the system is in Emergency State due to at least one deviation from the Operational Security Limits and no immediate Remedial Action is available to restore the system to Normal State; | Also in the case where Remedial Actions are not available until tomorrow (or next week), the system is in Emergency State! |  |  | legal |  |  |  | Non-confidential
0005-6f66-db6e-e7d3-9fbd | V1.0 for Public consultation version | 2 | 10 | 1 | - | 2014-11-28 15:52:13 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | the system is in Emergency State due to at least one deviation from the Operational Security Limits and no Remedial Action is available to restore the system to Normal State; | the system is in Emergency State due to at least one deviation from the Operational Security Limits and no immediate Remedial Action is available to restore the system to Normal State; | Also in the case where Remedial Actions are not available until tomorrow (or next week), the system is in Emergency State! |  |  | legal |  |  |  | Non-confidential
0005-bdc1-9caf-c993-94f7 | V1.0 for Public consultation version | 2 | 10 | 1 | - | 2014-12-08 19:51:14 | Roland Tual | SEDC | final | Such preparation concerns, but is not limited to, assistance for Active Power and manual Demand Disconnection. | [8 empty] | confidential
0005-e495-5e7a-d54d-2289 | V1.0 for Public consultation version | 2 | 10 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | In addition to the measures of the System Defence Plan to be automatically activated, each TSO shall activate a procedure of the System Defence Plan when: | In addition to the measures of the System Defence Plan to be automatically activated, each TSO shall activate, in coordination with the relevant DSOs , a procedure of the System Defence Plan when: | Cf. remark art. 9§2. |  |  | Technical
0005-e495-5e7a-d54d-2002 | V1.0 for Public consultation version | 2 | 10 | 1 | a | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | the system is in Emergency State due to at least one deviation from the Operational Security Limits and no Remedial Action is available to restore the system to Normal State; | the system is in Emergency State due to at least one deviation from the Operational Security Limits and no immediate Remedial Action is available to restore the system to Normal State; | Also in the case where Remedial Actions are not available until tomorrow (or next week), the system is in Emergency State.
0005-e495-5e7a-d54d-2157 | V1.0 for Public consultation version | 2 | 10 | 1 | a | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | the System is in Emergency State due to at least one deviation from the Operational Security Limits and no Remedial Action is available to restore the system to Normal State; | the system is in Emergency State due to at least one deviation from the Operational Security Limits and no Remedial Action is available to restore the system to Normal State; | There is a definition of 'Emergency State' and that's when the System Defence Plan should be activated. The additional words here will only confuse the situation. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1758 | V1.0 for Public consultation version | 2 | 10 | 1 | A | 2014-12-08 13:31 | Garth Graham | SSE |  | the system is in Emergency State due to at least one deviation from the Operational Security Limits and no Remedial Action is available to restore the system to Normal State; | the system is in Emergency State due to at least one deviation from the Operational Security Limits and no Remedial Action is available to restore the system to Normal State; | There is a definition of ‘Emergency State’ and that’s when the System defence Plan should be activated. The additional words here will only confuse the situation.
0005-e495-5e7a-d54d-2290 | V1.0 for Public consultation version | 2 | 10 | 1 | c | 2014-12-08 22:31 | Michael Wilch | RWE | final | in application of a specific procedure as defined in the System Defence Plan and notified to its National Regulatory Authority or, when explicitly foreseen in national law, other relevant national authorities. | in application of a specific procedure as defined in the System Defence Plan and notified to its National Regulatory Authority or, when explicitly foreseen in national law, other relevant national authorities. | This subparagraph does not fit with the main part of the paragraph ("when in application…"). It is also unnecessary, as it is obvious from the format and content of the whole draft NC that national regulation must define details and specific procedures. The example provided by the supporting document (solar eclipse 2015) in not appropriate, as the risk of an event like this (known long before its start) can be hedged using market instruments. |  |  | Technical
0005-e495-5e7a-d54d-2255 | V1.0 for Public consultation version | 2 | 10 | 1 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Such preparation concerns, but is not limited to, assistance for Active Power and manual Demand Disconnection. |  | The defense plan may include requiring consumers to manually turn everything off. This is unacceptable for small consumers and generators as it may cause safety issues. This required proper regulatory oversight and government supervision. (If small consumers/generators are not under consideration for this measure - why are they included in the code?)
0005-e495-5e7a-d54d-2158 | V1.0 for Public consultation version | 2 | 10 | 2 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each DSO and Significant Grid User shall execute System Defence Plan instructions issued by the TSO, according to System Defence Plan procedures. | Each DSO and Significant Grid User shall where technically feasible and without endangering personel safetly and damaging equipment execute System Defence Plan instructions issued by TSO, according to System Defence Plan procedures. | The action requested must be technically feasible and must not endanger personel or plant as this would violate health and safetly legislation and expose TSO to legal action. |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-1760 | V1.0 for Public consultation version | 2 | 10 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each DSO and Significant Grid User shall execute System Defence Plan instructions issued by the TSO, according to System Defence Plan procedures | Each DSO and Significant Grid User shall WHERE TECHNICALLY FEASIBLE AND WITHOUT ENDANGERING PERSONNEL SAFETY OR DAMAGING EQUIPMENT execute System Defence Plan instructions issued by the TSO, according to System Defence Plan procedures | The action requested must be technically feasible and must not endanger personnel or plant as this would violate health and safety legislation and expose the TSO to legal action, including, but not limited to, criminal proceedings. In addition it would also expose the TSO to the full liability with respect to Article 1 of the First Protocol of the European Convention on Human Rights.
0005-e495-5e7a-d54d-2291 | V1.0 for Public consultation version | 2 | 10 | 3 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall coordinate activation of System Defence Plan measures having a significant cross-border impact, with the impacted TSOs. | Each TSO shall coordinate activation of System Defence Plan measures having a significant cross-border impact, with the impacted TSOs. | By design, this NC must only handle issues with cross-border impact. It is therefore unnecessary to introduce an additional 'threshold' for coordination. |  |  | Technical
0005-e495-7771-2653-f88e | V1.0 for Public consultation version | 2 | 10 | 4 | - | 2014-12-08 17:01:16 | Jasmina PIERRE | EdF | final | A TSO may prepare the manual measures of its System Defence Plan prior to their activation. The TSO may launch such preparation phase in Normal or Alert State. Such preparation concerns, but is not limited to, assistance for Active Power and manual Demand Disconnection. | A TSO shall prepare the manual measures of its System Defence Plan prior to their activation. The TSO may launch such preparation phase in Normal or Alert State. Such preparation concerns, but is not limited to, assistance for Active Power and manual Demand Disconnection. | Measures of its System Plans needs to be prepared to minimize potential damages and costs due to rush actions. |  |  | technical |  |  |  | Non-confidential
0005-e4d1-375c-0c51-7168 | V1.0 for Public consultation version | 2 | 10 | 4 | - | 2014-12-08 17:15:53 | Paul Doyle | ESB Generation & Wholesale Markets | final | A TSO may prepare the manual measures of its System Defence Plan prior to their activation. The TSO may launch such preparation phase in Normal or Alert State. Such preparation concerns, but is not limited to, assistance for Active Power and manual Demand Disconnection. | A TSO shall prepare the manual measures of its System Defence Plan prior to their activation. The TSO may launch such preparation phase in Normal or Alert State. Such preparation concerns, but is not limited to, assistance for Active Power and manual Demand Disconnection. | To prevent panic actions leading to damages and costs, the TSO SHALL prepare it's measures. |  |  | technical |  |  |  | Non-confidential
0005-bd86-db6e-e7d3-e3e9 | V1.0 for Public consultation version | 2 | 10 | 4 | - | 2014-11-28 15:52:14 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | A TSO may prepare the manual measures of its System Defence Plan prior to their activation. The TSO may launch such preparation phase in Normal or Alert State. Such preparation concerns, but is not limited to, assistance for Active Power and manual Demand Disconnection. | A TSO shall prepare the manual measures of its System Defence Plan prior to their activation. The TSO may launch such preparation phase in Normal or Alert State. Such preparation concerns, but is not limited to, assistance for Active Power and manual Demand Disconnection. | To prevent panic actions leading to damages and costs, the TSO SHALL prepare it's measures. |  |  | technical |  |  |  | Non-confidential
0005-e4e5-85e5-a36c-ea13 | V1.0 for Public consultation version | 2 | 10 | 4 | - | 2014-12-07 12:51:41 | Herve MELJAC | EUR | final | When a TSO launches a preparation phase before activating a System Defence Plan measure with potential impact on interconnected transmission systems, it shall provide to the impacted TSOs all relevant information, including the expected time of activation and potential cross-border impact. | When a TSO launches a preparation phase before activating a System Defence Plan measure with potential impact on interconnected transmission systems, it shall provide to the impacted TSOs, DSOs and SGUs all relevant information, including the expected time of activation and potential cross-border impact. | Giving early heads-up of defence plan activation (or likely activation) to impacted SGUs and DSOs ultimately improves the likelihood that response will be optimal. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2292 | V1.0 for Public consultation version | 2 | 10 | 4 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | When a TSO launches a preparation phase before activating a System Defence Plan measure with potential impact on interconnected transmission systems, it shall provide to the impacted TSOs all relevant information, including the expected time of activation and potential cross-border impact. | When a TSO launches a preparation phase before activating a System Defence Plan measure with potential impact on interconnected transmission systems, it shall provide to the impacted TSOs and DSOs all relevant information, including the expected time of activation and potential cross-border impact. | Impacted DSOs, if any, should also be informed. |  |  | Technical
0005-e495-5e7a-d54d-2003 | V1.0 for Public consultation version | 2 | 10 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | A TSO may prepare the manual measures of its System Defence Plan prior to their activation. The TSO may launch such preparation phase in Normal or Alert State. Such preparation concerns, but is not limited to, assistance for Active Power and manual Demand Disconnection. | A TSO shall prepare the manual measures of its System Defence Plan prior to their activation. The TSO may launch such preparation phase in Normal or Alert State. Such preparation concerns, but is not limited to, assistance for Active Power and manual Demand Disconnection. | To prevent panic actions leading to damages and costs, the TSO shall prepare it's measures. There should be clear requirements on the TSOs.
0005-e495-5e7a-d54d-2159 | V1.0 for Public consultation version | 2 | 10 | 4 |  | 2014-12-08 21:33 | Wilch | RWE | final | Each notified DSO, Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and b) make available the measures implemented on its installations. |  | How will this be done in practice for new type A PGMs? This sounds very impractical. Even if the number of new type A PGMs being part of the defence plan might be limited in the beginning, this number will rise in the future. Furthermore, by only picking out a number of new type A PGMs, there may be a risk of discrimination because of not treating all new type A PGMs in the same way. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2004 | V1.0 for Public consultation version | 2 | 10 | 5 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | A new article should be added. The costs must be addressed to make sure that over all optimal economic sollutions will be used.
0005-e495-5e7a-d54d-2160 | V1.0 for Public consultation version | 2 | 10 | 5 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Add new Article | All measures of the System Defence Plan that are activated either automatically or manually shall be notified without delay to the NRAs and the concerned Member State(s) by the TSO. | The System Defence Plan is a key element of the NC ER and it's important, in the interest of openess and transparency, that any measure(s) activated is notified to the NRAs and the concerned Member State(s) by the TSO. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1764 | V1.0 for Public consultation version | 2 | 10 | 5 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | When a TSO launches …. | 5 When a TSO launches …. | Typo
0005-e495-5e7a-d54d-1765 | V1.0 for Public consultation version | 2 | 10 | 6 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Xyz | ALL MEASURED OF THE SYSTEM DEFENCE PLAN THAT ARE ACTIVATED EITHER AUTOMATICALLY OR MANUALLY SHALL BE NOTIFIED WITHOUT DELAY TO THE NRA(S) AND THE MEMBER STATE(S) BY THE TSO. | The System Defence Plan is a key element of the NC E&R and its important, in the interest of openness and transparency, that any measure(s) activated is notified to the NRAs and Member States immediately.
0005-6f65-75a1-298b-7b2e | V1.0 for Public consultation version | 2 | 10 | - | - | 2014-12-08 16:38:46 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | A new article should be added. The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | technical |  |  |  | Non-confidential
0005-96c5-c3c0-0e45-17ad | V1.0 for Public consultation version | 2 | 10 | - | - | 2014-12-08 17:15:55 | Paul Doyle | ESB Generation & Wholesale Markets | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | legal |  |  |  | Non-confidential
0005-968a-8d12-e963-697b | V1.0 for Public consultation version | 2 | 10 | - | - | 2014-11-28 15:52:14 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | legal |  |  |  | Non-confidential
0005-bd99-5fc4-a1cd-86b5 | V1.0 for Public consultation version | 2 | 11 | 1 | - | 2014-12-04 14:02:37 | Dekinderen Eric | Genrator company | final | Each TSO shall provide through AC Interconnectors any possible assistance to a neighbouring TSO in Emergency State, provided it does not endanger its own system. This assistance includes, but is not limited to, a curtailment of Cross Zonal Allocated Capacities in event of force majeure or Emergency Situation, according to Article 69 [NC CACM] and assistance for Active Power, according to Article 18. | Each TSO shall provide through AC interconnectors any possible assistance to a neighbouring TSO in Emergency State, provided it does not endanger its own system, hereby however duly respecting contracted generation capacity or other ressources for adequacy purposes with the neighbouring TSO. This assistance includes, but is not limited to, a curtailment of Cross Zonal Allocated Capacities in the event of force majeure or Emergency Situation, […] | XB CRM must be granted in emergency conditions. If not, XB CRM will be impossible |  |  | legal |  |  |  | Non-confidential
0005-e4a9-1011-2733-ecce | V1.0 for Public consultation version | 2 | 11 | 1 | - | 2014-12-08 16:38:48 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Each TSO shall provide through AC Interconnectors any possible assistance to a neighbouring TSO in Emergency State, provided it does not endanger its own system. This assistance includes, but is not limited to, a curtailment of Cross Zonal Allocated Capacities in event of force majeure or Emergency Situation, according to Article 69 [NC CACM] and assistance for Active Power, according to Article 18. | Each TSO shall provide through AC Interconnectors any possible assistance to a neighbouring TSO in Emergency State, provided it does not endanger its own system, hereby however duly respecting contracted generation capacity or other resources for adequacy purposes with the neighbouring TSO. This assistance includes, but is not limited to, a curtailment of Cross Zonal Allocated Capacities in event of an Emergency Situation, according to Article 69 [NC CACM] and assistance for Active Power, according to Article 18. | Why does this paragraph refer to "force majeur"? If there is an event which can be regarded as "force majeur", this event leads to an emergency situation (otherwise, it is not subject of this network code). It is therefore absolutely sufficient to refer only to emergency situations and close the backdoor of a general statement such as "force majeur". Energy contracted under a Capacity Remuneration Mechanism (CRM) should be delivered, even if its delivery may move the system hosting the CRM resource into the alert or emergency state. Otherwise CRMs in foreign system are not reliable, and CRM trading is de facto not feasible. | [6 empty] | Non-confidential
0005-6fb5-d360-0de1-ec2b | V1.0 for Public consultation version | 2 | 11 | 1 | - | 2014-12-08 17:15:56 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall provide through AC Interconnectors any possible assistance to a neighbouring TSO in Emergency State, provided it does not endanger its own system. This assistance includes, but is not limited to, a curtailment of Cross Zonal Allocated Capacities in event of force majeure or Emergency Situation, according to Article 69 [NC CACM] and assistance for Active Power, according to Article 18. | Each TSO shall provide through AC Interconnectors any possible assistance to a neighbouring TSO in Emergency State, provided it does not endanger its own system, hereby however duly respecting contracted generation capacity or other resources for adequacy purposes with the neighbouring TSO. This assistance includes, but is not limited to, a curtailment of Cross Zonal Allocated Capacities in event of an Emergency Situation, according to Article 69 [NC CACM] and assistance for Active Power, according to Article 18. | Why does this paragraph refer to "force majeur"? If there is an event which can be regarded as "force majeur", this event leads to an emergency situation (otherwise, it is not subject of this network code). It is therefore absolutely sufficient to refer only to emergency situations and close the backdoor of a general statement such as "force majeur". If this clause remains, CRM across borders is not possible. |  |  | legal |  |  |  | Non-confidential
0005-bdc2-087e-e8fe-9b27 | V1.0 for Public consultation version | 2 | 11 | 1 | - | 2014-11-28 15:52:15 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall provide through AC Interconnectors any possible assistance to a neighbouring TSO in Emergency State, provided it does not endanger its own system. This assistance includes, but is not limited to, a curtailment of Cross Zonal Allocated Capacities in event of force majeure or Emergency Situation, according to Article 69 [NC CACM] and assistance for Active Power, according to Article 18. | Each TSO shall provide through AC Interconnectors any possible assistance to a neighbouring TSO in Emergency State, provided it does not endanger its own system, hereby however duly respecting contracted generation capacity or other resources for adequacy purposes with the neighbouring TSO. This assistance includes, but is not limited to, a curtailment of Cross Zonal Allocated Capacities in event of an Emergency Situation, according to Article 69 [NC CACM] and assistance for Active Power, according to Article 18. | Why does this paragraph refer to "force majeur"? If there is an event which can be regarded as "force majeur", this event leads to an emergency situation (otherwise, it is not subject of this network code). It is therefore absolutely sufficient to refer only to emergency situations and close the backdoor of a general statement such as "force majeur". Energy contracted under a Capacity Remuneration Mechanism (CRM) should be delivered, even if its delivery may move the system hosting the CRM resource into the alert or emergency state. Otherwise CRMs in foreign system are not reliable, and CRM trading is de facto not feasible. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2293 | V1.0 for Public consultation version | 2 | 11 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall provide through AC Interconnectors any possible assistance to a neighbouring TSO in Emergency State, provided it does not endanger its own system. This assistance includes, but is not limited to, a curtailment of Cross Zonal Allocated Capacities in event of force majeure or Emergency Situation, according to Article 69 [NC CACM] and assistance for Active Power, according to Article 18. | Each TSO shall provide through AC Interconnectors any possible assistance to a neighbouring TSO in Emergency State, provided it does not endanger its own system. This assistance includes, but is not limited to, a curtailment of Cross Zonal Allocated Capacities in event of force majeure or an Emergency Situation, according to Article 69 [NC CACM] and assistance for Active Power, according to Article 18. | Why a limitation to only AC interconnectors? Why does this paragraph refer to "force majeure"? If there is an event which can be regarded as a force majeure, this event leads to an emergency situation (otherwise, it is not subject of this network code). It is therefore absolutely sufficient to refer only to emergency situations and close the backdoor for a general statement such as "force majeure". |  |  | Technical
0005-e495-5e7a-d54d-2005 | V1.0 for Public consultation version | 2 | 11 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall provide through AC Interconnectors any possible assistance to a neighbouring TSO in Emergency State, provided it does not endanger its own system. This assistance includes, but is not limited to, a curtailment of Cross Zonal Allocated Capacities in event of force majeure or Emergency Situation, according to Article 69 [NC CACM] and assistance for Active Power, according to Article 18. | Each TSO shall provide through AC Interconnectors any possible assistance to a neighbouring TSO in Emergency State, provided it does not endanger its own system, hereby however duly respecting contracted generation capacity or other resources for adequacy purposes with the neighbouring TSO. This assistance includes, but is not limited to, a curtailment of Cross Zonal Allocated Capacities in event of an Emergency Situation, according to Article 69 [NC CACM] and assistance for Active Power, according to Article 18. | Why does this paragraph refer to "force majeur"? If there is an event which can be regarded as "force majeur", this event leads to an emergency situation (otherwise, it is not subject of this network code). It is therefore absolutely sufficient to refer only to emergency situations and close the backdoor of a general statement such as "force majeur". Energy contracted under a Capacity Remuneration Mechanism (CRM) should be delivered, even if its delivery may move the system hosting the CRM resource into the alert or emergency state. Otherwise CRMs in foreign system are not reliable, and CRM trading is de facto not feasible.
0005-e495-5e7a-d54d-1766 | V1.0 for Public consultation version | 2 | 11 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | …to, a curtailment of Cross Zonal Allocated Capacities in event of …. | …to, a curtailment of Cross Zonal Allocated Capacities in THE event of …. | Typo
0005-bdd5-d4f4-a0a1-5603 | V1.0 for Public consultation version | 2 | 11 | 2 | - | 2014-12-04 14:03:35 | Dekinderen Eric | Genrator company | final | Each TSO shall announce and duly prepare any manual opening of an Interconnector in coordination with neighbouring TSOs, ensuring that this action will not endanger the remaining interconnected system. | Each TSO shall announce and duly prepare any manual opening of an interconnector in coordination with neighbouring TSOs, hereby however duly respecting contracted generation capacity or other ressources for adequacy purposes with the neighbouring TSO and ensuring that this action will not endanger the remaining interconnected system | XB CRM must be granted in emergency conditions. If not, XB CRM will be impossible |  |  | legal |  |  |  | Non-confidential
0005-2181-9ced-2927-1231 | V1.0 for Public consultation version | 2 | 11 | 2 | - | 2014-12-08 16:38:50 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Each TSO shall announce and duly prepare any manual opening of an Interconnector in coordination with neighbouring TSOs, ensuring that this action will not endanger the remaining interconnected system. | Each TSO shall announce and duly prepare any manual opening of an interconnector in coordination with neighbouring TSOs, hereby however duly respecting contracted generation capacity or other ressources for adequacy purposes with the neighbouring TSO and ensuring that this action will not endanger the remaining interconnected system. | Energy contracted under a Capacity Remuneration Mechanism (CRM) should be delivered, even if its delivery may move the system hosting the CRM resource into the alert or emergency state. Otherwise CRMs in foreign system are not reliable, and CRM trading is de facto not feasible. | [6 empty] | Non-confidential
0005-4869-c3c0-0d7d-3b4e | V1.0 for Public consultation version | 2 | 11 | 2 | - | 2014-12-08 17:15:58 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall announce and duly prepare any manual opening of an Interconnector in coordination with neighbouring TSOs, ensuring that this action will not endanger the remaining interconnected system. | Each TSO shall announce and duly prepare any manual opening of an interconnector in coordination with neighbouring TSOs, hereby however duly respecting contracted generation capacity or other ressources for adequacy purposes with the neighbouring TSO and ensuring that this action will not endanger the remaining interconnected system | If this clause remains, CRM across borders is not possible. |  |  | legal |  |  |  | Non-confidential
0005-2145-76f0-910c-6ae4 | V1.0 for Public consultation version | 2 | 11 | 2 | - | 2014-12-05 11:33:49 | Agnieszka Panek |  | final | Each TSO shall announce and duly prepare any manual opening of an Interconnector in coordination with neighbouring TSOs, ensuring that this action will not endanger the remaining interconnected system. | Each TSO shall announce and duly prepare any manual opening of an interconnector in coordination with neighbouring TSOs, hereby however duly respecting contracted generation capacity or other ressources for adequacy purposes with the neighbouring TSO and ensuring that this action will not endanger the remaining interconnected system | If this clause remains, CRM across borders is not possible. |  |  | legal |  |  |  | Non-confidential
0005-96b2-3f2e-e8fe-baa3 | V1.0 for Public consultation version | 2 | 11 | 2 | - | 2014-11-28 15:52:16 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall announce and duly prepare any manual opening of an Interconnector in coordination with neighbouring TSOs, ensuring that this action will not endanger the remaining interconnected system. | Each TSO shall announce and duly prepare any manual opening of an interconnector in coordination with neighbouring TSOs, hereby however duly respecting contracted generation capacity or other ressources for adequacy purposes with the neighbouring TSO and ensuring that this action will not endanger the remaining interconnected system | Energy contracted under a Capacity Remuneration Mechanism (CRM) should be delivered, even if its delivery may move the system hosting the CRM resource into the alert or emergency state. Otherwise CRMs in foreign system are not reliable, and CRM trading is de facto not feasible. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2006 | V1.0 for Public consultation version | 2 | 11 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall announce and duly prepare any manual opening of an Interconnector in coordination with neighbouring TSOs, ensuring that this action will not endanger the remaining interconnected system. | Each TSO shall announce and duly prepare any manual opening of an interconnector in coordination with neighbouring TSOs, hereby however duly respecting contracted generation capacity or other ressources for adequacy purposes with the neighbouring TSO and ensuring that this action will not endanger the remaining interconnected system. | Energy contracted under a Capacity Remuneration Mechanism (CRM) should be delivered, even if its delivery may move the system hosting the CRM resource into the alert or emergency state. Otherwise CRMs in foreign system are not reliable, and CRM trading is de facto not feasible.
0005-6f8d-5060-a3c1-6d7d | V1.0 for Public consultation version | 2 | 11 | 3 | - | 2014-12-04 14:05:09 | Dekinderen Eric | Genrator company | final | A TSO may manually open an Interconnector without prior coordination, in specific conditions including, but not limited to, the violation of threshold endangering personnel safety or damaging equipmen | TSO may manually open an interconnector without prior coordination in conditions where the system is operated in conditions that endanger personnel safety or damaging equipment. | The sentence "but not limited to" is too vague. Opening an interconnector can mean emergency / blackout for the power importing TSO |  |  | legal |  |  |  | Non-confidential
0005-6f66-a4be-e7d2-cb80 | V1.0 for Public consultation version | 2 | 11 | 3 | - | 2014-11-28 15:52:17 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | A TSO may manually open an Interconnector without prior coordination, in specific conditions including, but not limited to, the violation of threshold endangering personnel safety or damaging equipment. | A TSO may manually open an Interconnector without prior coordination in case of the violation of threshold endangering personnel safety or damaging equipment. | Of course, in case of endangering personal safety or damaging equipment, TSO may open an interconnector. Specific conditions must be defined. Otherwise it is always allowed. |  |  | legal |  |  |  | Non-confidential
0005-4891-104d-29ef-b364 | V1.0 for Public consultation version | 2 | 11 | 3 | - | 2014-12-08 16:38:52 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | A TSO may manually open an Interconnector without prior coordination, in specific conditions including, but not limited to, the violation of threshold endangering personnel safety or damaging equipment. | A TSO may manually open an Interconnector without prior coordination in case of the violation of threshold endangering personnel safety or damaging equipment. | Of course, in case of endangering personal safety or damaging equipment, TSO may open an interconnector. Specific conditions must be defined. Otherwise it is always allowed. | [6 empty] | Non-confidential
0005-6fa1-c3de-0f71-cde2 | V1.0 for Public consultation version | 2 | 11 | 3 | - | 2014-12-08 17:15:59 | Paul Doyle | ESB Generation & Wholesale Markets | final | A TSO may manually open an Interconnector without prior coordination, in specific conditions including, but not limited to, the violation of threshold endangering personnel safety or damaging equipment. | A TSO may manually open an Interconnector without prior coordination in case of the violation of threshold endangering personnel safety or damaging equipment. | Specific conditions must be defined. Otherwise it is always allowed. |  |  | legal |  |  |  | Non-confidential
0005-6fb5-9e00-929c-8665 | V1.0 for Public consultation version | 2 | 11 | 3 | - | 2014-12-05 11:33:49 | Agnieszka Panek |  | final | A TSO may manually open an Interconnector without prior coordination, in specific conditions including, but not limited to, the violation of threshold endangering personnel safety or damaging equipment. | A TSO may manually open an Interconnector without prior coordination in case of the violation of threshold endangering personnel safety or damaging equipment. | "Specific conditions" must be defined. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2007 | V1.0 for Public consultation version | 2 | 11 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | A TSO may manually open an Interconnector without prior coordination, in specific conditions including, but not limited to, the violation of threshold endangering personnel safety or damaging equipment. | A TSO may manually open an Interconnector without prior coordination in case of the violation of threshold endangering personnel safety or damaging equipment. | Of course, in case of endangering personal safety or damaging equipment, TSO may open an interconnector. Specific conditions must be defined. Otherwise it is always allowed.
0005-e495-5e7a-d54d-1768 | V1.0 for Public consultation version | 2 | 11 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | A TSO may manually open an Interconnector without prior coordination, in specific conditions including, but not limited to, the violation of threshold endangering personnel safety or damaging equipment. | A TSO may manually open an Interconnector without prior coordination, in specific conditions including, but not limited to, the violation of threshold endangering personnel safety or damaging equipment. | It is unacceptable, in any circumstance, to violate a threshold that endangers the safety of personnel.
0005-bd99-ae02-a105-9a83 | V1.0 for Public consultation version | 2 | 11 | 4 | - | 2014-12-04 14:07:03 | Dekinderen Eric | Genrator company | final | Each TSO shall provide through HVDC Interconnectors any possible assistance, provided it does not endanger its own system, upon request from a neighbouring TSO in Emergency State. | Each TSO shall provide through HVDC interconnectors [….] provided it does not endanger its own system hereby however duly respecting contracted generation capacity or other ressources for adequacy purposes with the neighbouring TSO, upon request from a neighbouring TSO in Emergency State. | XB CRM must be granted in emergency conditions. If not, XB CRM will be impossible |  |  | legal |  |  |  | Non-confidential
0005-4891-8541-285f-2cf5 | V1.0 for Public consultation version | 2 | 11 | 4 | - | 2014-12-08 16:38:54 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Each TSO shall provide through HVDC Interconnectors any possible assistance, provided it does not endanger its own system, upon request from a neighbouring TSO in Emergency State. | Each TSO shall provide through HVDC Interconnectors any possible assistance, provided it does not endanger its own system, hereby however duly respecting contracted generation capacity or other resources for adequacy purposes with the control area of the neighbouring TSO, upon request from a neighbouring TSO in Emergency State. | Energy contracted under a CRMshould be delivered, even if its delivery may move the system hosting the CRM resource into the alert or emergency state. Otherwise CRMs in foreign system are not reliable, and CRM trading is de facto not feasible. | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-2008 | V1.0 for Public consultation version | 2 | 11 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall provide through HVDC Interconnectors any possible assistance, provided it does not endanger its own system, upon request from a neighbouring TSO in Emergency State. | Each TSO shall provide through HVDC Interconnectors any possible assistance, provided it does not endanger its own system, hereby however duly respecting contracted generation capacity or other resources for adequacy purposes with the control area of the neighbouring TSO, upon request from a neighbouring TSO in Emergency State. | Energy contracted under a CRMshould be delivered, even if its delivery may move the system hosting the CRM resource into the alert or emergency state. Otherwise CRMs in foreign system are not reliable, and CRM trading is de facto not feasible.
0005-e495-5e7a-d54d-2161 | V1.0 for Public consultation version | 2 | 11 | 5 |  | 2014-12-08 21:33 | AG | RWE | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | A new article should be added. The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | Technical | Fundamental
0005-e4e5-d512-a03d-7574 | V1.0 for Public consultation version | 2 | 12 | 1 | - | 2014-12-04 14:10:48 | Dekinderen Eric | Genrator company | final | Frequency Deviation management procedure | Unique values for each step in the load shedding process (more data than in table 1) | Unique values for each load shedding step in each synchronous area are mandatory for harmonisation purposes |  |  | legal |  |  |  | Non-confidential
0005-9689-ac5e-d4e9-f31e | V1.0 for Public consultation version | 2 | 12 | 1 | - | 2014-12-08 23:56:23 | Gunnar Kaestle | Clausthal University of Technology | final | a) a decrease of generation shall be smaller than the decrease of Demand during low frequency events; b) a decrease of generation shall be greater than the decrease of Demand during high frequency events; | a) a decrease of generation shall be smaller than the decrease of load during low frequency events; b) a decrease of generation shall be greater than the decrease of load during high frequency events; | According to the Oxford Dictionary, Demand is "The desire of consumers, clients, employers, etc. for a particular commodity, service, or other item." (http://www.oxforddictionaries.com/definition/english/demand). So, demand describes the desire for e.g. electrical energy - if there is no supply, this demand is just a fluffy desire along a macroeconomic price curve. The load is a real technical quantity describing the amount of work which is done by a machine. |  |  | technical |  |  |  | Non-confidential
0005-487e-cbb0-e76e-1790 | V1.0 for Public consultation version | 2 | 12 | 1 | - | 2014-11-28 15:52:18 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The Frequency Deviation management procedure of the System Defence Plan shall contain a set of measures to manage System Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. This measure shall respect at least the following requirements: | The Frequency Deviation management procedure of the System Defence Plan shall contain a set of measures to manage System Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. This set of measures shall respect at least the following requirements: | Editorial. |  |  | legal |  |  |  | Non-confidential
0005-2195-85a9-a240-f71e | V1.0 for Public consultation version | 2 | 12 | 1 | - | 2014-12-07 12:51:41 | Herve MELJAC | EUR | final | The Frequency Deviation management procedure of the System Defence Plan shall contain a set of measures to manage System Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. This measure shall respect at least the following requirements: a) a decrease of generation shall be smaller than the decrease of Demand during low Frequency events; b) a decrease of generation shall be greater than the decrease of Demand during high Frequency events; and c) Interconnectors shall not be overloaded due to asymmetrical response of each LFC Area to low or high Frequency events. | to be defined | The meaning of this article is not clear. It should be reworded. No proposal since the meaning is not clear in the first place. |  |  | legal |  |  |  | Non-confidential
0005-96c5-c3fc-0c51-6e71 | V1.0 for Public consultation version | 2 | 12 | 1 | - | 2014-12-08 17:16:47 | Paul Doyle | ESB Generation & Wholesale Markets | final | The Frequency Deviation management procedure of the System Defence Plan shall contain a set of measures to manage System Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. This measure shall respect at least the following requirements: | The Frequency Deviation management procedure of the System Defence Plan shall contain a set of measures to manage System Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. This set of measures shall respect at least the following requirements: | Editorial. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2294 | V1.0 for Public consultation version | 2 | 12 | 1 | a | 2014-12-08 22:31 | Michael Wilch | RWE | final | a decrease of generation shall be smaller than the decrease of Demand during low Frequency events; | no text proposal. | DSOs ackowledge this is needed, but it could be quite challenging to model and to achieve as it seems to require that the demand reduction effects of say LFDD relays have to be matched with generation decreases. |  |  | Technical
0005-e495-5e7a-d54d-2009 | V1.0 for Public consultation version | 2 | 12 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The Frequency Deviation management procedure of the System Defence Plan shall contain a set of measures to manage System Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. This measure shall respect at least the following requirements: | The Frequency Deviation management procedure of the System Defence Plan shall contain a set of measures to manage System Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. This set of measures shall respect at least the following requirements: | Editorial.
0005-e495-5e7a-d54d-2162 | V1.0 for Public consultation version | 2 | 12 | 1 |  | 2014-12-08 21:33 | AG | RWE | final | The Frequency Deviation management procedure of the System Defence Plan shall contain a set of measures to manage System Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. This measure shall respect at least the following requirements: | The Frequency Deviation management procedure of the System Defence Plan shall contain a set of measures to manage System Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. This set of measures shall respect at least the following requirements: | Editorial. |  |  | Technical | Editorial
0005-6f65-4fb0-3c5c-2b06 | V1.0 for Public consultation version | 2 | 12 | 3 | - | 2014-12-05 10:27:33 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. Costs of the Significant Grid Users related to inbalance settlement shall be borne by the TSO | Costs for Signifcant Grid Users arising from instructed active power setpoints shall be borne by the TSO | 1 | 5 | legal |  |  |  | Non-confidential
0005-216d-7752-a3c1-e099 | V1.0 for Public consultation version | 2 | 12 | 3 | - | 2014-12-04 14:12:19 | Dekinderen Eric | Genrator company | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs | NA | Mandatory only for NEW significant grid users Not all old installations can do this |  |  | legal |  |  |  | Non-confidential
0005-6fb5-4ecb-c79f-567b | V1.0 for Public consultation version | 2 | 12 | 3 | - | 2014-12-08 19:51:14 | Roland Tual | SEDC | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response | [8 empty] | confidential
0005-e4a9-770e-929c-e34e | V1.0 for Public consultation version | 2 | 12 | 3 | - | 2014-12-05 11:33:49 | Agnieszka Panek |  | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users connected to the Transmission System shall execute the instructions given directly by the TSO and Significant Grid Users connected to the Distribution System shall execute the instructions given indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Instructions to the SGUs connected to the Distribution Systems only by the DSO. DSO's point of view regarding information and communication channels (NC OS). |  |  | technical |  |  |  | Non-confidential
0005-9675-d371-4a58-20ff | V1.0 for Public consultation version | 2 | 12 | 3 | - | 2014-12-08 20:11:08 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | The TSO may require that a consumer maintains their consumption level - therefore it is not allowed to turn off its oven, lights, heating system, etc. This requirement is not physically possible and even if it were possible, it would be too costly for households to implement. It could also raise safety issues with regard to devices. This provision is thus unacceptable without any proper structures in place for consumer protection. |  |  | legal |  |  |  | Non-confidential
0005-2196-7d72-ea2a-bd7c | V1.0 for Public consultation version | 2 | 12 | 3 | - | 2014-11-28 15:52:35 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users connected to the Transmission System shall execute the instructions given directly by the TSO and Significant Grid Users connected to the Distribution System shall execute the instructions given indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Instructions to the SGUs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). |  |  | technical |  |  |  | Non-confidential
0005-6fa1-c429-a114-369c | V1.0 for Public consultation version | 2 | 12 | 3 | - | 2014-12-07 12:51:41 | Herve MELJAC | EUR | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical, legal and operating permit constraints. | SGUs ability to execute can be impaired by constraints not limited to technical. |  |  | legal |  |  |  | Non-confidential
0005-6fb5-27bc-0c51-6d7e | V1.0 for Public consultation version | 2 | 12 | 3 | - | 2014-12-08 17:16:50 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users connected to the Transmission System shall execute the instructions given directly by the TSO and Significant Grid Users connected to the Distribution System shall execute the instructions given indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Instructions to the SGUs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2295 | V1.0 for Public consultation version | 2 | 12 | 3 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users connected to the Transmission System shall execute the instructions given directly by the TSO and Significant Grid Users connected to the Distribution System shall execute the instructions given indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Instructions to the SGUs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). See additional comments in art. 9§3. |  |  | Technical
0005-e495-5e7a-d54d-2010 | V1.0 for Public consultation version | 2 | 12 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall, while respecting the technical, legal and operation permit constraints, be entitled to define in cooperation with the SGU an Active Power set-point which the Significant Grid Users shall maintain. The contact for communication, direct from TSO to SGU or via DSO shall be agreed between involved parties. It will be described in the defence and restoration plans. Significant Grid Users shall execute these instructions concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response. | We should prevent different instructions from the DSO (to which the SGU is connected and the TSO. The setpoint should be discussed. If for example a hydro power plant can only deliver full load during a few hours, the TSO should know this and consider whether he needs two hours full load or four hours half load. There are many rivers with hydropower that span over the areas of several DSO´s. We can´t have multiple demands from many DSO´s for power plants in a cascade as the plants have to be often run as one (if there is no reservoir in between). The communication between SGUs abd DSO/TSO should be defined in the defence and restoration plans.
0005-e495-5e7a-d54d-2163 | V1.0 for Public consultation version | 2 | 12 | 3 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO shall be entitled to define an Active Power Set-point which the significant Grid User shall maintain. | Each TSO shall be entitled to define, subject to NRA approval and in cooperation with the Significant Grid User, an Active Power set-point which the Significant Grid Users shall maintain. | There must be NRA approval of the set point (and any changes to the set point). As a general comment (and as already stated), the Code lacks the NRA approvals which all TSO decisions shall be subject to. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2256 | V1.0 for Public consultation version | 2 | 12 | 3 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response |  | The TSO may require that a consumer maintains their consumption level - therefore they are not allowed to turn off their stove, lights, heating. This stipulation is not physically possible and even if it were possible, it is costly for the majority of businesses and households. It could also be dangerous. (If small consumers/generators are not under consideration for this measure - why are they included?)
0005-e495-5e7a-d54d-1770 | V1.0 for Public consultation version | 2 | 12 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. | Each TSO shall be entitled to define SUBJECT TO NRA APPROVAL, an Active Power set-point which the Significant Grid Users shall maintain. | There must be NRA approval of the set point (and any changes to that set point).
0005-e495-5e7a-d54d-1772 | V1.0 for Public consultation version | 2 | 12 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints IN ACCORDANCE WITH THE SERVICE PROCURED BY THE RELEVANT NETWORK OPERATOR. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-216d-c3fc-0e45-c99e | V1.0 for Public consultation version | 2 | 12 | 4 | - | 2014-12-08 17:16:50 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users connected to the Transmission System directly and Significant Grid Users connected to the Distribution System indirectly through the DSOs and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], indirectly through DSOs. | Instructions to the SGUs connected to the Distribution Systems and new type A PGMs only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Concerning feasibility for type A PGMs, see remark art. 8.4. |  |  | technical |  |  |  | Non-confidential
0005-6fa1-1010-0bed-3d02 | V1.0 for Public consultation version | 2 | 12 | 4 | - | 2014-12-08 17:16:51 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall provide through HVDC Interconnectors any possible assistance, provided it does not endanger its own system, upon request from a neighbouring TSO in Emergency State. | Each TSO shall provide through HVDC interconnectors [….] provided it does not endanger its own system hereby however duly respecting contracted generation capacity or other ressources for adequacy purposes with the neighbouring TSO, upon request from a neighbouring TSO in Emergency State. | If this clause remains, CRM across borders is not possible. |  |  | legal |  |  |  | Non-confidential
0005-487d-5f9e-9238-c1ad | V1.0 for Public consultation version | 2 | 12 | 4 | - | 2014-12-05 11:33:49 | Agnieszka Panek |  | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users connected to the Transmission System directly and Significant Grid Users connected to the Distribution System indirectly through the DSOs and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], indirectly through DSOs. | Instructions to the SGUs connected to the Distribution Systems and new type A PGMs only by the DSO. DSO's point of view regarding information and communication channels (NC OS). Concerning feasibility for type A PGMs, see remark art. 8.4. |  |  | technical |  |  |  | Non-confidential
0005-9675-d4f5-26b7-d879 | V1.0 for Public consultation version | 2 | 12 | 4 | - | 2014-12-08 17:01:16 | Jasmina PIERRE | EdF | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. This disconnection should not compromise others critical considerations, such as safety conditions of high priority significant grid users. | EDF underlines such a disconnection can compromise safety conditions from grids users installations (including nuclear plants). ENTSO-E proposal implies that grid security prevails over any others critical considerations, including nuclear safety, which is not acceptable. It is essential that TSO takes into account the specific needs of specific grid users regarding the conditions for their disconnection and re-energizing. |  |  | technical |  |  |  | Non-confidential
0005-4856-087e-e76e-efe9 | V1.0 for Public consultation version | 2 | 12 | 4 | - | 2014-11-28 15:52:36 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users connected to the Transmission System directly and Significant Grid Users connected to the Distribution System indirectly through the DSOs and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], indirectly through DSOs. | Instructions to the SGUs connected to the Distribution Systems and new type A PGMs only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Concerning feasibility for type A PGMs, see remark art. 8.4. |  |  | technical |  |  |  | Non-confidential
0005-48a6-087e-e8fe-8390 | V1.0 for Public consultation version | 2 | 12 | 4 | - | 2014-11-28 15:52:37 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall provide through HVDC Interconnectors any possible assistance, provided it does not endanger its own system, upon request from a neighbouring TSO in Emergency State. | Each TSO shall provide through HVDC interconnectors [….] provided it does not endanger its own system hereby however duly respecting contracted generation capacity or other ressources for adequacy purposes with the neighbouring TSO, upon request from a neighbouring TSO in Emergency State. | If this clause remains, CRM across borders is not possible. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2296 | V1.0 for Public consultation version | 2 | 12 | 4 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users connected to the Transmission System directly and Significant Grid Users connected to the Distribution System indirectly through the DSOs and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Instructions to the SGUs connected to the Distribution Systems and new type A PGMs only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). DSOs are convinced that new type A PGMs should not be part of the NC ER, cf. explanation art. 8§4. |  |  | Technical
0005-e495-5e7a-d54d-2011 | V1.0 for Public consultation version | 2 | 12 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users connected to the Transmission System directly and Significant Grid Users connected to the Distribution System indirectly through the DSOs and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], indirectly through DSOs. | Instructions to the SGUs connected to the Distribution Systems and new type A PGMs only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Concerning feasibility for type A PGMs, see remark art. 8.4.
0005-e495-5e7a-d54d-2012 | V1.0 for Public consultation version | 2 | 12 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall provide through HVDC Interconnectors any possible assistance, provided it does not endanger its own system, upon request from a neighbouring TSO in Emergency State. | Each TSO shall provide through HVDC interconnectors [….] provided it does not endanger its own system hereby however duly respecting contracted generation capacity or other ressources for adequacy purposes with the neighbouring TSO, upon request from a neighbouring TSO in Emergency State. | If this clause remains, CRM across borders is not possible.
0005-e495-5e7a-d54d-2164 | V1.0 for Public consultation version | 2 | 12 | 4 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | See the justification. | How this will be done in practice? Also, where is the 'reverse' instruction to re-connect? This procedure should be set out in the NC ER as well.
0005-e495-5e7a-d54d-1774 | V1.0 for Public consultation version | 2 | 12 | 4 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Xyz | Has the practicality of issuing instructions to new Type A generators been assessed. Also where is the ‘reverse’ instruction? Having been instructed to ‘disconnect’ where is the procedure set out in the E&R NC to instruct those parties disconnected to re-connect?
0005-96c5-d48d-d1f4-1ab9 | V1.0 for Public consultation version | 2 | 12 | 5 | - | 2014-12-05 17:01:43 | Til Kristian Vrana |  | final | Low Frequency Demand Disconnection | Under-Frequency Load Disconnection | Low frequency is not correct. The phenomenon is under-frequency, relating to a frequency being lower than it is supposed to be. Low frequency only relates to a low frequency (e.g. 16,7Hz) |  |  | technical |  |  |  | Non-confidential
0005-e4e5-516b-6ff0-6aae | V1.0 for Public consultation version | 2 | 12 | 5 | - | 2014-12-04 09:23:07 | Steve Wilkin | ELEXON Limited | final | In case of under-frequency deviation, each TSO shall activate Demand Side Response before activation of the automatic Low Frequency Demand Disconnection scheme described in Article 13, provided the rate of change of Frequency allows the TSO to do so. | See comment. | There are market-related impacts to this requirement that should at least be considered. If there is defined a Value of Lost Load for the affected area, and the price of Demand Side Response is a more expensive action than the Value of Lost Load, then it can be argued that the cheaper automatic disconnection should take place before the higher priced Demand Side Response, for example. Has this been considered and rejected? |  |  | technical |  |  |  | Non-confidential
0005-e495-ac8b-cabf-a8f9 | V1.0 for Public consultation version | 2 | 12 | 5 | - | 2014-12-08 19:51:14 | Roland Tual | SEDC | final | In case of under-frequency deviation, each TSO shall activate Demand Side Response before activation of the automatic Low Frequency Demand Disconnection scheme described in Article 13, provided the rate of change of Frequency allows the TSO to do so. | [8 empty] | confidential
0005-6fa1-103c-d4e9-8c1a | V1.0 for Public consultation version | 2 | 12 | 5 | - | 2014-12-08 23:56:23 | Gunnar Kaestle | Clausthal University of Technology | final | Low Frequency Demand Disconnection scheme | Under-Frequency Load Shedding scheme | LFDD may be a new and fresh word, but the old fashioned UFLS is still the more precise term. Demand is nothing which can be disconnected, as demand is a desire for consumption. Low Frequency is a whole range of frequencies, e.g. as defined by the ITU 30 kHz -300 kHz. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2257 | V1.0 for Public consultation version | 2 | 12 | 5 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | In case of under-frequency deviation, each TSO shall activate Demand Side Response before activation of the automatic Low Frequency Demand Disconnection scheme described in Article 13, provided the rate of change of Frequency allows the TSO to do so. |  | It is obvious that a TSO will active DSR prior to an emergency scheme - why is this sentence included? Does this mean the TSO can decide not to pay the consumer for their services?
0005-e495-5e7a-d54d-2365 | V1.0 for Public consultation version | 2 | 12 | 5 |  | 2014-12-09 09:29 | Dr. Til Kristian Vrana | Sintef | final | Low Frequency Demand Disconnection | Under-Frequency Load Disconnection | Low frequency is not correct. The phenomenon is under-frequency, relating to a frequency being lower than it is supposed to be. Low frequency only relates to a low frequency (e.g. 16,7Hz)
0005-e495-5e7a-d54d-2013 | V1.0 for Public consultation version | 2 | 12 | 6 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | A new article should be added. The costs must be addressed to make sure that over all optimal economic sollutions will be used.
0005-9689-c3fc-0c51-e52b | V1.0 for Public consultation version | 2 | 12 | - | - | 2014-12-08 17:16:52 | Paul Doyle | ESB Generation & Wholesale Markets | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | legal |  |  |  | Non-confidential
0005-969e-5680-e962-97ef | V1.0 for Public consultation version | 2 | 12 | - | - | 2014-11-28 15:52:38 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | legal |  |  |  | Non-confidential
0005-6f8d-ac7f-4b1f-4979 | V1.0 for Public consultation version | 2 | 12 | - | - | 2014-12-08 20:11:10 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | Duplication of communication channels: Significants grid users will receive orders directly from TSOs or indirectly through DSOs. This would imply duplication of communication channels for consumers whose installation costs would be prohibitive. Such requirement is not acceptable for residential consumers. |  |  | legal |  |  |  | Non-confidential
0005-6fb5-4eae-0cb5-f34c | V1.0 for Public consultation version | 2 | 13 | 1 | - | 2014-12-08 17:16:54 | Paul Doyle | ESB Generation & Wholesale Markets | final | The automatic low Frequency control scheme shall include an automatic Low Frequency Demand Disconnection scheme and the settings of Limited Frequency Sensitive Mode in the TSO LFC Area. | The automatic low Frequency control scheme shall include an automatic Low Frequency Demand Disconnection scheme and the settings of Limited Frequency Sensitive Mode in the TSO LFC Area. The scheme shall be approved by the NRA and be made available for parties identified in accordance with Article 8.4 | The scheme shall be available for involved parties and be approved by the NRA to prevent discrimination. |  |  | legal |  |  |  | Non-confidential
0005-bdd5-11c3-26b7-813c | V1.0 for Public consultation version | 2 | 13 | 1 | - | 2014-12-08 17:01:17 | Jasmina PIERRE | EdF | final | The automatic Low Frequency Demand Disconnection scheme of the System Defence Plan shall have the following parameters: a) Frequency range in which Low Frequency Demand Disconnection is possible (low Frequency allowed range); […] j) Frequency range in which demand disconnection based on Frequency gradient is possible (gradient Frequency allowed range). The parameters shall be in line with the following values for each Synchronous Area: [figures under review]. (empty table 1) | The automatic Low Frequency Demand Disconnection scheme of the System Defence Plan shall have the following parameters: a) Frequency range in which Low Frequency Demand Disconnection is possible (low Frequency allowed range); […] j) Frequency range in which demand disconnection based on Frequency gradient is possible (gradient Frequency allowed range). The parameters shall be in line with the following values for each Synchronous Area: [figures under review]. (empty table 1) | This engagement of mutual assistance throughout Europe should come along with a high level transparency regarding minimal performances for defense and restoration to be targeted within each control area. it is essential for TSOs to submit to public consultation the proposed values for the parameters to be defined in this code. In this perspective, EDF stresses the importance of opening to future additional consultation the values still under review (e.g. Table 1: automatic low frequency demand disconnection scheme parameters) in the current draft. |  |  | technical |  |  |  | Non-confidential
0005-487d-86f3-258b-7c5f | V1.0 for Public consultation version | 2 | 13 | 1 | - | 2014-12-08 17:01:17 | Jasmina PIERRE | EdF | final | The automatic low Frequency control scheme shall include an automatic Low Frequency Demand Disconnection scheme and the settings of Limited Frequency Sensitive Mode in the TSO LFC Area. | The automatic low Frequency control scheme shall include an automatic Low Frequency Demand Disconnection scheme and the settings of Limited Frequency Sensitive Mode in the TSO LFC Area. The scheme shall be approved by the NRA and be made available for parties identified in accordance with Article 8.4 | The engagement of mutual assistance throughout Europe should come along with a high level transparency regarding minimal performances for defense and restoration to be targeted within each control area. The scheme shall be available for involved parties and be approved by the NRA to prevent discrimination. |  |  | technical |  |  |  | Non-confidential
0005-e4e6-663e-e9c6-b2af | V1.0 for Public consultation version | 2 | 13 | 1 | - | 2014-11-28 15:52:38 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The automatic low Frequency control scheme shall include an automatic Low Frequency Demand Disconnection scheme and the settings of Limited Frequency Sensitive Mode in the TSO LFC Area. | The automatic low Frequency control scheme shall include an automatic Low Frequency Demand Disconnection scheme and the settings of Limited Frequency Sensitive Mode in the TSO LFC Area. The scheme shall be approved by the NRA and be made available for parties identified in accordance with Article 8.4 | The scheme shall be available for involved parties and be approved by the NRA to prevent discrimination. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2014 | V1.0 for Public consultation version | 2 | 13 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The automatic low Frequency control scheme shall include an automatic Low Frequency Demand Disconnection scheme and the settings of Limited Frequency Sensitive Mode in the TSO LFC Area. | The automatic low Frequency control scheme shall include an automatic Low Frequency Demand Disconnection scheme and the settings of Limited Frequency Sensitive Mode in the TSO LFC Area. The scheme shall be approved by the NRA and be made available for parties identified in accordance with Article 8.4 | The scheme shall be available for involved parties and be approved by the NRA to prevent discrimination.
0005-e495-5e7a-d54d-2015 | V1.0 for Public consultation version | 2 | 13 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | 1. The automatic low Frequency control scheme shall include an automatic Low Frequency Demand Disconnection scheme and the settings of Limited Frequency Sensitive Mode in the TSO LFC Area. |  | a)The concept of Limited Frequency Sensitive Mode is not defined. If it has the same definition as in the RfG NC, this should be added (according to the criteria defined in [NC RfG]), and if not, it should be defined. b) It is not clear whether the setting of this Mode is done in this NC or in the RfG NC, this should be clarified.
0005-e495-5e7a-d54d-2298 | V1.0 for Public consultation version | 2 | 13 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall activate Limited Frequency Sensitive Mode before activation of the automatic Low Frequency Demand Disconnection scheme, provided the rate of change of Frequency allows the TSO to do so. | no text proposal. | Does this imply that Limited Frequency Sensitive Mode is something that can be manually switched on/off? |  |  | Technical
0005-e495-5e7a-d54d-2016 | V1.0 for Public consultation version | 2 | 13 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | 2. Each TSO shall activate Limited Frequency Sensitive Mode before activation of the automatic Low Frequency Demand Disconnection scheme, provided the rate of change of Frequency allows the TSO to do so. | 2. Each TSO shall make sure that Limited Frequency Sensitive Mode will be activated before activation of the automatic Low Frequency Demand Disconnection scheme, provided the rate of change of Frequency allows the TSO to do so. | Paragraph 2 establises that each TSO shall activate Limited Frequency Sensitive Mode before activation of the automatic Low Frequency Demand Disconnection scheme. As both of them are automatic, clarification on this is needed.
0005-e4d1-85a9-a36c-3c8d | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-07 12:52:10 | Herve MELJAC | EUR | final | Table 1 empty | Table 1 shall be filled in. | - |  |  | legal |  |  |  | Non-confidential
0005-6fa1-9de2-93c8-c3b6 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-05 11:33:49 | Agnieszka Panek |  | final | Table 1 - figures missing. | ?? | It is very important for the market participants how the table will be filled. This table should be the object of separate public consultation |  |  | technical |  |  |  | Non-confidential
0005-2159-866e-e4ea-6c07 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-08 16:39:17 | Markus Hemmer | EnBW | final | The automatic Low Frequency Demand Disconnection scheme of the System Defence Plan shall have the following parameters: | The automatic Low Frequency Demand Disconnection scheme of the System Defence Plan shall have the following parameters respecting all related NCs (NC RfG, NC DC, NC HVDC): | This shall avoid an undermining of the provisions of this NCs. | [6 empty] | Non-confidential
0005-bd99-372e-d3bd-4948 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-08 23:56:24 | Gunnar Kaestle | Clausthal University of Technology | final | Frequency range in which Energy Storage shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | remove paragraph h) | As there are distributed generators which disconnect at under-frequency due to historical reasons (old grid codes), we should not wait several seconds until energy storages (usually large pumped hydro) are shedded. It is a common knowledge that any delay in control loops causes adverse effects (you react on a system state which was measured quite a long time ago). The only practical benefit is that the nadir (frequency minimum most often only after ~10s) may not cause a trip in pumping hydro plants. Nevertheless the system performance will be influence in future by other energy storages such as electric vehicles, which may perform an under-frequency droop (http://link.springer.com/article/10.1007/s00202-011-0210-x) so that no nadir will occur. The risk, that the under-frequency threshold of certain DERs will be met because of a delayed reaction of non critical loads such as pumped hydros, is nevertheless visible (The Impact of Dispersed Generation on Continental Europe’s Security of Supply, https://www.entsoe.eu/publications/system-operations-reports/continental-europe/the-impact-of-dispersed-generation-impact-on-continental-europe-region-security/Pages/default.aspx) |  |  | technical |  |  |  | Non-confidential
0005-2159-d39c-0d7d-5032 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-08 17:16:56 | Paul Doyle | ESB Generation & Wholesale Markets | final | maximum inaccuracy of Frequency measurements on Low Frequency Demand Disconnection relays (maximum inaccuracy); | maximum inaccuracy of the complete (sensor, transmission, calculation, analysis, protection relay) Frequency measurements on Low Frequency Demand Disconnection relays (maximum inaccuracy); | It is completely unclear if the whole measurement (sensor, transmission, calculation, analysis, protection function) is meant or only a subpart of the system. It is also unclear how the inaccuracy is to be determined. Please specify exactly what is meant or delete the value. |  |  | technical |  |  |  | Non-confidential
0005-6fb5-50c6-10df-3070 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-03 11:17:31 | AXPO Group |  | final | Table 1: Maximum delay, Ms | see Comment | Subpoint f) Regarding maximum delay MD the measuring unit "Ms" is unclear. Is it Mega-seconds or Minutes? Obviously it has the be milli-seconds and the standard abbreviation is ms. |  |  | technical |  |  |  | Non-confidential
0005-9689-5e30-0f71-eb42 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-08 17:16:58 | Paul Doyle | ESB Generation & Wholesale Markets | final | Frequency range in which Energy Storage shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | Frequency range in which Energy Storage (in demand mode) shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | Only in demand mode never in generation mode |  |  | technical |  |  |  | Non-confidential
0005-48a5-0241-2527-74bd | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-08 17:01:18 | Jasmina PIERRE | EdF | final | Frequency range in which Energy Storage shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | Frequency range in which Energy Storage (withdrawal mode) shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | It should be clear that this disposal do not apply when Storage facilities is injected energy (generation mode). |  |  | technical |  |  |  | Non-confidential
0005-96c5-00ac-0bed-6800 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-08 17:16:59 | Paul Doyle | ESB Generation & Wholesale Markets | final | The automatic Low Frequency Demand Disconnection scheme of the System Defence Plan shall have the following parameters: | The automatic Low Frequency Demand Disconnection scheme of the System Defence Plan shall have the following parameters respecting all related NCs (NC RfG, NC DC, NC HVDC): | This shall avoid an undermining of the provisions of other Network Codes. |  |  | legal |  |  |  | Non-confidential
0005-bdc1-008d-2f68-aae7 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-08 18:18:37 | Thomas Willson |  | final | Frequency range in which Energy Storage shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | remove paragraph h) | As there are distributed generators which disconnect at under-frequency due to historical reasons (old grid codes), we should not wait several seconds until energy storages (usually large pumped hydro) are shedded. It is a common wisdom that any delay in control loops causes adverse effects (you react on a system state which was measured quite a long time ago). The only practical benefit is that the nadir (most often only after ~10s) may not cause a trip in pumping hydro plants. Nevertheless the system performance will be influence in future by other energy storages such as electric vehicles, which may perform an under-frequency droop (http://link.springer.com/article/10.1007/s00202-011-0210-x) so that no nadir will occur. The risk, that the under-frequency threshold of certain DERs will be met because of a delayed reaction of non critical loads such as pumped hydros, is nevertheless visible (The Impact of Dispersed Generation on Continental Europe’s Security of Supply, https://www.entsoe.eu/publications/system-operations-reports/continental-europe/the-impact-of-dispersed-generation-impact-on-continental-europe-region-security/Pages/default.aspx) |  |  | technical |  |  |  | Non-confidential
0005-bdc2-7d90-e70a-f663 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-11-28 15:52:39 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | maximum inaccuracy of Frequency measurements on Low Frequency Demand Disconnection relays (maximum inaccuracy); | maximum inaccuracy of the complete (sensor, transmission, calculation, analysis, protection relay) Frequency measurements on Low Frequency Demand Disconnection relays (maximum inaccuracy); | It is completely unclear if the whole measurement (sensor, transmission, calculation, analysis, protection function) is meant or only a subpart of the system. It is also unclear how the inaccuracy is to be determined. Please specify exactly what is meant or delete the value. |  |  | technical |  |  |  | Non-confidential
0005-e4d1-4eae-0e45-432d | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-08 17:17:01 | Paul Doyle | ESB Generation & Wholesale Markets | final | Table 1 - figures missing. | - | The document states that the figures are under review. The figures should obviously respond to security requirements of the European power systems, but should also be coherent with existing capabilities of equipment and should therefore be justified through a cost benefit analysis. The figures that will be considered should avoid costly retrofits of existing low frequency demand disconnection schemes implemented by DSOs in several European countries. Notwithstanding the economic justification, the considered accuracy on frequency measurement and the overall performance of the proposed scheme should not be a technical burden to reach. The Working Group 3 of the TC8X of CENELEC (TC8X-WG3) has recently produced technical specifications (EN 50549-1 & EN 5049-2) and a standard (EN 50438) on requirements for generators connected to the distribution system. Amongst others, these technical specifications and standards specify the requirement proposed by ENTSOE in the NC RfG to reduce active power generated in case of high frequency. While completing this work, it appeared that no suitable standard is currently available for frequency measurement on electrical networks. The IEC 61000-4-30 standard is considered insufficient with regard to the measurement of frequency during dynamic behaviour of power systems. Therefore TC8X-WG3 is willing to launch the drafting of such a standard. If approved by CENELEC the drafting work for a standard on frequency measurement on electrical networks will probably require the collaboration of various technical Committees of CENELEC as well as, possibly, TSOs, DSOs and manufacturer experts. Without such approach, it seems therefore difficult to define the expected technical performances of LFDD in the NC ER. ENTSO-E mentioned that they are launching a study to confirm the parameters of the LFDD scheme. DSOs would be interested in being informed on the assumptions/conclusions of such study. |  |  | technical |  |  |  | Non-confidential
0005-e4e6-b45e-e962-2b7e | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-11-28 15:52:40 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Frequency range in which Energy Storage shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | Frequency range in which Energy Storage (in demand mode) shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | Only in demand mode never in generation mode |  |  | technical |  |  |  | Non-confidential
0005-4891-ac50-0ea9-e886 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-08 17:17:03 | Paul Doyle | ESB Generation & Wholesale Markets | final |  | Add realistic Figures, not leading to extreme costs for DSOs or Grid Users unless based on a CBA. Change the unit for Maximum Delay in ms (milliseconds) instead of Mega seconds, change the unit for Frequency gradient in Hz/s. | Figures in Table 1 are not available; Two faults in measuring units should be corrected. This is NOT ACCEPTABLE FOR PUBLIC CONSULTATION of a European regulation made by one stake holder (ENTSO-E)!! |  |  | legal |  |  |  | Non-confidential
0005-96c6-b45e-e8fe-c189 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-11-28 15:52:41 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The automatic Low Frequency Demand Disconnection scheme of the System Defence Plan shall have the following parameters: | The automatic Low Frequency Demand Disconnection scheme of the System Defence Plan shall have the following parameters respecting all related NCs (NC RfG, NC DC, NC HVDC): | This shall avoid an undermining of the provisions of other Network Codes. |  |  | legal |  |  |  | Non-confidential
0005-6f8e-569e-e70a-feb4 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-11-28 15:52:42 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Table 1 - figures missing. | - | The document states that the figures are under review. The figures should obviously respond to security requirements of the European power systems, but should also be coherent with existing capabilities of equipment and should therefore be justified through a cost benefit analysis. The figures that will be considered should avoid costly retrofits of existing low frequency demand disconnection schemes implemented by DSOs in several European countries. Notwithstanding the economic justification, the considered accuracy on frequency measurement and the overall performance of the proposed scheme should not be a technical burden to reach. The Working Group 3 of the TC8X of CENELEC (TC8X-WG3) has recently produced technical specifications (EN 50549-1 & EN 5049-2) and a standard (EN 50438) on requirements for generators connected to the distribution system. Amongst others, these technical specifications and standards specify the requirement proposed by ENTSOE in the NC RfG to reduce active power generated in case of high frequency. While completing this work, it appeared that no suitable standard is currently available for frequency measurement on electrical networks. The IEC 61000-4-30 standard is considered insufficient with regard to the measurement of frequency during dynamic behaviour of power systems. Therefore TC8X-WG3 is willing to launch the drafting of such a standard. If approved by CENELEC the drafting work for a standard on frequency measurement on electrical networks will probably require the collaboration of various technical Committees of CENELEC as well as, possibly, TSOs, DSOs and manufacturer experts. Without such approach, it seems therefore difficult to define the expected technical performances of LFDD in the NC ER. ENTSO-E mentioned that they are launching a study to confirm the parameters of the LFDD scheme. DSOs would be interested in being informed on the assumptions/conclusions of such study. |  |  | technical |  |  |  | Non-confidential
0005-48a6-3ef2-e8fe-a4cb | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-11-28 15:53:00 | VGB PowerTech e.V. | VGB PowerTech e.V. | final |  | Add realistic Figures, not leading to extreme costs for DSOs or Grid Users unless based on a CBA. Change the unit for Maximum Delay in ms (milliseconds) instead of Mega seconds, change the unit for Frequency gradient in Hz/s. | Figures in Table 1 are not available; Two faults in measuring units should be corrected. This is NOT ACCEPTABLE FOR PUBLIC CONSULTATION of a European regulation made by one stake holder (ENTSO-E)!! |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2299 | V1.0 for Public consultation version | 2 | 13 | 3 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Table 1 - figures missing. | - | The document states that the figures are under review. The figures should obviously respond to security requirements of the European power systems, but should also be coherent with existing capabilities of equipment and should therefore be justified through a CBA. The figures that will be considered should avoid costly retrofits of existing low frequency demand disconnection schemes implemented by DSOs in several European countries. Notwithstanding the economic justification, the considered accuracy on frequency measurement and the overall performance of the proposed scheme should not be a technical burden to reach. The Working Group 3 of the TC8X of CENELEC (TC8X-WG3) has recently produced technical specifications (EN 50549-1 & EN 5049-2) and a standard (EN 50438) on requirements for generators connected to the distribution system. Amongst others, these technical specifications and standard specify the requirement proposed by ENTSOE in the NC RfG to reduce active power generated in case of high frequency. While completing this work, it appeared that no suitable standard is currently available for frequency measurement on electrical networks. The IEC 61000-4-30 standard is considered insufficient with regard to the measurement of frequency during dynamic behaviour of power systems. Therefore TC8X-WG3 is willing to launch the drafting of such a standard. If approved by CENELEC the drafting work for a standard on frequency measurement on electrical networks will probably require the collaboration of various technical Committees of CENELEC as well as, possibly, TSOs, DSOs and manufacturer experts. Without such approach, it seems therefore difficult to define the expected technical performances of LFDD in the NC ER. ENTSO-E mentioned that they are launching a study to confirm the parameters of the LFDD scheme. DSOs would be interested in being informed on the assumptions/conclusions of such study. |  |  | Technical
0005-e495-5e7a-d54d-2017 | V1.0 for Public consultation version | 2 | 13 | 3 | g | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | maximum inaccuracy of Frequency measurements on Low Frequency Demand Disconnection relays (maximum inaccuracy); | maximum inaccuracy of the complete (sensor, transmission, calculation, analysis, protection relay) Frequency measurements on Low Frequency Demand Disconnection relays (maximum inaccuracy); | It is completely unclear if the whole measurement (sensor, transmission, calculation, analysis, protection function) is meant or only a subpart of the system. It is also unclear how the inaccuracy is to be determined. Please specify exactly what is meant or delete the value.
0005-e495-5e7a-d54d-2300 | V1.0 for Public consultation version | 2 | 13 | 3 | g | 2014-12-08 22:31 | Michael Wilch | RWE | final | maximum inaccuracy of Frequency measurements on Low Frequency Demand Disconnection relays (maximum inaccuracy); | maximum inaccuracy of Frequency measurements on Low Frequency Demand Disconnection relays (maximum inaccuracy); | It is completely unclear if the whole measurement (sensor, transmission, calculation, analysis, protection function) is meant or only a subpart of the system. It is also unclear how the inaccuracy is to be determined. Please specify exactly what is meant or delete the value. |  |  | Technical
0005-bdd5-2914-a1cd-ab77 | V1.0 for Public consultation version | 2 | 13 | 3 | h | 2014-12-04 14:13:05 | Dekinderen Eric | Genrator company | final | Frequency range in which Energy Storage shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | Frequency range in which Energy Storage shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | Only in demand mode. Never in generation mode |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2018 | V1.0 for Public consultation version | 2 | 13 | 3 | h | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Frequency range in which Energy Storage shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | Frequency range in which Energy Storage (in demand mode) shall be automatically disconnected with a time delay (Energy Storage delay Frequency range); | Only in demand mode never in generation mode
0005-969d-5024-a169-fc40 | V1.0 for Public consultation version | 2 | 13 | 3 | i | 2014-12-04 14:14:09 | Dekinderen Eric | Genrator company | final | Frequency range in which Energy Storage shall be automatically disconnected without a time delay (Energy Storage Frequency range); and | Frequency range in which Energy Storage (in consuming mode) shall be automatically disconnected without a time delay (Energy Storage Frequency range); and | Only in demand mode. Never in generation mode |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2301 | V1.0 for Public consultation version | 2 | 13 | 3 | j | 2014-12-08 22:31 | Michael Wilch | RWE | final | Frequency range in which demand disconnection based on Frequency gradient is possible (gradient Frequency allowed range). | no text proposal. | Definition or explanation of Frequency gradient? |  |  | Technical
0005-e495-5e7a-d54d-2019 | V1.0 for Public consultation version | 2 | 13 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The automatic Low Frequency Demand Disconnection scheme of the System Defence Plan shall have the following parameters: | The automatic Low Frequency Demand Disconnection scheme of the System Defence Plan shall have the following parameters respecting all related NCs (NC RfG, NC DC, NC HVDC): | This shall avoid an undermining of the provisions of other Network Codes.
0005-e495-5e7a-d54d-2020 | V1.0 for Public consultation version | 2 | 13 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Table 1 - figures missing. | - | The document states that the figures are under review. The figures should obviously respond to security requirements of the European power systems, but should also be coherent with existing capabilities of equipment and should therefore be justified through a cost benefit analysis. The figures that will be considered should avoid costly retrofits of existing low frequency demand disconnection schemes implemented by DSOs in several European countries. Notwithstanding the economic justification, the considered accuracy on frequency measurement and the overall performance of the proposed scheme should not be a technical burden to reach. The Working Group 3 of the TC8X of CENELEC (TC8X-WG3) has recently produced technical specifications (EN 50549-1 & EN 5049-2) and a standard (EN 50438) on requirements for generators connected to the distribution system. Amongst others, these technical specifications and standards specify the requirement proposed by ENTSOE in the NC RfG to reduce active power generated in case of high frequency. While completing this work, it appeared that no suitable standard is currently available for frequency measurement on electrical networks. The IEC 61000-4-30 standard is considered insufficient with regard to the measurement of frequency during dynamic behaviour of power systems. Therefore TC8X-WG3 is willing to launch the drafting of such a standard. If approved by CENELEC the drafting work for a standard on frequency measurement on electrical networks will probably require the collaboration of various technical Committees of CENELEC as well as, possibly, TSOs, DSOs and manufacturer experts. Without such approach, it seems therefore difficult to define the expected technical performances of LFDD in the NC ER. ENTSO-E mentioned that they are launching a study to confirm the parameters of the LFDD scheme. DSOs would be interested in being informed on the assumptions/conclusions of such study.
0005-e495-5e7a-d54d-2021 | V1.0 for Public consultation version | 2 | 13 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final |  | Add realistic Figures, not leading to extreme costs for DSOs or Grid Users unless based on a CBA. Change the unit for Maximum Delay in ms (milliseconds) instead of Mega seconds, change the unit for Frequency gradient in Hz/s. | Figures in Table 1 are not available; Two faults in measuring units should be corrected. All relevant information should be included in the document. This is a formal public consultation on the code and a consultation can be organised in an appropriate manner only when all information is available for stakeholders.
0005-e495-5e7a-d54d-2165 | V1.0 for Public consultation version | 2 | 13 | 3 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Table 1 - figures missing. | See the justification. | We understand (following the statement made at the ENTSO-E Stakeholder Workshop of 12 November and the information published on the ENTSO-E website) that this table (together with Chapter 4) will be subject to a separate and specific consultation form mid-December to mid-January.
0005-2182-181e-e70a-d3e4 | V1.0 for Public consultation version | 2 | 13 | 4 | - | 2014-11-28 15:51:09 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The DSO shall, when implementing the automatic Low Frequency Demand Disconnection scheme, pursuant to the notification under Article 9(2): | The DSO shall, with the required automatic Low Frequency Demand Disconnection scheme, pursuant to the notification under Article 9(2): | Not only when (read as in case of) implementing, he shall anyway do it! |  |  | legal |  |  |  | Non-confidential
0005-4855-103c-d4e9-b13d | V1.0 for Public consultation version | 2 | 13 | 4 | - | 2014-12-08 23:56:24 | Gunnar Kaestle | Clausthal University of Technology | final | a) … b) … | a) … b) … c) ensure that this scheme does lead to a overall load reduction similar to the characteristic curve of a droop (group droop of UF relais) | In Article 14 a droop is mentioned for the over-frequency situation. The under-frequency load shedding should be done in such a way that a shape of roughly a droop with a default value of X % is shown (so called group droop of switched elements). |  |  | technical |  |  |  | Non-confidential
0005-2159-ac8d-7eb6-4145 | V1.0 for Public consultation version | 2 | 13 | 4 | - | 2014-12-08 16:38:49 | Rothermann Philippe |  | final | a) ensure to minimise the total disconnected installed capacity of Power Generating Modules connected directly to its distribution system; and |  | In our experience, the DSO is usually only able to implement an automatic LFDD Scheme in substations. In other locations, the implementation of an automatic LFDD Scheme is not possible because there are no power flow measurements available. | [6 empty] | Non-confidential
0005-9675-27bb-30f8-1555 | V1.0 for Public consultation version | 2 | 13 | 4 | - | 2014-12-08 18:18:37 | Thomas Willson |  | final | a) … b) … | a) … b) … c) ensure that this scheme does lead to a overall load reduction similar to the characteristic curve of a droop (group droop of UF relais) | In Article 14 a droop is mention for the over-frequency situation, the under-frequency load shedding should be done in such a way that a shape of roughly a droop with a default value of X % is shown. |  |  | technical |  |  |  | Non-confidential
0005-2159-c3df-7e52-d91d | V1.0 for Public consultation version | 2 | 13 | 4 | - | 2014-12-08 16:38:50 | Rothermann Philippe |  | final | b) ensure that this scheme does not lead to power flow deviation and Voltage deviation outside Operational Security Limits. | b) ensure that this scheme does not lead to power flow deviation and Voltage deviation outside Operational Security Limits in the own distribution grid. | It is not possible for the DSO to ensure, that after a load shedding, the power flow or voltage deviation in the transmission grid or distribution grids of other DSOs is not outside the operational limits . | [6 empty] | Non-confidential
0005-6f79-2780-0bed-b458 | V1.0 for Public consultation version | 2 | 13 | 4 | - | 2014-12-08 17:17:32 | Paul Doyle | ESB Generation & Wholesale Markets | final | ensure that this scheme does not lead to power flow deviation and Voltage deviation outside Operational Security Limits. | ensure that this scheme does not lead to power flow deviation and Voltage deviation outside Operational Security Limits in its area. | Responsibility should be limited to the TSOs control area. |  |  | technical |  |  |  | Non-confidential
0005-e4e5-c3c0-0d19-d847 | V1.0 for Public consultation version | 2 | 13 | 4 | - | 2014-12-08 17:09:24 | Paul Doyle | ESB Generation & Wholesale Markets | final | The DSO shall, when implementing the automatic Low Frequency Demand Disconnection scheme, pursuant to the notification under Article 9(2): | The DSO shall, with the required automatic Low Frequency Demand Disconnection scheme, pursuant to the notification under Article 9(2): | Not only when (read as in case of) implementing, he shall anyway do it! |  |  | legal |  |  |  | Non-confidential
0005-bdae-7d72-e89a-1f48 | V1.0 for Public consultation version | 2 | 13 | 4 | - | 2014-11-28 15:53:01 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | ensure that this scheme does not lead to power flow deviation and Voltage deviation outside Operational Security Limits. | ensure that this scheme does not lead to power flow deviation and Voltage deviation outside Operational Security Limits in its area. | Responsibility should be limited to the TSOs control area. |  |  | technical |  |  |  | Non-confidential
0005-969d-01ae-3b30-e0b7 | V1.0 for Public consultation version | 2 | 13 | 4 | a | 2014-12-05 10:28:56 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | The DSO shall, when implementing the automatic Low Frequency Demand Disconnection scheme, pursuant to the notification under Article 9(2) ensure that this scheme does not lead to power flow deviation and Voltage deviation outside Operational Security Limits. | The DSO shall, when implementing the automatic Low Frequency Demand Disconnection scheme, pursuant to the notification under Article 9(2) take into account that this scheme does not lead to power flow deviation and Voltage deviation outside Operational Security Limits. | At injection points and according system voltage TSO actions have major impacts on power flow respectively system voltage. The DSO can ensure this only in his own area of responsibility. | 1 | 2 | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2302 | V1.0 for Public consultation version | 2 | 13 | 4 | a | 2014-12-08 22:31 | Michael Wilch | RWE | final | ensure to minimise the total disconnected installed capacity of Power Generating Modules connected directly to its distribution system; | ensure to minimise as much as possible the total disconnected installed capacity of Power Generating Modules connected directly to its distribution system; | There should be consideration of what is connected downstream - e.g. in a nested DSO. It does not seem reasonable to 'ensure to minimise' the amount of generation disconnected without this being subject to some form of CBA - otherwise this could result in a need to install LFDD relays on individual feeder circuit breakers in lower voltage substations rather than on the transformer circuit breakers at higher voltage substations. |  |  | Technical
0005-e495-5e7a-d54d-2022 | V1.0 for Public consultation version | 2 | 13 | 4 | b | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | ensure that this scheme does not lead to power flow deviation and Voltage deviation outside Operational Security Limits. | ensure that this scheme does not lead to power flow deviation and Voltage deviation outside Operational Security Limits in its area. | Responsibility should be limited to the TSOs control area.
0005-e495-5e7a-d54d-2303 | V1.0 for Public consultation version | 2 | 13 | 4 | b | 2014-12-08 22:31 | Michael Wilch | RWE | final | ensure that this scheme does not lead to power flow deviation and Voltage deviation outside Operational Security Limits. | ensure, in collaboration with the TSO, that this scheme does not lead to power flow deviation and Voltage deviation outside Operational Security Limits. | This should be done in collaboration between DSO and TSO. DSOs might not have the information to acurately assess the impact of the their LFDD design on operational security limits of transmission networks. |  |  | Technical
0005-e495-5e7a-d54d-2023 | V1.0 for Public consultation version | 2 | 13 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The DSO shall, when implementing the automatic Low Frequency Demand Disconnection scheme, pursuant to the notification under Article 9(2): | The DSO shall, with the required automatic Low Frequency Demand Disconnection scheme, pursuant to the notification under Article 9(2): | Not only when (read as in case of) implementing, the DSO should do this in in any case.
0005-e495-5e7a-d54d-2166 | V1.0 for Public consultation version | 2 | 13 | 4 |  | 2014-12-08 21:33 | AG | RWE | final | The DSO shall, when implementing the automatic Low Frequency Demand Disconnection scheme, pursuant to the notification under Article 9(2): | The TSO or DSO shall, with the required automatic Low Frequency Demand Disconnection scheme, pursuant to the notification under Article 9(2): | Not only when (read as in case of) implementing, the DSO should do this in in any case. Also demend may be connected at Transmission level as well. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2167 | V1.0 for Public consultation version | 2 | 13 | 4 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | When a DSO cannot fulfil the two requirements under paragraphs 4(a) and (b), it shall notify the TSO and propose which one of these requirements shall prevail. The TSO shall define the applicable requirements. | When a DSO cannot fulfil the two requirements under paragraphs 4(a) and (b), it shall notify the TSO and propose which one of these requirements shall prevail. The TSO shall define the applicable requirements. When a TSO cannot fulfil the two requirements under paragraph 4(a) and 4(b), it shall notify the NRA and propose which one of these requirements shall prevail. The NRA shall define the applicable requirements. | There should be an appropriate escalation process in place. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2241 | V1.0 for Public consultation version | 2 | 13 | 4 |  | 2014-12-08 12:24 | Wolfram Heckmann | Fraunhofer IWES | final | “a) ensure to minimize the total disconnected installed capacity of Power Generating Modules…” |  | Installed or better actual generating power, e.g. considering variable in-feed of renewables?
0005-e495-5e7a-d54d-1777 | V1.0 for Public consultation version | 2 | 13 | 4 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | The DSO shall, when implementing the automatic Low Frequency Demand Disconnection scheme, pursuant to the notification under Article 9(2): a) ensure to minimise the total disconnected installed capacity of Power Generating Modules connected directly to its distribution system; and | The TSO OR DSO shall, when implementing the automatic Low Frequency Demand Disconnection scheme, pursuant to the notification under Article 9(2): a) ensure to minimise the total disconnected installed capacity of Power Generating Modules connected directly to its TRANSMISSION OR distribution system; and | Demand maybe connected at Transmission level and it is discriminatory (and illegal under EU law?) not to apply this obligation to TSOs as well as DSOs.
0005-e495-5e7a-d54d-1780 | V1.0 for Public consultation version | 2 | 13 | 4 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | When a DSO cannot fulfil the two requirements under paragraphs 4(a) and 4(b), it shall notify the TSO and propose which one of these requirements shall prevail. The TSO shall define the applicable requirements. | When a DSO cannot fulfil the two requirements under paragraphs 4(a) and 4(b), it shall notify the TSO and propose which one of these requirements shall prevail. The TSO shall define the applicable requirements. WHEN A TSO CANNOT FULFIL THE TWO REQUIREMENTS UNDER PARAGRAPHS 4(A) AND 4(B), IT SHALL NOTIFY THE NRA AND PROPOSE WHICH ONE OF THESE REQUIREMENTS SHALL PREVAIL. THE NRA SHALL DEFINE THE APPLICABLE REQUIREMENTS. | As per the point made above, this needs to deal with LFDD on the transmission (as well as the distribution) system.
0005-4892-db6e-e836-3985 | V1.0 for Public consultation version | 2 | 13 | 5 | - | 2014-11-28 15:51:10 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | When the automatic Low Frequency Demand Disconnection scheme has to be implemented on Transmission System, the TSO shall respect principles set in paragraphs 4(a) and 4(b). | Where the automatic Low Frequency Demand Disconnection scheme has to be implemented on Transmission System, the TSO shall respect principles set in paragraphs 4(a) and 4(b). When a TSO cannot fulfil these requirements, it shall notify the NRA and propose which of these requirements shall prevail. The NRA shall define the applicable requirements. | Bring it in line with article 13.4. When the DSO fails, the TSO decides, when the TSO fails, the NRA decides! |  |  | legal |  |  |  | Non-confidential
0005-2159-75a1-7fe2-e8b4 | V1.0 for Public consultation version | 2 | 13 | 5 | - | 2014-12-08 16:38:50 | Rothermann Philippe |  | final | 5. When the automatic Low Frequency Demand Disconnection scheme has to be implemented on Transmission System, the TSO shall respect principles set in paragraphs 4(a) and 4(b). |  | If LFDD is applied in the transmission system, the TSO has to be sure, that substations are not interconnected by the distribution grid. Otherwise the total load is not reduced but only the load flows in the transmission grid and and the distribution grid are changed. This could lead to overload situations in the distribution grid. | [6 empty] | Non-confidential
0005-6f65-3720-0f0d-5215 | V1.0 for Public consultation version | 2 | 13 | 5 | - | 2014-12-08 17:09:25 | Paul Doyle | ESB Generation & Wholesale Markets | final | When the automatic Low Frequency Demand Disconnection scheme has to be implemented on Transmission System, the TSO shall respect principles set in paragraphs 4(a) and 4(b). | Where the automatic Low Frequency Demand Disconnection scheme has to be implemented on Transmission System, the TSO shall respect principles set in paragraphs 4(a) and 4(b). When a TSO cannot fulfil these requirements, it shall notify the NRA and propose which of these requirements shall prevail. The NRA shall define the applicable requirements. | Bring it in line with article 13.4. When the DSO fails, the TSO decides, when the TSO fails, the NRA decides! |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2024 | V1.0 for Public consultation version | 2 | 13 | 5 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | When the automatic Low Frequency Demand Disconnection scheme has to be implemented on Transmission System, the TSO shall respect principles set in paragraphs 4(a) and 4(b). | Where the automatic Low Frequency Demand Disconnection scheme has to be implemented on Transmission System, the TSO shall respect principles set in paragraphs 4(a) and 4(b). When a TSO cannot fulfil these requirements, it shall notify the NRA and propose which of these requirements shall prevail. The NRA shall define the applicable requirements. | Bring it in line with article 13.4. When the DSO fails, the TSO decides, when the TSO fails, the NRA should decides.
0005-e495-5e7a-d54d-1781 | V1.0 for Public consultation version | 2 | 13 | 5 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | When the automatic Low Frequency Demand Disconnection scheme has to be implemented on Transmission System, the TSO shall respect principles set in paragraphs 4(a) and 4(b). | When the automatic Low Frequency Demand Disconnection scheme has to be implemented on Transmission System, the TSO shall respect principles set in paragraphs 4(a) and 4(b). | Delete and amend Art 13(4) to include TSOs as they should be held to the same standard / obligation etc., as other parties (i.e. DSOs).
0005-4869-27ac-d615-de4b | V1.0 for Public consultation version | 2 | 13 | - | - | 2014-12-08 23:56:24 | Gunnar Kaestle | Clausthal University of Technology | final | Article 13 Automatic low Frequency control sheme | Article 13 Automatic Under-Frequency control sheme (and modify whole article accordingly) | Low Frequency is a frequency band, http://en.wikipedia.org/wiki/Low_frequency, the article describes actions that are triggered when the operating point (frequency as an indicator for the system state) goes under a special threshold. |  |  | technical |  |  |  | Non-confidential
0005-48a5-278e-d4e9-533f | V1.0 for Public consultation version | 2 | 13 | - | - | 2014-12-08 23:56:24 | Gunnar Kaestle | Clausthal University of Technology | final | Table 1: Automatic Low Frequency Demand Disconnection scheme parameters | Table 1: Automatic Under-Frequency Load Shedding scheme parameters + fill in parameters | without figures in table 1 no technical comments can be given. Editorial comment is again: Load Shedding is the correct term, done at Under-Frequency. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2297 | V1.0 for Public consultation version | 2 | 13 | - | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | - | - | General comment on Article 13: The automatic low frequency control scheme proposed in the code is only focused on disconnection of demand connected to Distribution Networks. The code should also add objectives on implementation of automatic low frequency schemes to SGUs connected to the transmission network. |  |  | Technical
0005-e495-5e7a-d54d-1776 | V1.0 for Public consultation version | 2 | 13 |  |  | 2014-12-08 13:31 | Garth Graham | SSE |  | TABLE 1 | XYZ | Without there being any numbers in this table we cannot comment on this Article in detail. WE reserve our right to respond, at a later date, when the numbers in this Table are published by ENTSOe.
0005-4891-11e0-a295-ca70 | V1.0 for Public consultation version | 2 | 14 | 1 | - | 2014-12-04 14:14:26 | Dekinderen Eric | Genrator company | final | The automatic high Frequency control scheme of the System Defence Plan shall lead to a decreases of the total Active Power of each LFC Area with a Droop between | The automatic high Frequency control scheme of the System Defence Plan shall lead to a decreases of the total injected Active Power of each LFC Area with a Droop between | To add the word "injected" |  |  | technical |  |  |  | Non-confidential
0005-6f66-181e-e76e-2950 | V1.0 for Public consultation version | 2 | 14 | 1 | - | 2014-11-28 15:51:10 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The automatic high Frequency control scheme of the System Defence Plan shall lead to a decreases of the total Active Power of each LFC Area with a Droop between 2% and 12%, in case of Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. | The automatic high Frequency control scheme of the System Defence Plan shall lead to a decreases of the total injected Active Power inside each LFC Area with a Droop between 2% and 12%, in case of Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. | Total active power is not defined. We are talking about the total feed in of active power inside the area! Decrease of consumed active power would be catastrophic! |  |  | technical |  |  |  | Non-confidential
0005-e4e5-297a-11a6-6516 | V1.0 for Public consultation version | 2 | 14 | 1 | - | 2014-12-03 11:19:40 | AXPO Group |  | final | The automatic high Frequency control scheme of the System Defence Plan shall lead to a decreases of the total Active Power of each LFC Area with a Droop between 2% and 12%, in case of Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. | see Comment | The application of this measure to every single power module (large and small) goes too far. A determination to which type of power module this measure applies is needed. The content and structure of article 14 has to be symmetrical to article 13 (Automatic low Frequency control scheme). Since both articles follow symmetrical approches. One for load (article 13). One for generation (article 14). |  |  | technical |  |  |  | Non-confidential
0005-bdd5-8540-0ea9-a02d | V1.0 for Public consultation version | 2 | 14 | 1 | - | 2014-12-08 17:09:26 | Paul Doyle | ESB Generation & Wholesale Markets | final | The automatic high Frequency control scheme of the System Defence Plan shall lead to a decreases of the total Active Power of each LFC Area with a Droop between 2% and 12%, in case of Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. | The automatic high Frequency control scheme of the System Defence Plan shall lead to a decreases of the total injected Active Power inside each LFC Area with a Droop between 2% and 12%, in case of Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. | Total active power is not defined. We are talking about the total feed in of active power inside the area! Decrease of consumed active power would be catastrophic! |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2025 | V1.0 for Public consultation version | 2 | 14 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The automatic high Frequency control scheme of the System Defence Plan shall lead to a decreases of the total Active Power of each LFC Area with a Droop between 2% and 12%, in case of Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. | The automatic high Frequency control scheme of the System Defence Plan shall lead to a decreases of the total injected Active Power inside each LFC Area with a Droop between 2% and 12%, in case of Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. | Total active power is not defined. We are talking about the total feed in of active power inside the area. Decrease of consumed active power would be catastrophic.
0005-e495-5e7a-d54d-2169 | V1.0 for Public consultation version | 2 | 14 | 1 |  | 2014-12-08 21:33 | AG | RWE | final | The automatic high Frequency control scheme of the System Defence Plan shall lead to a decreases of the total Active Power of each LFC Area with a Droop between 2% and 12%, in case of Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. | The automatic high Frequency control scheme of the System Defence Plan shall lead to a decreases of the total injected Active Power inside each LFC Area with a Droop between 2% and 12%, in case of Frequency Deviation outside System Frequency limits for Alert State defined in Article 42(4) [NC LFCR]. | Total active power is not defined. We are talking about the total feed in of active power inside the area. Decrease of consumed active power could be catastrophic. |  |  | Technical | Editorial
0005-216d-28ad-cf9c-cf3b | V1.0 for Public consultation version | 2 | 14 | 2 | - | 2014-12-05 17:01:43 | Til Kristian Vrana |  | final | automatic high Frequency control | automatic over-Frequency control | High frequency relates to high frequencies, often in the kHz and MHz range. The phenomenon referred to here is called over-frequency. |  |  | technical |  |  |  | Non-confidential
0005-e4e5-104c-0f0d-7e1f | V1.0 for Public consultation version | 2 | 14 | 2 | - | 2014-12-08 17:09:28 | Paul Doyle | ESB Generation & Wholesale Markets | final | In case the combined action of Limited Frequency Sensitive Mode of Power Generating Modules in a LFC Area are not sufficient to fulfil the above requirement, each TSO shall complement the automatic high Frequency control scheme of its System Defence Plan with a step-wise linear disconnection of Power Generating Modules. | In case the combined action of Limited Frequency Sensitive Mode of Power Generating Modules and/or HVDC in a LFC Area are not sufficient to fulfil the above requirement, each TSO shall complement the automatic high Frequency control scheme of its System Defence Plan with a step-wise linear disconnection of HVDC feed in and/or Power Generating Modules. | To prevent discrimination, also mention HVDC! |  |  | legal |  |  |  | Non-confidential
0005-bd86-cbce-e962-450f | V1.0 for Public consultation version | 2 | 14 | 2 | - | 2014-11-28 15:51:11 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | In case the combined action of Limited Frequency Sensitive Mode of Power Generating Modules in a LFC Area are not sufficient to fulfil the above requirement, each TSO shall complement the automatic high Frequency control scheme of its System Defence Plan with a step-wise linear disconnection of Power Generating Modules. | In case the combined action of Limited Frequency Sensitive Mode of Power Generating Modules and/or HVDC in a LFC Area are not sufficient to fulfil the above requirement, each TSO shall complement the automatic high Frequency control scheme of its System Defence Plan with a step-wise linear disconnection of HVDC feed in and/or Power Generating Modules. | To prevent discrimination, also mention HVDC! |  |  | legal |  |  |  | Non-confidential
0005-487d-ae03-245f-017f | V1.0 for Public consultation version | 2 | 14 | 2 | - | 2014-12-08 17:01:18 | Jasmina PIERRE | EdF | final | 2. In case the combined action of Limited Frequency Sensitive Mode of Power Generating Modules in a LFC Area are not sufficient to fulfil the above requirement, each TSO shall complement the automatic high Frequency control scheme of its System Defence Plan with a step-wise linear disconnection of Power Generating Modules. | 2. In case the combined action of Limited Frequency Sensitive Mode of Power Generating Modules in a LFC Area are not sufficient to fulfil the above requirement, each TSO shall complement the automatic high Frequency control scheme of its System Defence Plan with a step-wise linear disconnection of Power Generating Modules. The automatic high Frequency control scheme of the System Defence Plan shall include the following parameters: a) Frequency range in which High Frequency Demand Disconnection is possible (High Frequency allowed range); b) Frequency range in which High Frequency Demand Disconnection is mandatory (High Frequency mandatory range); The parameters shall be in line with the following values for each Synchronous Area: (new table 2) | The engagement of mutual assistance throughout Europe should come along with a high level transparency regarding minimal performances for defense and restoration to be targeted within each control area. Parameters for the automatic high Frequency control scheme of the System Defence Plan need also to be defined. Related values should be submitted for additional public consultation to be launched by ENTSO-E. |  |  | technical |  |  |  | Non-confidential
0005-bdd5-5e6d-7fe2-1a48 | V1.0 for Public consultation version | 2 | 14 | 2 | - | 2014-12-08 16:38:50 | Rothermann Philippe |  | final | 2. In case the combined action of Limited Frequency Sensitive Mode of Power Generating Modules in a LFC Area are not sufficient to fulfil the above requirement, each TSO shall complement the automatic high Frequency control scheme of its System Defence Plan with a step-wise linear disconnection of Power Generating Modules. |  | If power generating modules, which are being used by the TSO for primary or secondary control are automatically disconnected from the power grid, these machines are no longer available for frequency control. It is be better to only disconnect machines who are not participating in primary or secondary control. | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-2026 | V1.0 for Public consultation version | 2 | 14 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | In case the combined action of Limited Frequency Sensitive Mode of Power Generating Modules in a LFC Area are not sufficient to fulfil the above requirement, each TSO shall complement the automatic high Frequency control scheme of its System Defence Plan with a step-wise linear disconnection of Power Generating Modules. | In case the combined action of Limited Frequency Sensitive Mode of Power Generating Modules and/or HVDC in a LFC Area are not sufficient to fulfil the above requirement, each TSO shall complement the automatic high Frequency control scheme of its System Defence Plan with a step-wise linear disconnection of HVDC feed in and/or Power Generating Modules. | To prevent discrimination, also HVDC should be mentioned.
0005-e495-5e7a-d54d-2366 | V1.0 for Public consultation version | 2 | 14 | 2 |  | 2014-12-09 09:29 | Dr. Til Kristian Vrana | Sintef | final | automatic high Frequency control | automatic over-Frequency control | high frequency refers to high frequencies, typically in the kHz and MHz range. The phenomenon referred to here is over-frequency.
0005-e495-5e7a-d54d-2027 | V1.0 for Public consultation version | 2 | 14 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | A new article should be added. The costs must be addressed to make sure that over all optimal economic sollutions will be used.
0005-e495-5e7a-d54d-2170 | V1.0 for Public consultation version | 2 | 14 | 5 |  | 2014-12-08 21:33 | AG | RWE | final | When the automatic Low Frequency Demand Disconnection scheme has to be implemented on Transmission System, the TSO shall respect principles set in paragraphs 4(a) and 4(b). | Where the automatic Low Frequency Demand Disconnection scheme has to be implemented on Transmission System, the TSO shall respect principles set in paragraphs 4(a) and 4(b). When a TSO cannot fulfil these requirements, it shall notify the NRA and propose which of these requirements shall prevail. The NRA shall define the applicable requirements. | Bring it in line with article 13(4). When the DSO fails, the TSO decides, when the TSO fails, the NRA should decides. |  |  | Technical | Fundamental
0005-e4d1-d39c-0bed-1a44 | V1.0 for Public consultation version | 2 | 14 | - | - | 2014-12-08 17:09:30 | Paul Doyle | ESB Generation & Wholesale Markets | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | legal |  |  |  | Non-confidential
0005-bdc2-b422-e7d2-96f5 | V1.0 for Public consultation version | 2 | 14 | - | - | 2014-11-28 15:51:12 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | legal |  |  |  | Non-confidential
0005-48a5-4e9e-d679-bee1 | V1.0 for Public consultation version | 2 | 14 | - | - | 2014-12-08 23:56:24 | Gunnar Kaestle | Clausthal University of Technology | final | Article 14 Automatic High Frequency control scheme | Article 14 Automatic Over-Frequency control scheme | High Frequency is a term from the domain of radio transmission, use over-frequency instead. http://www.oxforddictionaries.com/definition/english/high-frequency?q=high+frequency |  |  | technical |  |  |  | Non-confidential
0005-9689-d55a-1016-96bc | V1.0 for Public consultation version | 2 | 14 | - | - | 2014-12-03 11:19:40 | AXPO Group |  | final | missing paragraph | see Comment | Add a new article. The costs must be addressed. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2168 | V1.0 for Public consultation version | 2 | 14 |  |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | See the wording of Article 14- automatic high Frequency control scheme- general comment | See the justification. | In some countries, there is no automatic high frequency control, or an automatic scheme against voltage collapse. To provide them will be costly with potentially limited benefit. |  |  | Technical | Fundamental
0005-bdd5-5fe2-a1cc-4fdf | V1.0 for Public consultation version | 2 | 15 | 1 | - | 2014-12-04 14:04:32 | Dekinderen Eric | Genrator company | final | The Voltage deviation management procedure of the System Defence Plan shall contain a set of measures to manage Voltage deviation outside Operational Security Limits defined in Article 10(1) and (2) [NC OS]. | The Voltage deviation management procedure of the System Defence Plan shall contain a set of measures to manage Voltage deviation outside Operational Security Limits defined in Article 10(1), (2) and (3) [NC OS]. | In NC OS Art.10,3 : provisions are specified for existing plants. Those plants have to be included in this provision |  |  | legal |  |  |  | Non-confidential
0005-968a-7d72-e89a-8614 | V1.0 for Public consultation version | 2 | 15 | 1 | - | 2014-11-28 15:51:13 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The Voltage deviation management procedure of the System Defence Plan shall contain a set of measures to manage Voltage deviation outside Operational Security Limits defined in Article 10(1) and (2) [NC OS]. | The Voltage deviation management procedure of the System Defence Plan shall contain a set of measures to manage Voltage deviation outside Operational Security Limits defined in Article 10(1), (2) and (3)[NC OS]. | A reference to OS Art.10.3 is mandatory for existing PGMs not conforming RfG. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2028 | V1.0 for Public consultation version | 2 | 15 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The Voltage deviation management procedure of the System Defence Plan shall contain a set of measures to manage Voltage deviation outside Operational Security Limits defined in Article 10(1) and (2) [NC OS]. | The Voltage deviation management procedure of the System Defence Plan shall contain a set of measures to manage Voltage deviation outside Operational Security Limits defined in Article 10(1), (2) and (3)[NC OS]. | A reference to OS Art.10.3 is mandatory for existing PGMs not conforming RfG.
0005-2159-76fc-3bf8-2a05 | V1.0 for Public consultation version | 2 | 15 | 2 | - | 2014-12-05 10:29:45 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each TSO shall organise these measures in such a way that Voltage control capabilities of Significant Grid Users are used before activating manual Demand disconnection as defined in Article 19. | Each TSO shall organise these measures in such a way that Voltage control capabilities of Significant Grid Users are used before activating other measures like manual Demand disconnection as defined in Article 19, considering the national legislation. | more generell formulated | 1 | 3 | legal |  |  |  | Non-confidential
0005-2159-11a5-25ef-b979 | V1.0 for Public consultation version | 2 | 15 | 2 | - | 2014-12-08 17:01:19 | Jasmina PIERRE | EdF | final | Each TSO shall organise these measures in such a way that Voltage control capabilities of Significant Grid Users are used before activating manual Demand disconnection as defined in Article 19. | Each TSO shall organise these measures in such a way that Voltage control capabilities of Significant Grid Users are used before activating manual Demand disconnection as defined in Article 19, while respecting their technical constraints. | It is essential all the instructions given by the TSO for execution respect the respective technical constraints and minimize related impacts for grid users. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2304 | V1.0 for Public consultation version | 2 | 15 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall organise these measures in such a way that Voltage control capabilities of Significant Grid Users are used before activating manual Demand disconnection as defined in Article 19. | Each TSO shall organise these measures in such a way that Voltage control capabilities of Significant Grid Users connected to the Transmission System are used before activating manual Demand disconnection as defined in Article 19. | The TSO should not take any actions on SGUs connected to the Distribution System. This paragraph still stays rather vague. What are the voltage control measures of SGUs and what means does the TSO have to organise them? |  |  | Technical
0005-e495-5e7a-d54d-1783 | V1.0 for Public consultation version | 2 | 15 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall organise these measures in such a way that Voltage control capabilities of Significant Grid Users are used before activating manual Demand disconnection as defined in Article 19. | Each TSO shall organise these measures in such a way that Voltage control capabilities of Significant Grid Users are PROCURED AND used before activating manual Demand disconnection as defined in Article 19. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-2145-387c-3c5c-2af6 | V1.0 for Public consultation version | 2 | 15 | 3 | - | 2014-12-05 10:48:05 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each TSO shall be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | Each TSO shall be entitled to define a Reactive Power or Voltage range and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | A Setpoint seems not to be practicable, because of the stochastic behavour of the load and renewable generation. | 1 | 2 | technical |  |  |  | Non-confidential
0005-6fa1-c3fc-0f0d-2736 | V1.0 for Public consultation version | 2 | 15 | 3 | - | 2014-12-08 17:09:31 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | Each TSO shall be entitled to define a Reactive Power or Voltage set-point for the Emergency State and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | TSO should only be entitled to define the set-points in Emergency State. Cf. DSOs remarks on this topic in the NC OS and NC DCC. |  |  | technical |  |  |  | Non-confidential
0005-e4bd-d360-0de0-c097 | V1.0 for Public consultation version | 2 | 15 | 3 | - | 2014-12-08 17:09:33 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | Each TSO shall be entitled to define a Reactive Power or Voltage set-point, while respecting the provisions of NC RfG, NC DC and NC HVDC, and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | This shall avoid an undermining of the provisions of other Network Codes. |  |  | legal |  |  |  | Non-confidential
0005-4869-86aa-e292-edb7 | V1.0 for Public consultation version | 2 | 15 | 3 | - | 2014-12-08 16:39:17 | Markus Hemmer | EnBW | final | Each TSO shall be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | Each TSO shall be entitled to define a Reactive Power or Voltage set-point, while respecting the provisions of NC RfG, NC DC and NC HVDC, and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | This shall avoid an undermining of the provisions of this NCs. | [6 empty] | Non-confidential
0005-968a-3f10-e70a-52f4 | V1.0 for Public consultation version | 2 | 15 | 3 | - | 2014-11-28 15:51:14 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | Each TSO shall be entitled to define a Reactive Power or Voltage set-point for the Emergency State and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | TSO should only be entitled to define the set-points in Emergency State. Cf. DSOs remarks on this topic in the NC OS and NC DCC. |  |  | technical |  |  |  | Non-confidential
0005-e4d2-a4be-e8fe-d2e9 | V1.0 for Public consultation version | 2 | 15 | 3 | - | 2014-11-28 15:51:15 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | Each TSO shall be entitled to define a Reactive Power or Voltage set-point, while respecting the provisions of NC RfG, NC DC and NC HVDC, and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | This shall avoid an undermining of the provisions of other Network Codes. |  |  | legal |  |  |  | Non-confidential
0005-9675-102f-7fe2-4fbd | V1.0 for Public consultation version | 2 | 15 | 3 | - | 2014-12-08 16:38:51 | Rothermann Philippe |  | final | Each TSO shall be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | Each TSO shall be entitled to define a Reactive Power or Voltage range and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | In Article 10 of the [NC OS] the term word voltage range is used. | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-2305 | V1.0 for Public consultation version | 2 | 15 | 3 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | Each TSO shall be entitled to define a Reactive Power or Voltage set-point for the Emergency State and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | TSO should only be entitled to define the set-points in Emergency State. Cf. DSOs remarks on this topic in the NC OS and NC DCC. |  |  | Technical
0005-e495-5e7a-d54d-2029 | V1.0 for Public consultation version | 2 | 15 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | Each TSO shall be entitled to define a Reactive Power or Voltage set-point for the Emergency State and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | TSO should only be entitled to define the set-points in Emergency State. Cf. DSOs remarks on this topic in the NC OS and NC DCC.
0005-e495-5e7a-d54d-2030 | V1.0 for Public consultation version | 2 | 15 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | Each TSO shall be entitled to define a Reactive Power or Voltage set-point, while respecting the provisions of NC RfG, NC DC and NC HVDC, and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | This shall avoid an undermining of the provisions of other Network Codes.
0005-e495-5e7a-d54d-2171 | V1.0 for Public consultation version | 2 | 15 | 3 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO shall be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | Each TSO shall, subject to NRA approval (…), be entitled (…) | There must be NRA approval of the set point (and any changes to the set point). As a general comment (and as already stated), the Code lacks the NRA approvals which all TSO decisions shall be subject to. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1785 | V1.0 for Public consultation version | 2 | 15 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users to maintain it, according to Article 10 [NC OS]. | Each TSO shall, SUBJECT TO NRA APPROVAL, be entitled to define a Reactive Power or Voltage set-point and instruct the DSOs, Closed Distribution Networks and Significant Grid Users PROVIDING PROCURED SERVICES to maintain it, according to Article 10 [NC OS]. | There must be NRA approval of the set point (and any changes to that set point). Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-6fa1-2780-0e44-18f8 | V1.0 for Public consultation version | 2 | 15 | 4 | - | 2014-12-08 17:09:34 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall, upon request of neighbouring TSO, make available all Reactive Power capabilities that do not endanger Operational Security in its Responsibility Area. During activation of this measure, the Operational Security Limits defined according to Article 8(8) [NC OS] may be exceeded. | Each TSO shall, upon request of neighbouring TSO being in operation outside Operational Security Limits defined in Article 10(1) and (2) [NC OS], make available all Reactive Power capabilities that do not endanger Operational Security in its Responsibility Area. During activation of this measure, the Operational Security Limits defined according to Article 8(8) [NC OS] may be exceeded. | Only valid in case of emergency in neighbour area. |  |  | legal |  |  |  | Non-confidential
0005-e4aa-7d90-e836-6a09 | V1.0 for Public consultation version | 2 | 15 | 4 | - | 2014-11-28 15:51:16 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall, upon request of neighbouring TSO, make available all Reactive Power capabilities that do not endanger Operational Security in its Responsibility Area. During activation of this measure, the Operational Security Limits defined according to Article 8(8) [NC OS] may be exceeded. | Each TSO shall, upon request of neighbouring TSO being in operation outside Operational Security Limits defined in Article 10(1) and (2) [NC OS], make available all Reactive Power capabilities that do not endanger Operational Security in its Responsibility Area. During activation of this measure, the Operational Security Limits defined according to Article 8(8) [NC OS] may be exceeded. | Only valid in case of emergency in neighbour area. |  |  | legal |  |  |  | Non-confidential
0005-e4bd-11e1-245f-41e1 | V1.0 for Public consultation version | 2 | 15 | 4 | - | 2014-12-08 17:01:19 | Jasmina PIERRE | EdF | final | 4. Each TSO shall, upon request of neighbouring TSO, make available all Reactive Power capabilities that do not endanger Operational Security in its Responsibility Area. During activation of this measure, the Operational Security Limits defined according to Article 8(8) [NC OS] may be exceeded. | 4. Each TSO shall, upon request of neighbouring TSO, make available all Reactive Power capabilities that do not endanger Operational Security in its Responsibility Area. During activation of this measure, the Operational Security Limits defined according to Article 8(8) [NC OS] may be exceeded. Cost recovery should be done according to the principles defined in Article [36]. | It is essential that TSOs shall bear all the costs incurred by grid users for (i) the actions/measures carried out upon TSO request; (ii) additional and redundant (voice) communication channels; (iii) measures to ensure the extended (>24h) availability of critical tools and facilities and (iv) for “compliance testing” of equipment and procedures required to ensure reliability of prepared System Defense and Restoration Plans. “Overall cost recovery” is required to incentivize TSOs to pursue cost overall efficiency and to prevent from any discrimination between grid users in competition through the markets, in accordance with principles defined in “general conditions” chapter (article 3.3.c). |  |  | technical |  |  |  | Non-confidential
0005-bdc1-8711-23fb-491e | V1.0 for Public consultation version | 2 | 15 | 4 | - | 2014-12-08 17:01:19 | Jasmina PIERRE | EdF | final | Each TSO shall, upon request of neighbouring TSO, make available all Reactive Power capabilities that do not endanger Operational Security in its Responsibility Area. During activation of this measure, the Operational Security Limits defined according to Article 8(8) [NC OS] may be exceeded. | Each TSO shall, upon request of neighbouring TSO being in operation outside Operational Security Limits defined in Article 10(1) and (2) [NC OS], make available all Reactive Power capabilities that do not endanger Operational Security in its Responsibility Area. During activation of this measure, the Operational Security Limits defined according to Article 8(8) [NC OS] may be exceeded. | It should be clear that such is disposal only apply in case of emergency in neighbouring areas. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2031 | V1.0 for Public consultation version | 2 | 15 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall, upon request of neighbouring TSO, make available all Reactive Power capabilities that do not endanger Operational Security in its Responsibility Area. During activation of this measure, the Operational Security Limits defined according to Article 8(8) [NC OS] may be exceeded. | Each TSO shall, upon request of neighbouring TSO being in operation outside Operational Security Limits defined in Article 10(1) and (2) [NC OS], make available all Reactive Power capabilities that do not endanger Operational Security in its Responsibility Area. During activation of this measure, the Operational Security Limits defined according to Article 8(8) [NC OS] may be exceeded. | Only valid in case of emergency in neighbour area.
0005-e495-5e7a-d54d-1786 | V1.0 for Public consultation version | 2 | 15 | 4 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall, upon request of neighbouring TSO, make available all Reactive Power capabilities that do not endanger Operational Security in its Responsibility Area. During activation of this measure, the Operational Security Limits defined according to Article 8(8) [NC OS] may be exceeded. | Each TSO shall, upon request of neighbouring TSO, make available all Reactive Power capabilities that do not endanger Operational Security in its Responsibility Area AND THE COSTS INCURRED BY THE SUPPORTING TSO OF DOING SO SHALL BE BORN BY THE REQUESTING TSO. During activation of this measure, the Operational Security Limits defined according to Article 8(8) [NC OS] may be exceeded. | There needs to be a clear reference to cost recovery to avoid the cost of providing support to another TSO in an Emergency, Black Start or Restoration State falling upon consumers in another TSO’s area
0005-e495-5e7a-d54d-2172 | V1.0 for Public consultation version | 2 | 15 | 5 |  | 2014-12-08 21:33 | AG | RWE | final | Add new paragraph. | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | A new article should be added. The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | Legal | Fundamental
0005-e4bd-27bc-0f70-2b6e | V1.0 for Public consultation version | 2 | 16 | 1 | - | 2014-12-08 17:09:35 | Paul Doyle | ESB Generation & Wholesale Markets | final | The automatic scheme against Voltage collapse of the System Defence Plan shall include at least an On Load Tap Changer Blocking scheme. | The automatic scheme against Voltage collapse of the System Defence Plan shall only include an On Load Tap Changer Blocking scheme if necessary, based on the assessment from the TSO pursuant to Article 20(3)c [NC DC]. | On-load tap changer blocking is described in art. 20 §3 (c) and (d) and §4 of the current version of the NC DC: “ §3 With regard to Low Voltage Demand Disconnection schemes: (…) (c) Based on the TSO assessment of system security the implementation of On load Tap Changer Blocking and Low Voltage Demand Disconnection shall be binding for Transmission Connected Distribution Network Operators. (d) If the Relevant TSO decides to implement a Low Voltage Demand Disconnection scheme, both On Load Tap Changer Blocking and Low Voltage Demand Disconnection shall be fitted in a coordinated way led by the TSO. §4 With regard to blocking of On Load Tap Changers: (a) The transformer at the Transmission Connected Distribution Network Connection Point to the Transmission Network shall be capable of automatic or manual On Load Tap Changer Blocking, if required by the Relevant TSO. (b) The automatic On Load Tap Changer Blocking scheme shall be specified by the Relevant TSO, while respecting the provisions of Article 9(3).” It is clear that the TSO has to make an assessment if the necessity for the use of on-load tap changer blocking, he cannot simply include it in the System Defence Plan. |  |  | legal |  |  |  | Non-confidential
0005-bdad-50a8-12d2-9e3c | V1.0 for Public consultation version | 2 | 16 | 1 | - | 2014-12-03 11:19:40 | AXPO Group |  | final | The automatic scheme against Voltage collapse of the System Defence Plan shall include at least an On Load Tap Changer Blocking scheme. | see Comment | This type of scheme is mentioned also in other codes. For example NC OS Article 10, subpoint 15 and 18. So far, this type of scheme is always based on a instruction between TSO and DSO. A scheme that works automatic was never required so far. The request for an automatic scheme goes too far. An On Load Tap Changer Blocking scheme shall be implemented only if necessary, based on the assessment from the TSO pursuant to Article 20(3)c [NC DC]. |  |  | technical |  |  |  | Non-confidential
0005-4892-a4a0-e7d2-1b2a | V1.0 for Public consultation version | 2 | 16 | 1 | - | 2014-11-28 15:51:17 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The automatic scheme against Voltage collapse of the System Defence Plan shall include at least an On Load Tap Changer Blocking scheme. | The automatic scheme against Voltage collapse of the System Defence Plan shall only include an On Load Tap Changer Blocking scheme if necessary, based on the assessment from the TSO pursuant to Article 20(3)c [NC DC]. | On-load tap changer blocking is described in art. 20 §3 (c) and (d) and §4 of the current version of the NC DC: “ §3 With regard to Low Voltage Demand Disconnection schemes: (…) (c) Based on the TSO assessment of system security the implementation of On load Tap Changer Blocking and Low Voltage Demand Disconnection shall be binding for Transmission Connected Distribution Network Operators. (d) If the Relevant TSO decides to implement a Low Voltage Demand Disconnection scheme, both On Load Tap Changer Blocking and Low Voltage Demand Disconnection shall be fitted in a coordinated way led by the TSO. §4 With regard to blocking of On Load Tap Changers: (a) The transformer at the Transmission Connected Distribution Network Connection Point to the Transmission Network shall be capable of automatic or manual On Load Tap Changer Blocking, if required by the Relevant TSO. (b) The automatic On Load Tap Changer Blocking scheme shall be specified by the Relevant TSO, while respecting the provisions of Article 9(3).” It is clear that the TSO has to make an assessment if the necessity for the use of on-load tap changer blocking, he cannot simply include it in the System Defence Plan. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2306 | V1.0 for Public consultation version | 2 | 16 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | The automatic scheme against Voltage collapse of the System Defence Plan shall include at least an On Load Tap Changer Blocking scheme. | The automatic scheme against Voltage collapse of the System Defence Plan shall may include one or more of the following schemes depending on the results of a TSO assessment of system security as described in Article 20(3) [NC DC]: a) Low Voltage Demand Disconnection scheme according to Article 20(3) [NC DC]; b) at least an On Load Tap Changer Blocking scheme according to Article 20(4) [NC DC]; and c) Special Protection Schemes for Voltage management. | On-load tap changer blocking is described in art. 20 §3 (c) and (d) and §4 of the current version of the NC DC: “ §3 With regard to Low Voltage Demand Disconnection schemes: (…) (c) Based on the TSO assessment of system security the implementation of On load Tap Changer Blocking and Low Voltage Demand Disconnection shall be binding for Transmission Connected Distribution Network Operators. (d) If the Relevant TSO decides to implement a Low Voltage Demand Disconnection scheme, both On Load Tap Changer Blocking and Low Voltage Demand Disconnection shall be fitted in a coordinated way led by the TSO. §4 With regard to blocking of On Load Tap Changers: (a) The transformer at the Transmission Connected Distribution Network Connection Point to the Transmission Network shall be capable of automatic or manual On Load Tap Changer Blocking, if required by the Relevant TSO. (b) The automatic On Load Tap Changer Blocking scheme shall be specified by the Relevant TSO, while respecting the provisions of Article 9(3).” It is clear that the TSO has to make an assessment if the necessity for the use of on-load tap changer blocking, he cannot simply include it in the System Defence Plan. |  |  | Legal
0005-e495-5e7a-d54d-2032 | V1.0 for Public consultation version | 2 | 16 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The automatic scheme against Voltage collapse of the System Defence Plan shall include at least an On Load Tap Changer Blocking scheme. | The automatic scheme against Voltage collapse of the System Defence Plan shall only include an On Load Tap Changer Blocking scheme if necessary, based on the assessment from the TSO pursuant to Article 20(3)c [NC DC]. | On-load tap changer blocking is described in art. 20 §3 (c) and (d) and §4 of the current version of the NC DC: “ §3 With regard to Low Voltage Demand Disconnection schemes: (…) (c) Based on the TSO assessment of system security the implementation of On load Tap Changer Blocking and Low Voltage Demand Disconnection shall be binding for Transmission Connected Distribution Network Operators. (d) If the Relevant TSO decides to implement a Low Voltage Demand Disconnection scheme, both On Load Tap Changer Blocking and Low Voltage Demand Disconnection shall be fitted in a coordinated way led by the TSO. §4 With regard to blocking of On Load Tap Changers: (a) The transformer at the Transmission Connected Distribution Network Connection Point to the Transmission Network shall be capable of automatic or manual On Load Tap Changer Blocking, if required by the Relevant TSO. (b) The automatic On Load Tap Changer Blocking scheme shall be specified by the Relevant TSO, while respecting the provisions of Article 9(3).” It is clear that the TSO has to make an assessment if the necessity for the use of on-load tap changer blocking, he cannot simply include it in the System Defence Plan.
0005-e495-5e7a-d54d-2173 | V1.0 for Public consultation version | 2 | 16 | 1 |  | 2014-12-08 21:33 | Wilch | RWE | final | The automatic scheme against Voltage collapse of the System Defence Plan shall include at least an On Load Tap Changer Blocking scheme. | The automatic scheme against Voltage collapse of the System Defence Plan shall only include an On Load Tap Changer Blocking scheme if necessary, based on the assessment from the TSO pursuant to Article 20(3)c [NC DC]. | On-load tap changer blocking is described in art. 20 §3 (c) and (d) and §4 of the current version of the NC DCC: “ §3 With regard to Low Voltage Demand Disconnection schemes: (…) (c) Based on the TSO assessment of system security the implementation of On load Tap Changer Blocking and Low Voltage Demand Disconnection shall be binding for Transmission Connected Distribution Network Operators. (d) If the Relevant TSO decides to implement a Low Voltage Demand Disconnection scheme, both On Load Tap Changer Blocking and Low Voltage Demand Disconnection shall be fitted in a coordinated way led by the TSO. §4 With regard to blocking of On Load Tap Changers: (a) The transformer at the Transmission Connected Distribution Network Connection Point to the Transmission Network shall be capable of automatic or manual On Load Tap Changer Blocking, if required by the Relevant TSO. (b) The automatic On Load Tap Changer Blocking scheme shall be specified by the Relevant TSO, while respecting the provisions of Article 9(3).” It is clear that the TSO has to make an assessment if the necessity for the use of on-load tap changer blocking, he cannot simply include it in the System Defence Plan. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2242 | V1.0 for Public consultation version | 2 | 16 | 1 |  | 2014-12-08 12:24 | Wolfram Heckmann | Fraunhofer IWES | final | “OLTC blocking scheme” |  | MV/LV transformers with automatic OLTC should also be put into consideration.
0005-e495-4e90-0de0-3c60 | V1.0 for Public consultation version | 2 | 16 | 2 | - | 2014-12-08 17:09:37 | Paul Doyle | ESB Generation & Wholesale Markets | final | The TSO shall define the conditions under which the On Load Tap Changer shall block according to Article 20(4) [NC DC], including at least: | The TSO shall define the conditions under which the On Load Tap Changer of distribution transformers shall block according to Article 20(4) [NC DC], including at least: | Make clear which OLTS are being referred to! |  |  | technical |  |  |  | Non-confidential
0005-6f7a-2f52-e8fe-e91b | V1.0 for Public consultation version | 2 | 16 | 2 | - | 2014-11-28 15:52:06 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The TSO shall define the conditions under which the On Load Tap Changer shall block according to Article 20(4) [NC DC], including at least: | The TSO shall define the conditions under which the On Load Tap Changer of distribution transformers shall block according to Article 20(4) [NC DC], including at least: | Make clear which OLTS are being referred to! |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2307 | V1.0 for Public consultation version | 2 | 16 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | The TSO shall define the conditions under which the On Load Tap Changer shall block according to Article 20(4) [NC DC], including at least: a) method of blocking (automatic or manual); b) Voltage level threshold at the Connection Point; c) Reactive Power flow direction; and d) maximum time delay between threshold detection and blocking. | If the assessment demonstrates that the implementation of the On Load Tap Changer blocking scheme is necessary to prevent a Voltage collapse in the TSO Responsibility Area, the TSO shall define the conditions under which the On Load Tap Changer shall block according to Article 20(4) [NC DC], including at least: a) method of blocking (automatic or manual local or remote from Control Room); b) Voltage level threshold at the Connection Point; c) Reactive Power flow direction; and d) maximum time delay between threshold detection and blocking. | Cf. remarks 16§1.
0005-bd85-76fc-3dec-228e | V1.0 for Public consultation version | 2 | 16 | 2 | a | 2014-12-05 10:48:45 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | method of blocking (automatic or manual); | delete | should be deleted, because manual blocking is too slow and should not be taken into consideration. | 1 | 1 | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2033 | V1.0 for Public consultation version | 2 | 16 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The TSO shall define the conditions under which the On Load Tap Changer shall block according to Article 20(4) [NC DC], including at least: | The TSO shall define the conditions under which the On Load Tap Changer of distribution transformers shall block according to Article 20(4) [NC DC], including at least: | Make clear which OLTS are being referred to.
0005-e495-5e7a-d54d-2174 | V1.0 for Public consultation version | 2 | 16 | 2 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | The TSO shall define the conditions under which the On Load Tap Changer shall block according to Article 20(4) [NC DC], including at least: | Each TSO shall define, subject to NRA approval (…) | There must be NRA approval of the conditions, given the relationship with the NC DCC which contains a regulatory oversight. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1789 | V1.0 for Public consultation version | 2 | 16 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | The TSO shall define the conditions under which the On Load Tap Changer shall block according to Article 20(4) [NC DC], including at least | The TSO shall define, SUBJECT TO NRA APPROVAL, the conditions under which the On Load Tap Changer shall block according to Article 20(4) [NC DC], including at least | There must be NRA approval of the conditions etc., given the NRA oversight set out in NC DC.
0005-e495-5e7a-d54d-2308 | V1.0 for Public consultation version | 2 | 16 | 3 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall define automatic Low Voltage Demand Disconnection schemes, as defined in Article 20(3) [NC DC], or other System Protection Schemes for Voltage management, when deemed necessary considering local network conditions. | Each TSO shall define automatic Low Voltage Demand Disconnection schemes, as defined in Article 20(3) [NC DC], or other System Protection Schemes for Voltage management, when deemed necessary considering local network conditions of the relevant transmission and distribution networks. The TSO shall only define other System Protection Schemes if their benefit has been confirmed as the result of a CBA. | Added paragraph to be more specific, also considering possible problems in the distribution network. It does not seem justified that for defining other system protection schemes the TSO can just do so when he thinks it is needed. |  |  | Technical
0005-e495-5e7a-d54d-2175 | V1.0 for Public consultation version | 2 | 16 | 3 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO shall define automatic Low Voltage Demand Disconnection schemes, as defined in Article 20(3) [NC DC} or other… | Each TSO shall define, subject to NRA approval (…) | There must be NRA approval of the schemes, given the relationship with the NC DCC which contains a regulatory oversight. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1792 | V1.0 for Public consultation version | 2 | 16 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall define automatic Low Voltage Demand Disconnection schemes, as defined in Article 20(3) [NC DC], or other… | Each TSO shall define , SUBJECT TO NRA APPROVAL, THE automatic Low Voltage Demand Disconnection schemes, as defined in Article 20(3) [NC DC], or other…. | There must be NRA approval of the schemes etc., given the NRA oversight set out in NC DC.
0005-bd99-4eaf-80aa-859d | V1.0 for Public consultation version | 2 | 16 | - | - | 2014-12-08 16:38:51 | Rothermann Philippe |  | final |  |  | For which transformers do the on load tap changer blocking have to be implemented? Only for the transformers between transmission grid and distribution grid or for all transformers? | [6 empty] | Non-confidential
0005-6fb5-6000-a169-a4a8 | V1.0 for Public consultation version | 2 | 17 | 1 | - | 2014-12-04 14:14:57 | Dekinderen Eric | Genrator company | final | The power flow management procedure of the System Defence Plan shall include a set of measures to manage power flow deviation outside Operational Security Limits defined in accordance with Article 8(5) [NC OS]. These measures shall be used in addition to the measures developed according to Article 12(4) [NC OS] | The power flow management procedure of the System Defence Plan shall include a set of measures to manage power flow outside Operational Security Limits defined in accordance with Article 8(5) [NC OS]. These measures shall be used in addition to the measures developed according to Article 12(4) [NC OS] | to erase "Deviation" |  |  | technical |  |  |  | Non-confidential
0005-6f65-373e-0ea8-a39b | V1.0 for Public consultation version | 2 | 17 | 1 | - | 2014-12-08 17:09:38 | Paul Doyle | ESB Generation & Wholesale Markets | final | The power flow management procedure of the System Defence Plan shall include a set of measures to manage power flow deviation outside Operational Security Limits defined in accordance with Article 8(5) [NC OS]. These measures shall be used in addition to the measures developed according to Article 12(4) [NC OS] | The power flow management procedure of the System Defence Plan shall include a set of measures to manage power flow outside Operational Security Limits defined in accordance with Article 8(5) [NC OS]. These measures shall be used in addition to the measures developed according to Article 12(4) [NC OS] | The inclusion of the term 'deviation' is not necessary. |  |  | technical |  |  |  | Non-confidential
0005-968a-db32-e9c6-5412 | V1.0 for Public consultation version | 2 | 17 | 1 | - | 2014-11-28 15:52:11 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The power flow management procedure of the System Defence Plan shall include a set of measures to manage power flow deviation outside Operational Security Limits defined in accordance with Article 8(5) [NC OS]. These measures shall be used in addition to the measures developed according to Article 12(4) [NC OS] | The power flow management procedure of the System Defence Plan shall include a set of measures to manage power flow outside Operational Security Limits defined in accordance with Article 8(5) [NC OS]. These measures shall be used in addition to the measures developed according to Article 12(4) [NC OS]. The System Defence Plan shall respect the comitments derived from CRMs contracted by facilities located in its area that require delivery in other areas. | The inclusion of the term 'deviation' is not necessary. Energy contracted under a CRM should be delivered, even if its delivery may move the system hosting the CRM resource into the alert or emergency state. Otherwise CRMs in foreign system are not reliable, and CRM trading is de facto not feasible. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2034 | V1.0 for Public consultation version | 2 | 17 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The power flow management procedure of the System Defence Plan shall include a set of measures to manage power flow deviation outside Operational Security Limits defined in accordance with Article 8(5) [NC OS]. These measures shall be used in addition to the measures developed according to Article 12(4) [NC OS] | The power flow management procedure of the System Defence Plan shall include a set of measures to manage power flow outside Operational Security Limits defined in accordance with Article 8(5) [NC OS]. These measures shall be used in addition to the measures developed according to Article 12(4) [NC OS]. The System Defence Plan shall respect the comitments derived from CRMs contracted by facilities located in its area that require delivery in other areas. | The inclusion of the term 'deviation' is not necessary. Energy contracted under a CRM should be delivered, even if its delivery may move the system hosting the CRM resource into the alert or emergency state. Otherwise CRMs in foreign system are not reliable, and CRM trading is de facto not feasible.
0005-4891-adac-3dec-dff4 | V1.0 for Public consultation version | 2 | 17 | 2 | - | 2014-12-05 10:49:35 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs,… | Each TSO shall be entitled to define, in the course as defined in Article 8, an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs,… | the setpoint should be argreed with the relevant DSO according to the procedure described in article 8.1. | 1 | 3 | technical |  |  |  | Non-confidential
0005-e4e5-2932-a3c1-e2e5 | V1.0 for Public consultation version | 2 | 17 | 2 | - | 2014-12-04 14:15:23 | Dekinderen Eric | Genrator company | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. The financial consequences of the modification of the set-point have to be described in a contract, agreed upfront. | The financial consequences of an imposed set-point have to be agreed upfront. This process is already accepted by the TSO in Belgium |  |  | legal |  |  |  | Non-confidential
0005-bdd5-d3e7-a2a4-d6ef | V1.0 for Public consultation version | 2 | 17 | 2 | - | 2014-12-07 12:51:41 | Herve MELJAC | EUR | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical, legal and operating permit constraints. | SGUs ability to execute can be impaired by constraints not limited to technical. |  |  | legal |  |  |  | Non-confidential
0005-e4d2-db50-e70a-f9e4 | V1.0 for Public consultation version | 2 | 17 | 2 | - | 2014-11-28 15:52:12 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall, as far as possible execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | The Power Flow of Wind farms, Solar farms or heat process coupled generation etc. may not be able to follow the set-point defined by the TSO. |  |  | technical |  |  |  | Non-confidential
0005-4869-5e6b-c803-6fb7 | V1.0 for Public consultation version | 2 | 17 | 2 | - | 2014-12-08 19:51:15 | Roland Tual | SEDC | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | [8 empty] | confidential
0005-e4d1-75cf-4a58-6ea8 | V1.0 for Public consultation version | 2 | 17 | 2 | - | 2014-12-08 20:11:08 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | The TSO may require that a consumer maintains their consumption level - therefore it is not allowed to turn off its oven, lights, heating system, etc. This requirement is not physically possible and even if it were possible, it would be too costly for households to implement. It could also raise safety issues with regard to devices. This provision is thus unacceptable without any proper structures in place for consumer protection. |  |  | legal |  |  |  | Non-confidential
0005-bdd5-c3c1-2797-f95c | V1.0 for Public consultation version | 2 | 17 | 2 | - | 2014-12-08 16:38:47 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. The financial consequences of the modification of the set-point have to be described in a contract, agreed upfront. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | The Power Flow of Wind farms, Solar farms or heat process coupled generation etc. may not be able to follow the set-point defined by the TSO. It happens often that a TSO imposes new set-points to avoid congestion. The financial consequences should be known upfront and accepted by both parties as soon as possible. | [6 empty] | Non-confidential
0005-e495-102e-0ea8-2f0f | V1.0 for Public consultation version | 2 | 17 | 2 | - | 2014-12-08 17:15:45 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users connected to the Transmission System shall execute the instructions given directly by the TSO and Significant Grid Useres connected to the Disrtribution System shall execute the instructions given indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Instructions to the SGUs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). |  |  | technical |  |  |  | Non-confidential
0005-96c5-00ac-0f0c-5586 | V1.0 for Public consultation version | 2 | 17 | 2 | - | 2014-12-08 17:15:47 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall, as far as possible execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | The Power Flow of Wind farms, Solar farms or heat process coupled generation etc. may not be able to follow the set-point defined by the TSO. |  |  | technical |  |  |  | Non-confidential
0005-bdc2-8d30-ea2a-4dc2 | V1.0 for Public consultation version | 2 | 17 | 2 | - | 2014-11-28 15:52:12 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users connected to the Transmission System shall execute the instructions given directly by the TSO and Significant Grid Useres connected to the Disrtribution System shall execute the instructions given indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Instructions to the SGUs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2309 | V1.0 for Public consultation version | 2 | 17 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users connected to the Transmission System shall execute the instructions given directly by the TSO and Significant Grid Useres connected to the Disrtribution System shall execute the instructions given indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Instructions to the SGUs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). In addition to the TSO being entitled to define a set point, doesn't the SGU have a requirement to comply within a reasonable timeframe - what mechanism will be used to do this? |  |  | Technical
0005-e495-5e7a-d54d-2035 | V1.0 for Public consultation version | 2 | 17 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users connected to the Transmission System shall execute the instructions given directly by the TSO and Significant Grid Useres connected to the Disrtribution System shall execute the instructions given indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Instructions to the SGUs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS).
0005-e495-5e7a-d54d-2036 | V1.0 for Public consultation version | 2 | 17 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. The financial consequences of the modification of the set-point have to be described in a contract, agreed upfront. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | The Power Flow of Wind farms, Solar farms or heat process coupled generation etc. may not be able to follow the set-point defined by the TSO. It happens often that a TSO imposes new set-points to avoid congestion. The financial consequences should be known upfront and accepted by both parties as soon as possible.
0005-e495-5e7a-d54d-2176 | V1.0 for Public consultation version | 2 | 17 | 2 |  | 2014-12-08 21:33 | AG | RWE | final | The TSO shall define the conditions under which the On Load Tap Changer shall block according to Article 20(4) [NC DC], including at least: | Each TSO shall define, subject to NRA approval, the conditions under which the On Load Tap Changer of distribution transformers shall block according to Article 20(4) [NC DC], including at least: | Make clear which OLTS are being referred to. Also there must be approval of the set point (and any changes to the set point). |  |  | Technical | Editorial
0005-e495-5e7a-d54d-2258 | V1.0 for Public consultation version | 2 | 17 | 2 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. |  | The TSO may require that a consumer maintains their consumption level - therefore they are not allowed to turn off their stove, lights, heating. This stipulation is not physically possible and potentially abusive. Smaller consumers and generators should not be included here - this is unacceptable. (If small consumers/generators are not under consideration for this measure - why are they included in the code?)
0005-e495-5e7a-d54d-1794 | V1.0 for Public consultation version | 2 | 17 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall be entitled to define an Active Power set-point which the Significant Grid Users shall maintain. | Each TSO shall be entitled to define, SUBJECT TO NRA APPROVAL, an Active Power set-point which the Significant Grid Users shall maintain. | There must be NRA approval of the set point (and any changes to that set point).
0005-e495-5e7a-d54d-1796 | V1.0 for Public consultation version | 2 | 17 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Significant Grid Users shall execute the instructions given directly by the TSO or indirectly through DSOs, concerning the power set-point of their Power Generating Modules or Demand Facilities IN ACCORDANCE WITH THE SERVICE PROCURED BY THE RELEVANT NETWORK OPERATOR or Closed Distribution Networks providing Demand Side Response, while respecting their technical constraints. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-1798 | V1.0 for Public consultation version | 2 | 17 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Significant Grid Users shall execute the instructions given directly… | Significant Grid Users shall execute the instruction(s) given directly… | Typo
0005-96c5-11a4-a2f9-9193 | V1.0 for Public consultation version | 2 | 17 | 3 | - | 2014-12-04 14:17:46 | Dekinderen Eric | Genrator company | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power | Each TSO shall be entitled to disconnect Significant Grid Users and type A & B Power Generating Modules to cease Active Power | No communication channels are installed for the majority of Tpe A & type B PGMs. This is not coherent with the basic principle "RfG is only for NEW installations" |  |  | technical |  |  |  | Non-confidential
0005-968a-a4a0-e7d2-cdac | V1.0 for Public consultation version | 2 | 17 | 3 | - | 2014-11-28 15:52:13 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users connected to the Transmission System directly and Significant Grid Users connected to the Distribution System indirectly through the DSOs and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], indirectly through DSOs. | Instructions to the SGUs connected to the Distribution Systems and new type A PGMs only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Concerning feasibility for type A PGMs, see remark art. 8.4. |  |  | technical |  |  |  | Non-confidential
0005-e4a9-855d-c867-4449 | V1.0 for Public consultation version | 2 | 17 | 3 | - | 2014-12-08 19:51:15 | Roland Tual | SEDC | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | [8 empty] | confidential
0005-9675-3721-2ab7-f532 | V1.0 for Public consultation version | 2 | 17 | 3 | - | 2014-12-08 16:38:49 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users connected to the Transmission System directly and Significant Grid Users connected to the Distribution System indirectly through the DSOs and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], indirectly through DSOs. | Instructions to the SGUs connected to the Distribution Systems and new type A PGMs only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Concerning feasibility for type A PGMs, see remark art. 8.4. | [6 empty] | Non-confidential
0005-e4bd-4e90-0ea8-b604 | V1.0 for Public consultation version | 2 | 17 | 3 | - | 2014-12-08 17:15:49 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users connected to the Transmission System directly and Significant Grid Users connected to the Distribution System indirectly through the DSOs and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], indirectly through DSOs. | Instructions to the SGUs connected to the Distribution Systems and new type A PGMs only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Concerning feasibility for type A PGMs, see remark art. 8.4. |  |  | technical |  |  |  | Non-confidential
0005-6fa1-7771-258b-13dd | V1.0 for Public consultation version | 2 | 17 | 3 | - | 2014-12-08 17:01:19 | Jasmina PIERRE | EdF | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. This disconnection should not compromise others critical considerations, such as safety conditions of high priority significant grid users. | EDF underlines such a disconnection can compromise safety conditions from grids users installations (including nuclear plants). ENTSO-E proposal implies that grid security prevails over any others critical considerations, including nuclear safety, which is not acceptable. It is essential that TSO takes into account the specific needs of specific grid users regarding the conditions for their disconnection and re-energizing. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2310 | V1.0 for Public consultation version | 2 | 17 | 3 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users connected to the Transmission System directly and Significant Grid Users connected to the Distribution System indirectly through the DSOs and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Instructions to the SGUs connected to the Distribution Systems and new type A PGMs only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). DSOs are convinced that new type A PGMs should not be part of the NC ER, cf. explanation art. 8§4. |  |  | Technical
0005-e495-5e7a-d54d-2037 | V1.0 for Public consultation version | 2 | 17 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users connected to the Transmission System directly and Significant Grid Users connected to the Distribution System indirectly through the DSOs and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], indirectly through DSOs. | Instructions to the SGUs connected to the Distribution Systems and new type A PGMs only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Concerning feasibility for type A PGMs, see remark art. 8.4.
0005-e495-5e7a-d54d-2177 | V1.0 for Public consultation version | 2 | 17 | 3 |  | 2014-12-08 21:33 | Wilch | RWE | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | Each TSO shall be entitled to disconnect Significant Grid Users connected to the Transmission System directly and Significant Grid Users connected to the Distribution System indirectly through the DSOs and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], indirectly through DSOs. | Instructions to the SGUs connected to the Distribution Systems and new type A PGMs only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Has this been considered practically? Also where is the 'reverse@ instruction? (i.e. the procedure to instruct the disconnected parties to re-connect). |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2259 | V1.0 for Public consultation version | 2 | 17 | 3 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. |  | The ability to disconnect will require to install a direct communication line (€25,000) and automated controls between themselves and the DSO. This will create prohibitive costs to consumers and to DSOs. Will the TSO be paying for these costs? Will anyone ask the consumer's permission before requiring this? (If small consumers/generators are not under consideration for this measure - why are they included?)
0005-e495-5e7a-d54d-1799 | V1.0 for Public consultation version | 2 | 17 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall be entitled to disconnect Significant Grid Users and to instruct new type A Power Generating Modules to cease Active Power, in accordance with Article 8(1)(f) [NC RFG], directly or indirectly through DSOs. | xyz | Has the practicality of issuing instructions to new Type A generators been assessed. Also where is the ‘reverse’ instruction? Having been instructed to ‘disconnect’ where is the procedure set out in the E&R NC to instruct those parties disconnected to re-connect?
0005-e495-5e7a-d54d-2038 | V1.0 for Public consultation version | 2 | 17 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used.
0005-968a-6602-e962-f2d6 | V1.0 for Public consultation version | 2 | 17 | - | - | 2014-11-28 15:52:14 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | legal |  |  |  | Non-confidential
0005-bd85-4edd-4b84-8a2c | V1.0 for Public consultation version | 2 | 17 | - | - | 2014-12-08 20:11:08 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | Duplication of communication channels: significants grid users will receive orders directly from TSOs or indirectly through DSOs. This would imply duplication of communication channels for consumers whose installation costs would be prohibitive. Such requirement is not acceptable for residential consumers. |  |  | legal |  |  |  | Non-confidential
0005-e4a9-4eaf-298b-1d9f | V1.0 for Public consultation version | 2 | 17 | - | - | 2014-12-08 16:38:51 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used. | [6 empty] | Non-confidential
0005-48a5-279e-0ea8-192f | V1.0 for Public consultation version | 2 | 17 | - | - | 2014-12-08 17:15:50 | Paul Doyle | ESB Generation & Wholesale Markets | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | legal |  |  |  | Non-confidential
0005-bdc2-3f10-e836-ce7a | V1.0 for Public consultation version | 2 | 18 | 1 | - | 2014-11-28 15:52:15 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | in case of absence of Responsibility Area Adequacy in day-ahead and intraday, as defined in Article 49 [NC OPS], provided the TSO activated all available Balancing Energy or taken into account all available Balancing Energy at the moment of absence of Adequacy, within its Coordinated Balancing Area, according to Article 39 [NC EB]. | in case of absence of Responsibility Area Adequacy in day-ahead and intraday, as defined in Article 49 [NC OPS], provided the TSO activated all available Balancing Energy or and taken into account all available Balancing Energy at the moment of absence of Adequacy, within its Coordinated Balancing Area, according to Article 39 [NC EB]. | It is not sufficient to either activate balancing energy or take the energy into account. |  |  | technical |  |  |  | Non-confidential
0005-2159-9ced-29ef-cc41 | V1.0 for Public consultation version | 2 | 18 | 1 | - | 2014-12-08 16:38:53 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | in case of absence of Responsibility Area Adequacy in day-ahead and intraday, as defined in Article 49 [NC OPS], provided the TSO activated all available Balancing Energy or taken into account all available Balancing Energy at the moment of absence of Adequacy, within its Coordinated Balancing Area, according to Article 39 [NC EB]. | in case of absence of Responsibility Area Adequacy in day-ahead and intraday, as defined in Article 49 [NC OPS], provided the TSO activated all available Balancing Energy or and taken into account all available Balancing Energy at the moment of absence of Adequacy, within its Coordinated Balancing Area, according to Article 39 [NC EB]. | It is not sufficient to either activate balancing energy or take the energy into account. | [6 empty] | Non-confidential
0005-4891-102e-0bec-f3ca | V1.0 for Public consultation version | 2 | 18 | 1 | - | 2014-12-08 17:15:52 | Paul Doyle | ESB Generation & Wholesale Markets | final | in case of absence of Responsibility Area Adequacy in day-ahead and intraday, as defined in Article 49 [NC OPS], provided the TSO activated all available Balancing Energy or taken into account all available Balancing Energy at the moment of absence of Adequacy, within its Coordinated Balancing Area, according to Article 39 [NC EB]. | in case of absence of Responsibility Area Adequacy in day-ahead and intraday, as defined in Article 49 [NC OPS], provided the TSO activated all available Balancing Energy or and taken into account all available Balancing Energy at the moment of absence of Adequacy, within its Coordinated Balancing Area, according to Article 39 [NC EB]. | It is not sufficient to either activate balancing energy or take the energy into account. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2039 | V1.0 for Public consultation version | 2 | 18 | 1 | a | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | in case of absence of Responsibility Area Adequacy in day-ahead and intraday, as defined in Article 49 [NC OPS], provided the TSO activated all available Balancing Energy or taken into account all available Balancing Energy at the moment of absence of Adequacy, within its Coordinated Balancing Area, according to Article 39 [NC EB]. | in case of absence of Responsibility Area Adequacy in day-ahead and intraday, as defined in Article 49 [NC OPS], provided the TSO activated all available Balancing Energy or and taken into account all available Balancing Energy at the moment of absence of Adequacy, within its Coordinated Balancing Area, according to Article 39 [NC EB]. | It is not sufficient to either activate balancing energy or take the energy into account.
0005-9675-9cec-0f0c-a84d | V1.0 for Public consultation version | 2 | 18 | 2 | - | 2014-12-08 17:15:54 | Paul Doyle | ESB Generation & Wholesale Markets | final | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from, in coordination with the relevant network operator, any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. | Influencing of a significant grid user must always be done in coordination with relevant network operator. |  |  | technical |  |  |  | Non-confidential
0005-48a5-3720-0cb4-7226 | V1.0 for Public consultation version | 2 | 18 | 2 | - | 2014-12-08 17:15:55 | Paul Doyle | ESB Generation & Wholesale Markets | final | The Balancing Service Provider and the Significant Grid User shall make available to the TSO all its Active Power, provided it was not already activated through any Balancing mechanism. | The Balancing Service Provider and the Significant Grid User shall make available to the TSO all its Active Power, provided it was not already activated through any Balancing mechanism or limited by the relevant system operator. | Limits of the connecting system operator must be respected even in defence situations, as otherwise we take the risk of losing the whole generator or a subpart of a grid. |  |  | technical |  |  |  | Non-confidential
0005-6f65-c3dd-c993-a6c6 | V1.0 for Public consultation version | 2 | 18 | 2 | - | 2014-12-08 19:51:15 | Roland Tual | SEDC | final | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. | [8 empty] | confidential
0005-486a-0860-ea2a-6dd6 | V1.0 for Public consultation version | 2 | 18 | 2 | - | 2014-11-28 15:52:16 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from, in coordination with the relevant network operator, any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. | Influencing of a significant grid user must always be done in coordination with relevant network operator. |  |  | technical |  |  |  | Non-confidential
0005-2196-a4a0-e8fe-3022 | V1.0 for Public consultation version | 2 | 18 | 2 | - | 2014-11-28 15:52:16 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The Balancing Service Provider and the Significant Grid User shall make available to the TSO all its Active Power, provided it was not already activated through any Balancing mechanism. | The Balancing Service Provider and the Significant Grid User shall make available to the TSO all its Active Power, provided it was not already activated through any Balancing mechanism or limited by the relevant system operator. | Limits of the connecting system operator must be respected even in defence situations, as otherwise we take the risk of losing the whole generator or a subpart of a grid. |  |  | technical |  |  |  | Non-confidential
0005-216d-3956-107a-c271 | V1.0 for Public consultation version | 2 | 18 | 2 | - | 2014-12-03 11:20:06 | AXPO Group |  | final | The Balancing Service Provider and the Significant Grid User shall make available to the TSO all its Active Power, provided it was not already activated through any Balancing mechanism. | If feasible, the Balancing Service Provider and the Significant Grid User shall make available to the TSO Active Power, provided it was not already activated through any Balancing mechanism. | Problematic is the term "... shall make available to the TSO all its Active Power...". For a System Defence Plan this measure goes too far. Within this plan the control of the power station must retain entirely with the operator of the power station. |  |  | legal |  |  |  | Non-confidential
0005-6f65-9cb1-298b-7e02 | V1.0 for Public consultation version | 2 | 18 | 2 | - | 2014-12-08 16:38:55 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from, in coordination with the relevant network operator, any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. | Influencing of a significant grid user must always be done in coordination with relevant network operator. | [6 empty] | Non-confidential
0005-487d-0223-2653-111a | V1.0 for Public consultation version | 2 | 18 | 2 | - | 2014-12-08 17:01:20 | Jasmina PIERRE | EdF | final | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. The Balancing Service Provider and the Significant Grid User shall make available to the TSO all its Active Power, provided it was not already activated through any Balancing mechanism. | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider, while respecting their technical constraints. The Balancing Service Provider and the Significant Grid User shall make available to the TSO all its Active Power, provided it was not already activated through any Balancing mechanism. | It is essential all the instructions given by the TSO for execution respect the respective technical constraints and minimize related impacts for grid users. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2311 | V1.0 for Public consultation version | 2 | 18 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. The Balancing Service Provider and the Significant Grid User shall make available to the TSO all its Active Power, provided it was not already activated through any Balancing mechanism. | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and - in coordination with the relevant Network Operator - from any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. The Balancing Service Provider and the Significant Grid User shall make available to the TSO all its Active Power, provided it was not already activated through any Balancing mechanism or limited by the Relevant System Operator. | Influencing of a significant grid user must always be done in coordination with relevant network operator. Limits of the connecting system operator must be respected even in defence situations, as otherwise we take the risk of losing the whole generator or a subpart of a grid. |  |  | Technical
0005-e495-5e7a-d54d-2040 | V1.0 for Public consultation version | 2 | 18 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from, in coordination with the relevant network operator, any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. | Influencing of a significant grid user must always be done in coordination with relevant network operator.
0005-e495-5e7a-d54d-2041 | V1.0 for Public consultation version | 2 | 18 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The Balancing Service Provider and the Significant Grid User shall make available to the TSO all its Active Power, provided it was not already activated through any Balancing mechanism. | The Balancing Service Provider and the Significant Grid User shall make available to the TSO all its Active Power, provided it was not already activated through any Balancing mechanism or limited by the relevant system operator. | Limits of the connecting system operator must be respected even in defence situations, as otherwise we take the risk of losing the whole generator or a subpart of a grid.
0005-e495-5e7a-d54d-2260 | V1.0 for Public consultation version | 2 | 18 | 2 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. |  | If a grid user does not have an agreement with a BRP, that may well be because they do not want to participate in DR under certain circumstances! Will the TSOs will now be able to force them to participate? Again this leaves this code open to abuse. (If small consumers/generators are not under consideration for this measure - why are they included?)
0005-e495-5e7a-d54d-1801 | V1.0 for Public consultation version | 2 | 18 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | The TSO in the situation referred in paragraph 1(a) shall be entitled to request assistance for Active Power from Balancing Service Providers and from any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. | The TSO in the situation referred in paragraph 1(a) shall be entitled to request AND PROCURE assistance for Active Power from Balancing Service Providers and from any Significant Grid User connected in its LFC Area that does not have an agreement with a Balancing Service Provider. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-1803 | V1.0 for Public consultation version | 2 | 18 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | The TSO in the situations referred in paragraph 1(a) and (b) shall be entitled to request assistance for Active Power from all neighbouring TSOs, irrespective of their participation into its Coordinated Balancing Area. | The TSO in the situations referred in paragraph 1(a) and (b) shall be entitled to request assistance for Active Power from all neighbouring TSOs, irrespective of their participation into its Coordinated Balancing Area AND THE COSTS INCURRED BY THE NEIGHBOURING TSOS OF DOING SO SHALL BE BORN BY THE REQUESTING TSO. | There needs to be a clear reference to cost recovery to avoid the cost of providing support to another TSO in an Emergency, Black Start or Restoration State falling upon consumers in another TSO’s area
0005-e495-5e7a-d54d-1805 | V1.0 for Public consultation version | 2 | 18 | 4 | C | 2014-12-08 13:31 | Garth Graham | SSE |  | be entitled to request assistance for Active Power from its Balancing Service Providers and to any Significant Grid User connected in its Responsibility Area that does not have an agreement with a Balancing Service Provider, in order to provide the corresponding power to the requesting TSO. | be entitled to request AND PROCURE assistance for Active Power from its Balancing Service Providers and to any Significant Grid User connected in its Responsibility Area that does not have an agreement with a Balancing Service Provider, in order to provide the corresponding power to the requesting TSO. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-48a5-9e62-a3c1-5523 | V1.0 for Public consultation version | 2 | 18 | 5 | - | 2014-12-04 14:20:11 | Dekinderen Eric | Genrator company | final | Assistance for Active Power shall be firm, unless the TSO providing the said assistance enters into Emergency or Blackout States | Assistance for Active Power shall be firm, duly respecting contracted generation capacity or other ressources for adequacy purposes with the neighbouring TSO. | Cross border CRM must be granted in emergency conditions. If not, "Cross border CRM" will be impossible |  |  | legal |  |  |  | Non-confidential
0005-bd85-1010-0d7c-9da1 | V1.0 for Public consultation version | 2 | 18 | 5 | - | 2014-12-08 17:15:57 | Paul Doyle | ESB Generation & Wholesale Markets | final | Assistance for Active Power shall be firm, unless the TSO providing the said assistance enters into Emergency or Blackout States. |  | If this clause remains, CRM across borders is not possible. |  |  | legal |  |  |  | Non-confidential
0005-48a6-8d4e-e9c6-1425 | V1.0 for Public consultation version | 2 | 18 | 5 | - | 2014-11-28 15:52:17 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Assistance for Active Power shall be firm, unless the TSO providing the said assistance enters into Emergency or Blackout States. | Assistance for Active Power shall be firm, unless the TSO providing the said assistance enters into Emergency or Blackout States. In whatever circumstances, assistance will respect CRM comitments. | Energy contracted under a CRM should be delivered, even if its delivery may move the system hosting the CRM resource into the alert or emergency state. Otherwise CRMs in foreign system are not reliable, and CRM trading is de facto not feasible. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2312 | V1.0 for Public consultation version | 2 | 18 | 5 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Assistance for Active Power shall be firm, unless the TSO providing the said assistance enters into Emergency or Blackout States. | no text proposal. | Iwhat is the meaning of 'shall be firm' ? |  |  | Technical
0005-e495-5e7a-d54d-2042 | V1.0 for Public consultation version | 2 | 18 | 5 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Assistance for Active Power shall be firm, unless the TSO providing the said assistance enters into Emergency or Blackout States. | Assistance for Active Power shall be firm, unless the TSO providing the said assistance enters into Emergency or Blackout States. In whatever circumstances, assistance will respect CRM comitments. | Energy contracted under a CRM should be delivered, even if its delivery may move the system hosting the CRM resource into the alert or emergency state. Otherwise CRMs in foreign system are not reliable, and CRM trading is de facto not feasible.
0005-e495-5e7a-d54d-2043 | V1.0 for Public consultation version | 2 | 18 | 6 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic solutions will be used.
0005-e495-5e7a-d54d-2178 | V1.0 for Public consultation version | 2 | 18 | 6 |  | 2014-12-08 21:33 | AG | RWE | final | Add new paragraph. | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | There needs to be a clear reference to cost recovery to avoid the costs of providing support to another TSO in an Emergency, Black Start or Restoration State falling upon consumers in another TSO's area. |  |  | Technical | Fundamental
0005-e4bd-ade5-2527-1206 | V1.0 for Public consultation version | 2 | 18 | - | - | 2014-12-08 17:01:20 | Jasmina PIERRE | EdF | final | (new) | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | It is essential that TSOs shall bear all the costs incurred by grid users for (i) the actions/measures carried out upon TSO request; (ii) additional and redundant (voice) communication channels; (iii) measures to ensure the extended (>24h) availability of critical tools and facilities and (iv) for “compliance testing” of equipment and procedures required to ensure reliability of prepared System Defense and Restoration Plans. “Overall cost recovery” is required to incentivize TSOs to pursue cost overall efficiency and to prevent from any discrimination between grid users in competition through the markets, in accordance with principles defined in “general conditions” chapter (article 3.3.c). |  |  | technical |  |  |  | Non-confidential
0005-2195-4ecc-0cb4-941b | V1.0 for Public consultation version | 2 | 18 | - | - | 2014-12-08 17:15:58 | Paul Doyle | ESB Generation & Wholesale Markets | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic solutions will be used. |  |  | legal |  |  |  | Non-confidential
0005-2196-db32-e9c6-c0e8 | V1.0 for Public consultation version | 2 | 18 | - | - | 2014-11-28 15:52:34 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic solutions will be used. |  |  | legal |  |  |  | Non-confidential
0005-9675-297a-1336-6c14 | V1.0 for Public consultation version | 2 | 18 | - | - | 2014-12-03 11:20:07 | AXPO Group |  | final | missing paragraph | see Comment | There is need for a new subpoint 6. The costs generated by the request for assistance for active power shall be compensated by the TSO. |  |  | legal |  |  |  | Non-confidential
0005-6f65-5e6c-0bec-b0b5 | V1.0 for Public consultation version | 2 | 19 | 1 | - | 2014-12-08 17:29:55 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected, directly or indirectly through DSOs, when necessary to prevent any propagation or worsening of an Emergency State, in order to: a) solve overloads or under Voltage situations; or b) solve situations in which assistance for Active Power according to Article 18 has been requested but is not sufficient to ensure Adequacy on its Responsibility Area in D-1 and intraday as defined in Article 49 [NC OPS], leading to a risk of Frequency deterioration in the Synchronous Area. | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected in coordination with the DSO if relevant, directly for Demand connected to the Transmission System or indirectly through DSOs for Demand connected to the Distribution System, when necessary to prevent any propagation or worsening of an Emergency State, in order to: a) solve overloads or under Voltage situations; or b) solve situations in which assistance for Active Power according to Article 18 has been requested but is not sufficient to ensure Adequacy on its Responsibility Area in D-1 and intraday as defined in Article 49 [NC OPS], leading to a risk of Frequency deterioration in the Synchronous Area. | Manual disconnection of SGUs connected to the Distribution Systems only by the DSO. Cf. DSOs position that all actions on the Distribution system should be agreed with and executed by the DSOs. |  |  | technical |  |  |  | Non-confidential
0005-968a-7d72-e8fe-770d | V1.0 for Public consultation version | 2 | 19 | 1 | - | 2014-11-28 15:52:35 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected, directly or indirectly through DSOs, when necessary to prevent any propagation or worsening of an Emergency State, in order to: a) solve overloads or under Voltage situations; or b) solve situations in which assistance for Active Power according to Article 18 has been requested but is not sufficient to ensure Adequacy on its Responsibility Area in D-1 and intraday as defined in Article 49 [NC OPS], leading to a risk of Frequency deterioration in the Synchronous Area. | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected in coordination with the DSO if relevant, directly for Demand connected to the Transmission System or indirectly through DSOs for Demand connected to the Distribution System, when necessary to prevent any propagation or worsening of an Emergency State, in order to: a) solve overloads or under Voltage situations; or b) solve situations in which assistance for Active Power according to Article 18 has been requested but is not sufficient to ensure Adequacy on its Responsibility Area in D-1 and intraday as defined in Article 49 [NC OPS], leading to a risk of Frequency deterioration in the Synchronous Area. | Manual disconnection of SGUs connected to the Distribution Systems only by the DSO. Cf. DSOs position that all actions on the Distribution system should be agreed with and executed by the DSOs. |  |  | technical |  |  |  | Non-confidential
0005-6fa1-75cf-4c4b-b5d8 | V1.0 for Public consultation version | 2 | 19 | 1 | - | 2014-12-08 20:11:10 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | Duplication of communication channels: significants grid users will receive orders directly from TSOs or indirectly through DSOs. This would imply duplication of communication channels for consumers whose installation costs would be prohibitive. Such requirement is not acceptable for residential consumers. |  |  | legal |  |  |  | Non-confidential
0005-6f8d-2998-12d2-424d | V1.0 for Public consultation version | 2 | 19 | 1 | - | 2014-12-03 11:20:07 | AXPO Group |  | final | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected, directly or indirectly through DSOs, when necessary to prevent any propagation or worsening of an Emergency State, in order to: … | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected when necessary to prevent any propagation or worsening of an Emergency State, in order to: … | The direct disconnection of load by the TSO is not acceptable. Load on the distribution system is detached by and only by the DSO. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2313 | V1.0 for Public consultation version | 2 | 19 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected, directly or indirectly through DSOs, when necessary to prevent any propagation or worsening of an Emergency State, in order to: a) solve overloads or under Voltage situations; or b) solve situations in which assistance for Active Power according to Article 18 has been requested but is not sufficient to ensure Adequacy on its Responsibility Area in D-1 and intraday as defined in Article 49 [NC OPS], leading to a risk of Frequency deterioration in the Synchronous Area. | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected in coordination with the DSO if relevant, directly for Demand connected to the Transmission System or indirectly through DSOs for Demand connected to the Distribution System, when necessary to prevent any propagation or worsening of an Emergency State, in order to: a) solve overloads or under Voltage situations; or b) solve situations in which assistance for Active Power according to Article 18 has been requested but is not sufficient to ensure Adequacy on its Responsibility Area in D-1 and intraday as defined in Article 49 [NC OPS], leading to a risk of Frequency deterioration in the Synchronous Area. | Manual disconnection of Demand connected to the Distribution Systems only by the DSO. Cf. DSOs position that all actions on the Distribution system should be agreed with and executed by the DSOs. |  |  | Technical
0005-e495-5e7a-d54d-2044 | V1.0 for Public consultation version | 2 | 19 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected, directly or indirectly through DSOs, when necessary to prevent any propagation or worsening of an Emergency State, in order to: a) solve overloads or under Voltage situations; or b) solve situations in which assistance for Active Power according to Article 18 has been requested but is not sufficient to ensure Adequacy on its Responsibility Area in D-1 and intraday as defined in Article 49 [NC OPS], leading to a risk of Frequency deterioration in the Synchronous Area. | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected in coordination with the DSO if relevant, directly for Demand connected to the Transmission System or indirectly through DSOs for Demand connected to the Distribution System, when necessary to prevent any propagation or worsening of an Emergency State, in order to: a) solve overloads or under Voltage situations; or b) solve situations in which assistance for Active Power according to Article 18 has been requested but is not sufficient to ensure Adequacy on its Responsibility Area in D-1 and intraday as defined in Article 49 [NC OPS], leading to a risk of Frequency deterioration in the Synchronous Area. | Manual disconnection of SGUs connected to the Distribution Systems only by the DSO. Cf. DSOs position that all actions on the Distribution system should be agreed with and executed by the DSOs.
0005-e495-5e7a-d54d-2179 | V1.0 for Public consultation version | 2 | 19 | 1 |  | 2014-12-08 21:33 | Wilch | RWE | final | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected, directly or indirectly through DSOs, when necessary to prevent any propagation or worsening of an Emergency State, in order to: a) solve overloads or under Voltage situations; or b) solve situations in which assistance for Active Power according to Article 18 has been requested but is not sufficient to ensure Adequacy on its Responsibility Area in D-1 and intraday as defined in Article 49 [NC OPS], leading to a risk of Frequency deterioration in the Synchronous Area. | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected in coordination with the DSO if relevant, directly for Demand connected to the Transmission System or indirectly through DSOs for Demand connected to the Distribution System, when necessary to prevent any propagation or worsening of an Emergency State, in order to: a) solve overloads or under Voltage situations; or b) solve situations in which assistance for Active Power according to Article 18 has been requested but is not sufficient to ensure Adequacy on its Responsibility Area in D-1 and intraday as defined in Article 49 [NC OPS], leading to a risk of Frequency deterioration in the Synchronous Area. | Manual disconnection of SGUs connected to the Distribution Systems only by the DSO. Cf. DSOs position that all actions on the Distribution system should be agreed with and executed by the DSOs. |  |  | Technical | Fundamental
0005-4869-373e-0f70-96b3 | V1.0 for Public consultation version | 2 | 19 | 2 | - | 2014-12-08 17:16:49 | Paul Doyle | ESB Generation & Wholesale Markets | final | The TSO shall notify to DSOs the amount of Demand to be disconnected on their distribution systems. Each DSO shall disconnect the notified amount of Demand, without undue delay. | The TSO shall notify to DSOs directly connected to the transmission system the amount of Demand to be disconnected on their distribution systems. Each DSO shall disconnect the notified amount of Demand including indirectly connected DSOs, without undue delay. | To work conform the framework of cascading measures, each System Operator shall notify only its own customers |  |  | technical |  |  |  | Non-confidential
0005-96b2-a4a0-e9c6-6349 | V1.0 for Public consultation version | 2 | 19 | 2 | - | 2014-11-28 15:52:36 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The TSO shall notify to DSOs the amount of Demand to be disconnected on their distribution systems. Each DSO shall disconnect the notified amount of Demand, without undue delay. | The TSO shall notify to DSOs directly connected to the transmission system the amount of Demand to be disconnected on their distribution systems. Each DSO shall disconnect the notified amount of Demand including indirectly connected DSOs, without undue delay. | To work conform the framework of cascading measures, each System Operator shall notify only its own customers |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2314 | V1.0 for Public consultation version | 2 | 19 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | The TSO shall notify to DSOs the amount of Demand to be disconnected on their distribution systems. Each DSO shall disconnect the notified amount of Demand, without undue delay. | The TSO shall notify to DSOs directly connected to the transmission system the amount of Demand to be disconnected on their distribution systems. Each DSO shall disconnect the notified amount of Demand, after instruction. without undue delay. | To keep within the framework of cascading measures, each System Operator shall notify only underlying SOs. |  |  | Technical
0005-e495-5e7a-d54d-2045 | V1.0 for Public consultation version | 2 | 19 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The TSO shall notify to DSOs the amount of Demand to be disconnected on their distribution systems. Each DSO shall disconnect the notified amount of Demand, without undue delay. | The TSO shall notify to DSOs directly connected to the transmission system the amount of Demand to be disconnected on their distribution systems. Each DSO shall disconnect the notified amount of Demand including indirectly connected DSOs, without undue delay. | To work conform the framework of cascading measures, each System Operator shall notify only its own customers
0005-e495-5e7a-d54d-2180 | V1.0 for Public consultation version | 2 | 19 | 2 |  | 2014-12-08 21:33 | Wilch | RWE | final | The TSO shall notify to DSOs the amount of Demand to be disconnected on their distribution systems. Each DSO shall disconnect the notified amount of Demand, without undue delay. | The TSO shall notify to DSOs directly connected to the transmission system the amount of Demand to be disconnected on their distribution systems. Each DSO shall disconnect the notified amount of Demand including indirectly connected DSOs, without undue delay. | Each System Operator shall notify solely its own customers. | 1 | 2 | Technical | Fundamental
0005-e495-5e7a-d54d-2046 | V1.0 for Public consultation version | 2 | 19 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used.
0005-e495-5e7a-d54d-2181 | V1.0 for Public consultation version | 2 | 19 | 3 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Add new paragraph. | Each TSO will notify the NRA without delay the amount of demand to be manually disconnected, directly or indirectly through DSOs it has determined in accordance with paragraph (1) above. | It is important, in the interest of openess and transparency that anything to be determined by the TSO(s) is notified to the NRA(s). |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1807 | V1.0 for Public consultation version | 2 | 19 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Xyz | THE TSO WILL NOTIFY THE NRA WITHOUT DELAY THE AMOUNT OF DEMAND TO BE MANUALLY DISCONNECTED, DIRECTLY OR INDIRECTLY THROUGH DSOS IT HAS DETERMINED IN ACCORDANCE WITH (1) ABOVE. | It Is important, in the interest of openness and transparency, that anything to be determined by the TSO(s) is notified to the NRA(s).
0005-e495-5e7a-d54d-2182 | V1.0 for Public consultation version | 2 | 19 | 6 |  | 2014-12-08 21:33 | AG | RWE | final | Add new paragraph. | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | There needs to be a clear reference to cost recovery to avoid the costs of providing support to another TSO in an Emergency, Black Start or Restoration State falling upon consumers in another TSO's area. |  |  | Technical | Fundamental
0005-bdd5-76c0-3acc-3435 | V1.0 for Public consultation version | 2 | 19 | - | - | 2014-12-05 10:52:14 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected, directly or indirectly through DSOs, when necessary to prevent any propagation or worsening of an Emergency State, in order to: | Each TSO shall be entitled to determine an amount of Demand to be manually disconnected, directly or indirectly through DSOs, as defined in Article 8, … | the measures should be argreed with the relevant DSO according to the procedure described in article 8.1. | 1 | 3 | legal |  |  |  | Non-confidential
0005-bdad-75a1-7f7e-c4da | V1.0 for Public consultation version | 2 | 19 | - | - | 2014-12-08 16:38:51 | Rothermann Philippe |  | final |  |  | Which criterion have the DSO to apply for manual demand disconnection? Non-discriminatory or technical best solution? | [6 empty] | Non-confidential
0005-487d-5fc5-2397-70d8 | V1.0 for Public consultation version | 2 | 19 | - | - | 2014-12-08 17:01:20 | Jasmina PIERRE | EdF | final | (new) | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | It is essential that TSOs shall bear all the costs of grid users incurred by requested actions from TSO. “Overall cost recovery” is required to incentivize TSOs to pursue cost overall efficiency and to prevent from any discrimination between grid users in competition through the markets, in accordance with principles defined in “general conditions” chapter (article 3.3.c). |  |  | technical |  |  |  | Non-confidential
0005-48a5-75dc-0e44-8b1b | V1.0 for Public consultation version | 2 | 19 | - | - | 2014-12-08 17:16:50 | Paul Doyle | ESB Generation & Wholesale Markets | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | legal |  |  |  | Non-confidential
0005-215a-2f52-e8fe-28c1 | V1.0 for Public consultation version | 2 | 19 | - | - | 2014-11-28 15:52:37 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Add a new article! The costs must be addressed to make sure that over all optimal economic sollutions will be used. |  |  | legal |  |  |  | Non-confidential
0005-216d-c5f6-1336-2e22 | V1.0 for Public consultation version | 2 | 19 | - | - | 2014-12-03 11:20:07 | AXPO Group |  | final | missing paragraph | see Comment | There is need for a new subpoint 3. The costs generated by the disconnection of demand shall be compensated by the TSO. |  |  | legal |  |  |  | Non-confidential
0005-9689-ae86-1142-27df | V1.0 for Public consultation version | 3 | 20 | 1 | - | 2014-12-03 11:14:54 | AXPO Group |  | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design a Restoration Plan, in coordination with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | The design shall be in coordination, not consultation (as defined in Article 5) with DSO's and others. Measures generate costs. DSO's and others have a cost liability towards regulating authorities. Therefore they need to have the right for participation in decision-making. |  |  | legal |  |  |  | Non-confidential
0005-96c5-6001-258b-6b34 | V1.0 for Public consultation version | 3 | 20 | 1 | - | 2014-12-08 17:01:20 | Jasmina PIERRE | EdF | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design a Restoration Plan, in coordination with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | The consultation process proposed by ENTSO-E would lead the final decision to TSO without possible recourse from others parties if their constraints are not duly considered. It is essential all the instructions given by the TSO for execution respect the respective technical constraints and minimize related impacts for grid users. ENTSO-E proposals should be reinforced and foresee a final neutral decision from relevant NRA in case no agreement is reached (reference to coordination process defined in article 5). |  |  | technical |  |  |  | Non-confidential
0005-2181-28ea-e422-a65c | V1.0 for Public consultation version | 3 | 20 | 1 | - | 2014-12-08 16:39:17 | Markus Hemmer | EnBW | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design a Restoration Plan, in consultation and agreement with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | This Plan shall not only be consulted but also be agreed by all involved parties. | [6 empty] | Non-confidential
0005-6f79-c3de-0f70-5de3 | V1.0 for Public consultation version | 3 | 20 | 1 | - | 2014-12-08 17:16:52 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design a Restoration Plan, in consultation coordination with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | It is important for the DSOs that there is a mutual agreement (based on mutual understanding and trust) between the DSO and the TSO on the design of the restoration plan. A consultation does not provide for this agreement (cf. art. 5). |  |  | technical |  |  |  | Non-confidential
0005-bd85-857d-7f1a-1d30 | V1.0 for Public consultation version | 3 | 20 | 1 | - | 2014-12-08 16:38:53 | Rothermann Philippe |  | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design a Restoration Plan, in coordination with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Coordination and not only consultation | [6 empty] | Non-confidential
0005-216d-279e-0f70-ce38 | V1.0 for Public consultation version | 3 | 20 | 1 | - | 2014-12-08 17:16:53 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design a Restoration Plan, in coordination and agreement with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | This Plan shall not only be consulted but also be agreed by all involved parties. |  |  | legal |  |  |  | Non-confidential
0005-215a-cbb0-e6a6-cf7f | V1.0 for Public consultation version | 3 | 20 | 1 | - | 2014-11-28 15:52:38 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design a Restoration Plan, in consultation coordination with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | It is important for the DSOs that there is a mutual agreement (based on mutual understanding and trust) between the DSO and the TSO on the design of the restoration plan. A consultation does not provide for this agreement (cf. art. 5). |  |  | technical |  |  |  | Non-confidential
0005-4892-2f70-e89a-ec8b | V1.0 for Public consultation version | 3 | 20 | 1 | - | 2014-11-28 15:52:39 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design a Restoration Plan, in coordination and agreement with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | This Plan shall not only be consulted but also be agreed by all involved parties. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2315 | V1.0 for Public consultation version | 3 | 20 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design a Restoration Plan, in consultation coordination with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | It is important for the DSOs that there is a mutual agreement (based on mutual understanding and trust) between the DSO and the TSO on the design of the restoration plan. A consultation does not provide for this agreement (cf. art. 5). It is not sufficient to only consult on a restoration plan, it must be coordinated to respect the constraints of the overall vertically interconnected system. As the design phase of the plan is a non time-critical issue, exactness rather than speed should rule the process. The NC OS (umbrella code) does not provide the use of consultation instead of coordination. All actions and/or decisions specified in the NC OS in which the DSO is involved are always in coordination with the TSO, so it makes no sense to introduce consultation in the NC ER. ENTSO-E should consider to introduce the definition of 'coordination' (now in art. 5) in the NC OS so that it is valid in all system operation codes. Using "consultation" instead of "coordination" does also contradict the regulations on DSOs in Directive 2003/54/EC (Article 14). |  |  | Technical
0005-e495-5e7a-d54d-2047 | V1.0 for Public consultation version | 3 | 20 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design a Restoration Plan, in consultation coordination with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | It is important for the DSOs that there is a mutual agreement (based on mutual understanding and trust) between the DSO and the TSO on the design of the restoration plan. A consultation does not provide for this agreement (cf. art. 5).
0005-e495-5e7a-d54d-2048 | V1.0 for Public consultation version | 3 | 20 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design a Restoration Plan, in coordination and agreement with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | This Plan shall not only be consulted but also be agreed by all involved parties.
0005-e495-5e7a-d54d-2184 | V1.0 for Public consultation version | 3 | 20 | 1 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall propose a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible, which shall be submitted to NRA(s) for approval. | This is the critical element of the NC ER and it's vital that NRAs approve this. |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-2261 | V1.0 for Public consultation version | 3 | 20 | 1 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. |  | How is coordination with other regulatory and environmental permits foreseen? Safety and environmental measures should also be a consideration (e.g. flaring)
0005-e495-5e7a-d54d-1808 | V1.0 for Public consultation version | 3 | 20 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall design a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible. | Each TSO shall design PROPOSE a Restoration Plan, in consultation with DSOs, Significant Grid Users and neighbouring TSOs, to return its system to Normal State as fast as possible, WHICH SHALL BE SUBMITTED TO THE NRA(S) FOR APPROVAL.. | This is a critical element of the whole NC E&R and its vital that NRAs approve this.
0005-6fb6-2f8e-e70a-cd49 | V1.0 for Public consultation version | 3 | 20 | 2 | - | 2014-11-28 15:52:40 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | characteristics of its Network. | characteristics of the Network in its control area. | Also DSO networks inside his control area must be considered. |  |  | technical |  |  |  | Non-confidential
0005-2181-602a-11a6-a515 | V1.0 for Public consultation version | 3 | 20 | 2 | - | 2014-12-03 11:20:07 | AXPO Group |  | final | When designing a Restoration Plan, each TSO shall take into account, at least: a) the expected behaviour of the Significant Grid Users and of existing and new type A Power Generating Modules in its Responsibility Area; | When designing a Restoration Plan, each TSO shall take into account, at least: a) the expected behaviour of the Significant Grid Users in its Responsibility Area; | Delete new type A Power Generating Modules completely from Restoration Plan. These, mainly renewable power sources are NOT available at any time. The weather decides if they are available or not. The are obviousely productive only when the sun shines and the wind blows. And the level of production is very variable. A serious Restoration Plan cannot be depending on the daytime, weather or the seasons. In addition they are unmanned. A precise, controlled generation, as is needed in restoration, is not possible. |  |  | technical |  |  |  | Non-confidential
0005-9689-7609-a36c-4f09 | V1.0 for Public consultation version | 3 | 20 | 2 | - | 2014-12-07 12:51:42 | Herve MELJAC | EUR | final |  | We propose to merge Article 20.2 and 20.4, to make clearer that technical capability of SGUs in the design of System Defence plans. | The current drafting is confusing |  |  | legal |  |  |  | Non-confidential
0005-487d-857c-0cb4-a135 | V1.0 for Public consultation version | 3 | 20 | 2 | - | 2014-12-08 17:16:54 | Paul Doyle | ESB Generation & Wholesale Markets | final | characteristics of its Network. | characteristics of the Network in its control area. | Also DSO networks inside his control area must be considered. |  |  | technical |  |  |  | Non-confidential
0005-e4bd-28dc-3cc0-1a76 | V1.0 for Public consultation version | 3 | 20 | 2 | a | 2014-12-05 10:53:20 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | the expected behaviour of the Significant Grid Users and of existing and new type A Power Generating Modules in its Responsibility Area | the expected behaviour of the Significant Grid Users in its Responsibility Area | Type A Generators are not mentioned in the scope, so in our understanding they cannot be taken into accout, eccept they are significant (article 1, 6.) | 1 | 2 | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2049 | V1.0 for Public consultation version | 3 | 20 | 2 | c | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | characteristics of its Network. | characteristics of the Network in its control area. | Also DSO networks inside his control area must be considered.
0005-e495-5e7a-d54d-2316 | V1.0 for Public consultation version | 3 | 20 | 2 | c | 2014-12-08 22:31 | Michael Wilch | RWE | final | characteristics of its Network. | characteristics of its Network and of DSOs' network specificities. | Actions to be taken on DSOs' networks must take into account their specificities in order to not endanger their operational security. |  |  | Technical
0005-e495-5e7a-d54d-2317 | V1.0 for Public consultation version | 3 | 20 | 2 | d | 2014-12-08 22:31 | Michael Wilch | RWE | final | - | characteristics and requirements of underlying Distribution Systems. | DSOs play a a special role in this NC and should therefore be mentioned explicitly. Respecting the underlying distribution system properly is crucial for the success of any system restoration plan. |  |  | Technical
0005-9689-4eb0-d249-42bc | V1.0 for Public consultation version | 3 | 20 | 3 | - | 2014-12-08 16:38:55 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. d) the technical capabilities of the PGMs | Technical capabilities of existing and new PGMs must be respected. |  |  | technical |  |  |  | Non-confidential
0005-6fb5-c3fc-0cb4-e355 | V1.0 for Public consultation version | 3 | 20 | 3 | - | 2014-12-08 17:17:00 | Paul Doyle | ESB Generation & Wholesale Markets | final | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. d) the technical capabilities of the PGMs | Technical capabilities of existing and new PGMs must be respected. |  |  | technical |  |  |  | Non-confidential
0005-96b1-279e-0ea8-6f8f | V1.0 for Public consultation version | 3 | 20 | 3 | - | 2014-12-08 17:17:02 | Paul Doyle | ESB Generation & Wholesale Markets | final | In the design of its Restoration Plan, each TSO shall respect the following principles: […] | In the design of its Restoration Plan, each TSO shall respect the following principles: […] d) the measures do not lead to damages on the assets of Grid Users or Sysgtem Operators. | This point is essential to avoid any harm to assets which could be usefull for the Restoration of the System. Since e.g. TSOs are not anymore concerned with the possibilities and needs of the assets of stakeholders, there is a risk that some requirements ould lead to damages. |  |  | technical |  |  |  | Non-confidential
0005-bdd6-0860-e836-9ce1 | V1.0 for Public consultation version | 3 | 20 | 3 | - | 2014-11-28 15:52:41 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | the measures are economically efficient; and | the measures are over all economically efficient for all participants; | The concept of an “economically efficient" restoration is ambiguous, as it has to be put in the context of the time it takes to fully restore the service. It should not only be economically efficient for the TSO! It could be applicable to the provision of black-start capabilities or any other preventive action, but it is not clear how the concept applies to the actual restoration actions. |  |  | legal |  |  |  | Non-confidential
0005-e4aa-b45e-e76e-6f93 | V1.0 for Public consultation version | 3 | 20 | 3 | - | 2014-11-28 15:52:41 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; c) the minimum necessary measures are activated and d) the measures are suitable for foreseeable purposes. | Add the suitability for foreseeable purposes. |  |  | technical |  |  |  | Non-confidential
0005-9675-7735-2527-e8bf | V1.0 for Public consultation version | 3 | 20 | 3 | - | 2014-12-08 17:01:20 | Jasmina PIERRE | EdF | final | 3. In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. | 3. In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal and, notably, do not lead to damages on the assets ; b) the measures are economically efficient (cost efficiency including all participants); and c) the minimum necessary measures are activated; and e) the technical capabilities of the PGMs; | Technical capabilities of existing and new PGMs must be respected and the activated measures should avoid any harm to assets which contribute for the Restoration of the System. |  |  | technical |  |  |  | Non-confidential
0005-2196-6620-ea2a-c7b8 | V1.0 for Public consultation version | 3 | 20 | 3 | - | 2014-11-28 15:52:42 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. d) the technical capabilities of the PGMs | Technical capabilities of existing and new PGMs must be respected. |  |  | technical |  |  |  | Non-confidential
0005-e4be-569e-e6a6-8a6b | V1.0 for Public consultation version | 3 | 20 | 3 | - | 2014-11-28 15:53:00 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | In the design of its Restoration Plan, each TSO shall respect the following principles: […] | In the design of its Restoration Plan, each TSO shall respect the following principles: […] d) the measures do not lead to damages on the assets of Grid Users or Sysgtem Operators. | This point is essential to avoid any harm to assets which could be usefull for the Restoration of the System. Since e.g. TSOs are not anymore concerned with the possibilities and needs of the assets of stakeholders, there is a risk that some requirements ould lead to damages. |  |  | technical |  |  |  | Non-confidential
0005-e4a9-868c-e35a-401a | V1.0 for Public consultation version | 3 | 20 | 3 | - | 2014-12-08 16:39:18 | Markus Hemmer | EnBW | final | In the design of its Restoration Plan, each TSO shall respect the following principles: […] | In the design of its Restoration Plan, each TSO shall respect the following principles: […] d) the measures do not lead to damages on the assets of Grid Users or Sysgtem Operators. | This point is essential to avoid any harm to assets which could be usefull for the Restoration of the System. Since e.g. TSOs are not anymore concerned with the possibilities and needs of the assets of stakeholders, there is a risk that some requirements ould lead to damages. | [6 empty] | Non-confidential
0005-2181-4eae-0d7c-65f1 | V1.0 for Public consultation version | 3 | 20 | 3 | - | 2014-12-08 17:16:57 | Paul Doyle | ESB Generation & Wholesale Markets | final | the measures are economically efficient; and | the measures are over all economically efficient for all participants; | Not only economically efficient for the TSO! |  |  | legal |  |  |  | Non-confidential
0005-e4e5-104c-0d7c-9acf | V1.0 for Public consultation version | 3 | 20 | 3 | - | 2014-12-08 17:16:58 | Paul Doyle | ESB Generation & Wholesale Markets | final | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; c) the minimum necessary measures are activated and d) the measures are suitable for foreseeable purposes. | Add the suitability for foreseeable purposes. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-1810 | V1.0 for Public consultation version | 3 | 20 | 3 | A | 2014-12-08 13:31 | Garth Graham | SSE |  | the impact for Grid Users is minimal | the impact for SIGNIFICANT Grid Users is minimal | The reference to just ‘Grid Users’ is misleading as the definition in the metadata repository only refer to the NC HVDC definition – and as that code is limited in its application (to HVDC users) it gives a misleading and inappropriate application if used here.
0005-e495-5e7a-d54d-2050 | V1.0 for Public consultation version | 3 | 20 | 3 | b | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | the measures are economically efficient; and | the measures are over all economically efficient for all participants; | The concept of an “economically efficient" restoration is ambiguous, as it has to be put in the context of the time it takes to fully restore the service. It should not only be economically efficient for the TSO! It could be applicable to the provision of black-start capabilities or any other preventive action, but it is not clear how the concept applies to the actual restoration actions.
0005-e495-5e7a-d54d-2186 | V1.0 for Public consultation version | 3 | 20 | 3 | b | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | (…) the measures are economically efficient; and | (…) the measures are economic, efficient, reasonable and proportionate | The terms "reasonable" and "proportionate" appear in Article 4(2) and should be used here as wel |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2318 | V1.0 for Public consultation version | 3 | 20 | 3 | b | 2014-12-08 22:31 | Michael Wilch | RWE | final | the measures are economically efficient; and | the measures are economically efficient for the overall economy; and | It must be clear that the overall economy is meant, and not one single market participant. |  |  | Legal
0005-e495-5e7a-d54d-1812 | V1.0 for Public consultation version | 3 | 20 | 3 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | the measures are economically efficient; and | the measures are economically , efficient, REASONABLE AND PROPORTIONATE | The words reasonable and proportionate appears in Art 4(2) and should be used here as well.
0005-e495-5e7a-d54d-2319 | V1.0 for Public consultation version | 3 | 20 | 3 | c | 2014-12-08 22:31 | Michael Wilch | RWE | final | the minimum necessary measures are activated. | the minimum necessary measures, to manage the situation that can be foreseen, with minimum impact on society and overall economy are activated. | The 'minimum' has to be defined to make this statement binding. |  |  | Legal
0005-e495-5e7a-d54d-2051 | V1.0 for Public consultation version | 3 | 20 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; c) the minimum necessary measures are activated and d) the measures are suitable for foreseeable purposes. | Add the suitability for foreseeable purposes.
0005-e495-5e7a-d54d-2052 | V1.0 for Public consultation version | 3 | 20 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. | In the design of its Restoration Plan, each TSO shall respect the following principles: a) the impact for Grid Users is minimal; b) the measures are economically efficient; and c) the minimum necessary measures are activated. d) the technical capabilities of the PGMs | Technical capabilities of existing and new PGMs must be respected.
0005-e495-5e7a-d54d-2053 | V1.0 for Public consultation version | 3 | 20 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | In the design of its Restoration Plan, each TSO shall respect the following principles: […] | In the design of its Restoration Plan, each TSO shall respect the following principles: […] d) the measures do not lead to damages on the assets of Grid Users or Sysgtem Operators. | This point is essential to avoid any harm to assets which could be usefull for the Restoration of the System. Since e.g. TSOs are not anymore concerned with the possibilities and needs of the assets of stakeholders, there is a risk that some requirements ould lead to damages.
0005-e495-5e7a-d54d-2185 | V1.0 for Public consultation version | 3 | 20 | 3 |  | 2014-12-08 21:33 | Eberhard | EnBW | final | In the design of its Restoration Plan, each TSO shall respect the following principles: […] | In the design of its Restoration Plan, each TSO shall respect the following principles: […] d) the measures do not lead to damages on the assets of Grid Users or System Operators. | This point is essential to avoid any harm to assets which could be usefull for the Restoration of the System. Since e.g. TSOs are not anymore concerned with the possibilities and needs of the assets of stakeholders, there is a risk that some requirements ould lead to damages. |  |  | Technical | Fundamental
0005-969d-102e-0cb4-91fb | V1.0 for Public consultation version | 3 | 20 | 4 | - | 2014-12-08 17:17:31 | Paul Doyle | ESB Generation & Wholesale Markets | final | In the design of its Restoration Plan, each TSO shall consider the capabilities required: a) for Significant Grid Users and for new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | In the design of its Restoration Plan, each TSO shall consider the capabilities required: a) for new Significant Grid Users and for new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC] c) available communication interfaces | The TSO seems only to consider certain capabilities. What are the criteria to determine whether the TSO will consider certain capabilities or not? We understand the intention and probably the need to consider the behaviour of type A PGMs in the design of the restoration plan, but do not see the immediate need fur using the capabilities as such. Is this reasonable for type A? The communication interface will be present in all the new type A PGMs, as described in the NC RfG, but the communication link will not necessarily exist. |  |  | technical |  |  |  | Non-confidential
0005-6f7a-db6e-ea2a-8b82 | V1.0 for Public consultation version | 3 | 20 | 4 | - | 2014-11-28 15:53:01 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | In the design of its Restoration Plan, each TSO shall consider the capabilities required: a) for Significant Grid Users and for new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | In the design of its Restoration Plan, each TSO shall consider the capabilities required: a) for new Significant Grid Users and for new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC] c) available communication interfaces | The TSO seems only to consider certain capabilities. What are the criteria to determine whether the TSO will consider certain capabilities or not? We understand the intention and probably the need to consider the behaviour of type A PGMs in the design of the restoration plan, but do not see the immediate need fur using the capabilities as such. Is this reasonable for type A? The communication interface will be present in all the new type A PGMs, as described in the NC RfG, but the communication link will not necessarily exist. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2320 | V1.0 for Public consultation version | 3 | 20 | 4 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | In the design of its Restoration Plan, each TSO shall consider the capabilities required: a) for Significant Grid Users and for new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | In the design of its Restoration Plan, each TSO shall consider the capabilities required: a) for Significant Grid Users and for new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | Same remarks as for art. 8§4. |  |  | Technical
0005-e495-5e7a-d54d-1814 | V1.0 for Public consultation version | 3 | 20 | 4 | A | 2014-12-08 13:31 | Garth Graham | SSE |  | for Significant Grid Users and for new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and | for FROM Significant Grid Users and new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and | Typo
0005-bdc1-86aa-e5b2-afd6 | V1.0 for Public consultation version | 3 | 20 | 4 | b | 2014-12-08 16:39:18 | Markus Hemmer | EnBW | final | in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC] or bilateral contracts. | There are many Grid users which have their own contracts with TSOs which requirements they have to fullfil. In national legislation there are usually no requirements named so contracts are a better base for this reason. | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-1816 | V1.0 for Public consultation version | 3 | 20 | 4 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | SET OUT in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | Typo
0005-e495-5e7a-d54d-2054 | V1.0 for Public consultation version | 3 | 20 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | In the design of its Restoration Plan, each TSO shall consider the capabilities required: a) for Significant Grid Users and for new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | In the design of its Restoration Plan, each TSO shall consider the capabilities required: a) for new Significant Grid Users and for new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC] c) available communication interfaces | The TSO seems only to consider certain capabilities. What are the criteria to determine whether the TSO will consider certain capabilities or not? We understand the intention and probably the need to consider the behaviour of type A PGMs in the design of the restoration plan, but do not see the immediate need fur using the capabilities as such. Is this reasonable for type A? The communication interface will be present in all the new type A PGMs, as described in the NC RfG, but the communication link will not necessarily exist.
0005-e495-5e7a-d54d-2187 | V1.0 for Public consultation version | 3 | 20 | 4 |  | 2014-12-08 21:33 | Wilch | RWE | final | In the design of its Restoration Plan, each TSO shall consider the capabilities required: a) for Significant Grid Users and for new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC]. | In the design of its Restoration Plan, each TSO shall consider the capabilities required: a) for new Significant Grid Users and for new type A Power Generating Modules, in [NC RfG], [NC DC] and [NC HVDC]; and b) in the national laws for those Significant Grid Users who are not subject to or are derogated from [NC RfG], [NC DC] and [NC HVDC] c) available communication interfaces | The TSO seems only to consider certain capabilities. What are the criteria to determine whether the TSO will consider certain capabilities or not? We understand the intention and probably the need to consider the behaviour of type A PGMs in the design of the restoration plan, but do not see the immediate need fur using the capabilities as such. Is this reasonable for type A? The communication interface will be present in all the new type A PGMs, as described in the NC RfG, but the communication link will not necessarily exist. |  |  | Technical | Fundamental
0005-4855-ad8e-3b94-78a6 | V1.0 for Public consultation version | 3 | 20 | 5 | - | 2014-12-05 10:53:59 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the Restoration Plan. | Each TSO shall, in agreement with nationally relevant DSOs, identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the Restoration Plan. | the measures should be argreed with the relevant DSO according to the procedure described in article 8.1. | 1 | 3 | legal |  |  |  | Non-confidential
0005-e4d1-9ee6-1336-4cc9 | V1.0 for Public consultation version | 3 | 20 | 5 | - | 2014-12-03 11:20:07 | AXPO Group |  | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the Restoration Plan. | see Comment | Not the TSO shall identify new type A Power Generating Modules. That is the job of the DSO. The DSO then reports to the TSO. Even better is NOT to consider new type A Power Generating Modules in the Restoration Plan at all. |  |  | legal |  |  |  | Non-confidential
0005-6f79-855e-0f70-8786 | V1.0 for Public consultation version | 3 | 20 | 5 | - | 2014-12-08 17:17:32 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the Restoration Plan. |  | Will type A PGMs be considered individually or not? If affirmative, how will the TSO do this in practice? Will the DSO be involved in this process? If negative, will this be done in an aggregated way? Same questions here, how will the DSO/aggregator identify the type A PGM's? |  |  | technical |  |  |  | Non-confidential
0005-e4d2-8d4e-e76e-c20f | V1.0 for Public consultation version | 3 | 20 | 5 | - | 2014-11-28 15:51:09 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the Restoration Plan. |  | Will type A PGMs be considered individually or not? If affirmative, how will the TSO do this in practice? Will the DSO be involved in this process? If negative, will this be done in an aggregated way? Same questions here, how will the DSO/aggregator identify the type A PGM's? |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2321 | V1.0 for Public consultation version | 3 | 20 | 5 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the Restoration Plan. | Based on the econonmically efficiency requirement of Article 8 §3.b), each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the Restoration Plan and involve them in the process. | DSOs are convinced that new type A PGMs should not be part of the NC ER, cf. explanation art. 8§4. TSO must involve all parties that have an active role to play in the Restoration Plan. |  |  | Technical
0005-e495-5e7a-d54d-2055 | V1.0 for Public consultation version | 3 | 20 | 5 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the Restoration Plan. |  | Will type A PGMs be considered individually or not? If affirmative, how will the TSO do this in practice? Will the DSO be involved in this process? If negative, will this be done in an aggregated way? Same questions here, how will the DSO/aggregator identify the type A PGM's?
0005-e495-5e7a-d54d-2188 | V1.0 for Public consultation version | 3 | 20 | 5 |  | 2014-12-08 21:33 | Wilch | RWE | final | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the Restoration Plan. |  | Will type A PGMs be considered individually or not? If affirmative, how will this will be done in practice? Will the DSO be involved in this process? If negative, will this be done in an aggregated way? Same questions here, how will the DSO/aggregator identify the type A PGM's? |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1819 | V1.0 for Public consultation version | 3 | 20 | 5 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary services in case of activation of the Restoration Plan. | Each TSO shall identify the DSOs, Significant Grid Users and new type A Power Generating Modules that have an active role for providing the necessary PROCURED services in case of activation of the Restoration Plan. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to those services being procured.
0005-9689-c4fe-3cc0-17ff | V1.0 for Public consultation version | 3 | 20 | 6 | - | 2014-12-05 10:54:50 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | In the design of its Restoration Plan, each TSO shall identify the possible power sources in its Responsibility Area that can be used in Bottom-up Re-energisation Strategy, having the following capabilities: | In the design of its Restoration Plan, each TSO shall identify the possible power sources in its Responsibility Area that can be used in Bottom-up Re-energisation Strategy, having the following capabilities: Each TSO shall contract the power sources necessary to activate the System Restoration Plan | According to FWGL FG-2011-E-003 on System Operations, TSOs shall ensure access (contracted or otherwise procured) to sufficient black-start capacities and islanding capabilities to allow for the efficient and fast restoration. | 1 | 3 | legal |  |  |  | Non-confidential
0005-6f79-c3c0-0bec-5340 | V1.0 for Public consultation version | 3 | 20 | 6 | - | 2014-12-08 17:09:24 | Paul Doyle | ESB Generation & Wholesale Markets | final | In the design of its Restoration Plan, each TSO shall identify the possible power sources in its Responsibility Area that can be used in Bottom-up Re-energisation Strategy, having the following capabilities: | In the design of its Restoration Plan, each TSO shall identify the possible power sources in its Responsibility Area that can be used in Bottom-up Re-energisation Strategy, having the following capabilities contracted: | Only if these services are agreed on a contractual base (see. NC RfG). These services are expensive ones and have to be compensated. |  |  | legal |  |  |  | Non-confidential
0005-216e-cbce-e9c6-0448 | V1.0 for Public consultation version | 3 | 20 | 6 | - | 2014-11-28 15:51:10 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | In the design of its Restoration Plan, each TSO shall identify the possible power sources in its Responsibility Area that can be used in Bottom-up Re-energisation Strategy, having the following capabilities: | In the design of its Restoration Plan, each TSO shall identify the possible power sources in its Responsibility Area that can be used in Bottom-up Re-energisation Strategy, having the following capabilities contracted: | Only if these services are agreed on a contractual base (see. NC RfG). These services are expensive ones and have to be compensated. |  |  | legal |  |  |  | Non-confidential
0005-2145-ad7e-e3be-6639 | V1.0 for Public consultation version | 3 | 20 | 6 | - | 2014-12-08 16:39:18 | Markus Hemmer | EnBW | final | In the design of its Restoration Plan, each TSO shall identify the possible power sources in its Responsibility Area that can be used in Bottom-up Re-energisation Strategy, having the following capabilities: | In the design of its Restoration Plan, each TSO shall identify the possible power sources in its Responsibility Area that can be used in Bottom-up Re-energisation Strategy, having the following capabilities contracted: | Only if this services are agreed on a contractual base (see. NC RfG). This services are expensive ones and have to be compensated. | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-2322 | V1.0 for Public consultation version | 3 | 20 | 6 | c | 2014-12-08 22:31 | Michael Wilch | RWE | final | Island Operation. | Controlled Island Operation. | It seems better to use 'controlled' island operation. |  |  | Technical
0005-e495-5e7a-d54d-2056 | V1.0 for Public consultation version | 3 | 20 | 6 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | In the design of its Restoration Plan, each TSO shall identify the possible power sources in its Responsibility Area that can be used in Bottom-up Re-energisation Strategy, having the following capabilities: | In the design of its Restoration Plan, each TSO shall identify the possible power sources in its Responsibility Area that can be used in Bottom-up Re-energisation Strategy, having the following capabilities contracted: | Only if these services are agreed on a contractual base (see. NC RfG). These services are expensive ones and have to be compensated.
0005-e495-5e7a-d54d-2189 | V1.0 for Public consultation version | 3 | 20 | 6 |  | 2014-12-08 21:33 | Eberhard | EnBW | final | In the design of its Restoration Plan, each TSO shall identify the possible power sources in its Responsibility Area that can be used in Bottom-up Re-energisation Strategy, having the following capabilities: | In the design of its Restoration Plan, each TSO shall identify the possible power sources in its Responsibility Area that can be used in Bottom-up Re-energisation Strategy, having the following capabilities contracted: | Only if these services are agreed on a contractual base (see. NC RfG). These services are expensiveshould be compensated. |  |  | Technical | Fundamental
0005-6fb5-5f50-3b94-3634 | V1.0 for Public consultation version | 3 | 20 | 7 | - | 2014-12-05 10:55:44 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | In the design of its Restoration Plan, each TSO shall define the power sources within its Responsibility Area necessary to re-energize its System with Bottom-up Strategy, … | In the design of its Restoration Plan, each TSO shall, after consultation with nationally relevant DSOs, define the power sources within its Responsibility Area necessary to re-energize its System with Bottom-up Strategy, … | the measures should be argreed with the relevant DSO according to the procedure described in article 8.1. | 1 | 3 | legal |  |  |  | Non-confidential
0005-2145-c3ce-d54d-f202 | V1.0 for Public consultation version | 3 | 20 | 7 | - | 2014-12-08 23:56:24 | Gunnar Kaestle | Clausthal University of Technology | final | geographical distribution of power sources with Black Start and Island Operation capabilities | geographical distribution of power sources with Black Start and Island Operation and the voltage level of their point of connection | With a rising share of distributed generation (PV, Wind, CHP, Storage) it may be possible that also those source help during restoration phase. This concept (although today not very feasable) shall not be prohibited but enabled by the NC ER |  |  | technical |  |  |  | Non-confidential
0005-2181-9ccd-30f8-674e | V1.0 for Public consultation version | 3 | 20 | 7 | - | 2014-12-08 18:18:38 | Thomas Willson |  | final | geographical distribution of power sources with Black Start and Island Operation capabilities | geographical distribution of power sources with Black Start and Island Operation and the voltage level of their point of connection | With a rising share of distributed generation (PV, Wind, CHP, Storage) it may be possible that also those source help during restoration phase. This concept (although today not very feasable) shall not be prohibited but enabled by the NC ER |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-1823 | V1.0 for Public consultation version | 3 | 20 | 7 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | In the design of its Restoration Plan, each TSO shall define the power sources within its Responsibility Area necessary to re-energize its System with Bottom-up Strategy, taking into account at least: | In the design of its Restoration Plan, each TSO shall define, SUBJECT TO NRA APPROVAL, the power sources within its Responsibility Area necessary to re-energize its System with Bottom-up Strategy, taking into account at least: | There must be NRA approval of the power sources to be used to avoid TSOs targeting obligations on certain parties (such as generators or demand) whilst avoiding others (such as interconnectors) which they have a financial interest in.
0005-e495-5e7a-d54d-2323 | V1.0 for Public consultation version | 3 | 20 | 8 | b | 2014-12-08 22:31 | Michael Wilch | RWE | final | monitoring and performing Island Operation; and | monitoring and performing controlled Island Operation; and | It seems better to use 'controlled' island operation. |  |  | Technical
0005-e495-5e7a-d54d-2324 | V1.0 for Public consultation version | 3 | 20 | 8 | c | 2014-12-08 22:31 | Michael Wilch | RWE | final | resynchronising Island Operation areas. | resynchronising controlled Island Operation areas. | It seems better to use 'controlled' island operation. |  |  | Technical
0005-9675-373e-0bec-7132 | V1.0 for Public consultation version | 3 | 20 | 11 | - | 2014-12-08 17:09:25 | Paul Doyle | ESB Generation & Wholesale Markets | final | b) context triggering the measures of the Restoration Plan; and | b) parameters and limits triggering the measures of the System Restoration Plan; and | The term "context" is far too vague for the purpose |  |  | technical |  |  |  | Non-confidential
0005-2181-8540-0d7c-d7c1 | V1.0 for Public consultation version | 3 | 20 | 11 | - | 2014-12-08 17:09:27 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall notify the concept of the Restoration Plan to the National Regulatory Authorities or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the Restoration Plan. | Each TSO shall notify the concept of the Restoration Plan to the National Regulatory Authorities and parties identified in accordance with Article 8.4 or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the Restoration Plan. | Also parties mentioned in Article 8.4 must be informed! |  |  | legal |  |  |  | Non-confidential
0005-2196-8d30-e7d1-107a | V1.0 for Public consultation version | 3 | 20 | 11 | - | 2014-11-28 15:51:11 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | b) context triggering the measures of the Restoration Plan; and | b) parameters and limits triggering the measures of the System Restoration Plan; and | The term "context" is far too vague for the purpose |  |  | technical |  |  |  | Non-confidential
0005-6f8e-3f10-e961-446b | V1.0 for Public consultation version | 3 | 20 | 11 | - | 2014-11-28 15:51:12 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall notify the concept of the Restoration Plan to the National Regulatory Authorities or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the Restoration Plan. | Each TSO shall notify the concept of the Restoration Plan to the National Regulatory Authorities and parties identified in accordance with Article 8.4 or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the Restoration Plan. | Also parties mentioned in Article 8.4 must be informed! |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2325 | V1.0 for Public consultation version | 3 | 20 | 11 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall notify the concept of the Restoration Plan to the National Regulatory Authorities or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the Restoration Plan. | Each TSO shall notify the concept of the Restoration Plan to the National Regulatory Authorities or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the Restoration Plan. | It seems only logical to notify the complete Restoration Plan to the NRA, not only the concept. |  |  | Technical
0005-e495-5e7a-d54d-2057 | V1.0 for Public consultation version | 3 | 20 | 11 | b | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | b) context triggering the measures of the Restoration Plan; and | b) parameters and limits triggering the measures of the System Restoration Plan; and | The term "context" is far too vague for the purpose
0005-e495-5e7a-d54d-2326 | V1.0 for Public consultation version | 3 | 20 | 11 | b | 2014-12-08 22:31 | Michael Wilch | RWE | final | context triggering the measures of the Restoration Plan; and | parameters and limits triggering the measures of the System Defence Plan; and | The term "context" is far too less specific for the purpose. |  |  | Technical
0005-e495-5e7a-d54d-2058 | V1.0 for Public consultation version | 3 | 20 | 11 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall notify the concept of the Restoration Plan to the National Regulatory Authorities or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the Restoration Plan. | Each TSO shall notify the concept of the Restoration Plan to the National Regulatory Authorities and parties identified in accordance with Article 8.4 or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the Restoration Plan. | Also parties mentioned in Article 8.4 must be informed.
0005-e495-5e7a-d54d-2190 | V1.0 for Public consultation version | 3 | 20 | 11 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO shall notify the concept of the Restoration Plan to the National Regulatory Authorities or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to this article and subsequently pursuant to any changes of the concept of the Restoration Plan. | Each TSO shall submit the Restoration Plan to the National Regulatory Authorities or, when explicitly foreseen in national law, other relevant national authorities, following its preparation by the TSO pursuant to this article and subsequently pursuant to this article and subsequently pursuant to any changes to the Restoration Plan. | The Restoration Plan is a key element of the NC ER and must be subject to explicit NRA approval. External oversight is vital to give confidence to all stakeholders and consumers across the 28 Member States that the Restoration Plan(s) are robust and fit for purpose. |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-2191 | V1.0 for Public consultation version | 3 | 20 | 11 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | The concept of the Restoration Plan shall include the following: | The Restoration Plan shall include the following: | We need a Restoration Paln and not its concept. Of not in the Code, where the Restoration Plan will be defined? |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2251 | V1.0 for Public consultation version | 3 | 20 | 11 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each TSO shall notify the concept of the System Defense Plan to its National Regulatory, Authority or, when explicitly foreseen in national law, other relevant national authorities, |  | The TSO will only notify national governments what they have already planned concerning national citizens. They do not ask permission. This is unacceptable when customers and small generators are included in national plans. A wider set of considerations must be taken into account than those under the TSO's control.
0005-e495-5e7a-d54d-1825 | V1.0 for Public consultation version | 3 | 20 | 11 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall notify the concept of the Restoration Plan to the National Regulatory Authorities or, when explicitly foreseen in national law, other relevant national authorities, following its design pursuant to this article and subsequently pursuant to any changes of the concept of the Restoration Plan. | Each TSO shall notify the concept of SUBMIT the Restoration Plan to the National Regulatory Authorities or, when explicitly foreseen in national law, other relevant national authorities, following its design PREPARATION BY THE TSO pursuant to this article and subsequently pursuant to any changes of the concept of the Restoration Plan. | The Restoration Plan is a key element of the NC E&R and MUST be subject to explicit NRA approval. If an NRA is unable / unwilling to do this then they should be able to ask ACER to do it on their behalf. It must be remembered that the event, in November 2006, that gave rise to the Network Codes being developed arose from the actions of TSOs and NOT Significant Grid Users. It would therefore be perverse to allow the TSOs alone to write their own homework question, answer it and then mark it. External oversight is vital to give confidence to all stakeholders and consumers across the 28 Member States that the Restoration Plan(s) are robust and fit for purpose.
0005-e495-5e7a-d54d-1827 | V1.0 for Public consultation version | 3 | 20 | 11 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | The concept of the Restoration Plan shall include the following: | The concept of the Restoration Plan shall include the following: | We do not need ‘concepts’ we need, in the Restoration Plan, the details themselves to restore the system. After all if the details are NOT to be found in the restoration Plan where will they be found? And who / how is this other document(s) (with the detail not in the restoration Plan) to be approved by the NRA(s)?
0005-e495-5e7a-d54d-2192 | V1.0 for Public consultation version | 3 | 20 | 12 |  | 2014-12-08 21:33 | AG | RWE | final | Add new paragraph. | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | There needs to be a clear reference to cost recovery to avoid the costs of providing support to another TSO in an Emergency, Black Start or Restoration State falling upon consumers in another TSO's area. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2183 | V1.0 for Public consultation version | 3 | 20 |  |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | See the wording of Article 20- general comment | See the justification. | It is disappointing that the Code is not a pan-European System Defence Plan/ Restoration Plan, but rather a loosly linked collection of each TSOs national plans. One may ask: what is the added value of a pan-European network code in comparison to the current situation? |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-2243 | V1.0 for Public consultation version | 3 | 20 |  |  | 2014-12-08 12:24 | Wolfram Heckmann | Fraunhofer IWES | final |  |  | General remark to this section: Intentional islanding of distribution grid areas should also be covered and their support of system restoration considered.
0005-4869-9d19-a36c-3060 | V1.0 for Public consultation version | 3 | 21 | 1 | - | 2014-12-07 12:51:42 | Herve MELJAC | EUR | final | Each TSO shall make available the measures of its Restoration Plan which are to be implemented on the Transmission System. | Each TSO shall make sure the measures of its Restoration Plan which are to be implemented on the Transmission System are available for use at all time. | Wording not clear. When reading the initial version, the read is tempted to ask "to whom? Where? How?" |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2193 | V1.0 for Public consultation version | 3 | 21 | 1 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO shall make available the measures of its Restoration Plan which are to be implemented on the Transmission System. | Each TSO shall implement and make available the measures of the Restoration Plan which are to be implemented on the Transmission System in the timescales specified by the NRA(s). | You have to implement something first in order to make it available. |  |  | Legal | Editorial
0005-e495-5e7a-d54d-1828 | V1.0 for Public consultation version | 3 | 21 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall make available the measures of its Restoration Plan which are to be implemented on the Transmission System. | Each TSO shall IMPLEMENT AND make available the measures of its THE Restoration Plan which are to be implemented on the Transmission System IN THE TIMSECALES SPECIFIED BY THE NRA(S). | Given the reference in Art 21 (2) (a) and (b) to DSO and SGUs having to implement the measures its important that the TSOs, likewise, have to implement the measures…after all if they are not ‘implemented’ then they cannot (as suggested with the current wording) be ‘made available’. It is important to recognise that the Restoration Plan it not the TSO’s, so ‘its’ should be replaced by ‘the’. Measures to be implemented on the transmission system should be specified by the NRA. Given that the TSO is not proposing (in Art 21 (2) (a) or (b) any appeal on the deadlines they set for DSOs or SGUs then they presumably do not require any appeal for a deadline set by the NRA(s)?!
0005-2145-28ea-e35a-d1c9 | V1.0 for Public consultation version | 3 | 21 | 2 | - | 2014-12-08 16:39:18 | Markus Hemmer | EnBW | final | notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs the measures of the Restoration Plan which of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | technical |  |  |  | Non-confidential
0005-96c6-6620-e6a5-36fa | V1.0 for Public consultation version | 3 | 21 | 2 | - | 2014-11-28 15:51:15 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall: a) notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; b) notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | Each TSO shall: a) notify DSOs directly connected to the transmission system the measures of the Restoration Plan, determined in collaboration between the TSO and the DSO, which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; b) notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. | To work conform the framework of cascading measures, each System Operator shall notify only its own customers. The article imposes measures to be implemented on their installations within a certain deadline. It seems a rather uniderictional order coming from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO and the DSO. Notification of the SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). |  |  | technical |  |  |  | Non-confidential
0005-6fa1-d360-0e44-1060 | V1.0 for Public consultation version | 3 | 21 | 2 | - | 2014-12-08 17:09:29 | Paul Doyle | ESB Generation & Wholesale Markets | final | notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | legal |  |  |  | Non-confidential
0005-487d-d39c-0c50-035d | V1.0 for Public consultation version | 3 | 21 | 2 | - | 2014-12-08 17:09:30 | Paul Doyle | ESB Generation & Wholesale Markets | final | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | legal |  |  |  | Non-confidential
0005-bd99-5e6c-0bec-44a3 | V1.0 for Public consultation version | 3 | 21 | 2 | - | 2014-12-08 17:09:32 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall: a) notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; b) notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | Each TSO shall: a) notify DSOs directly connected to the transmission system the measures of the Restoration Plan, determined in collaboration between the TSO and the DSO, which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; b) notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. | To work conform the framework of cascading measures, each System Operator shall notify only its own customers. The article imposes measures to be implemented on their installations within a certain deadline. It seems a rather uniderictional order coming from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO and the DSO. Notification of the SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). |  |  | technical |  |  |  | Non-confidential
0005-6f66-0860-e9c5-805f | V1.0 for Public consultation version | 3 | 21 | 2 | - | 2014-11-28 15:51:12 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | legal |  |  |  | Non-confidential
0005-bdae-3f10-e899-aa34 | V1.0 for Public consultation version | 3 | 21 | 2 | - | 2014-11-28 15:51:13 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2327 | V1.0 for Public consultation version | 3 | 21 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall: a) notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; b) notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | Each TSO shall: a) notify DSOs directly connected to the transmission system the measures of the Restoration Plan, determined in collaboration between the TSO and the DSO, which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation, agreed upon between TSO, DSOs and NRA; b) notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | To keep within the framework of cascading measures, each System Operator shall notify only underlying SOs. The article imposes measures to be implemented on their installations within a certain deadline. It seems a rather uniderictional order coming from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO and the DSO. Notification of the SGUs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). DSOs are convinced that new type A PGMs should not be part of the NC ER, cf. explanation art. 8§4. |  |  | Technical
0005-4869-01cc-3d24-684a | V1.0 for Public consultation version | 3 | 21 | 2 | a | 2014-12-05 10:57:42 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each TSO shall notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation | Each TSO shall elaborate a recommendation for each DSO, based on the consultation in Article 8, according … | the measures should be argreed with the relevant DSO according to the procedure described in article 8.1, the TSO is not a NRA. | 1 | 5 | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2059 | V1.0 for Public consultation version | 3 | 21 | 2 | a | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC.
0005-e495-5e7a-d54d-2194 | V1.0 for Public consultation version | 3 | 21 | 2 | a | 2014-12-08 21:33 | Eberhard | EnBW | final | notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1830 | V1.0 for Public consultation version | 3 | 21 | 2 | A | 2014-12-08 13:31 | Garth Graham | SSE |  | notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or TO BE PROCURED FROM the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-e4d1-86aa-e616-aace | V1.0 for Public consultation version | 3 | 21 | 2 | b | 2014-12-08 16:39:18 | Markus Hemmer | EnBW | final | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2060 | V1.0 for Public consultation version | 3 | 21 | 2 | b | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC.
0005-e495-5e7a-d54d-2195 | V1.0 for Public consultation version | 3 | 21 | 2 | b | 2014-12-08 21:33 | Eberhard | EnBW | final | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1833 | V1.0 for Public consultation version | 3 | 21 | 2 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be PROCURED AND implemented on their installations, including the deadlines for implementation. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-1835 | V1.0 for Public consultation version | 3 | 21 | 2 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. | notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. A SIGNIFICANT GRID USER MAY USE THE DEROGATION AND APPEAL PROCESS SET OUT IN THE NC RFG OR NC DC (AS APPROPRIATE) IF THEY BELIEVE THE SYSTEM DEFENCE PLAN MEASURES PROPOSED BY THE TSO ARE TO ONEROUS. | If the measures are not to be procured then a derogation and appeal process is required whereby SGUs can appeal to the NRA.
0005-e495-5e7a-d54d-2061 | V1.0 for Public consultation version | 3 | 21 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall: a) notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; b) notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | Each TSO shall: a) notify DSOs directly connected to the transmission system the measures of the Restoration Plan, determined in collaboration between the TSO and the DSO, which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; b) notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. | To work conform the framework of cascading measures, each System Operator shall notify only its own customers. The article imposes measures to be implemented on their installations within a certain deadline. It seems a rather uniderictional order coming from the TSO. It would be appropriate to add that these measures will be implemented in a collaboration between the TSO and the DSO. Notification of the SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS).
0005-e495-5e7a-d54d-2196 | V1.0 for Public consultation version | 3 | 21 | 2 |  | 2014-12-08 21:33 | Wilch | RWE | final | Each TSO shall: a) notify DSOs the measures of the Restoration Plan which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; b) notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. When provided in national legislation, the TSO shall notify Significant Grid Users and new type A Power Generating Modules connected to Distribution Systems and shall inform the concerned DSO of such notification. | Each TSO shall: a) notify DSOs directly connected to the transmission system the measures of the Restoration Plan, determined in collaboration between the TSO and the DSO, which are to be implemented on their installations and/or the installations of Significant Grid Users and new type A Power Generating Modules connected to their Distribution System, including the deadlines for implementation; b) notify Significant Grid Users directly connected to its Transmission System the measures of the Restoration Plan which are to be implemented on their installations, including the deadlines for implementation. | Each System Operator shall notify solely its own customers. It is also advisable that this work is done in collaboration between the TSOs and DSOs. |  |  | Technical | Fundamental
0005-6f8d-ae02-a295-d6e8 | V1.0 for Public consultation version | 3 | 21 | 3 | - | 2014-12-04 14:21:20 | Dekinderen Eric | Genrator company | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan ……….. | Each DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan ……….. | Why not all DSOs???????? |  |  | technical |  |  |  | Non-confidential
0005-9675-115c-e486-5198 | V1.0 for Public consultation version | 3 | 21 | 3 | - | 2014-12-08 16:39:18 | Markus Hemmer | EnBW | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | technical |  |  |  | Non-confidential
0005-48a6-569e-e7d1-fac1 | V1.0 for Public consultation version | 3 | 21 | 3 | - | 2014-11-28 15:51:16 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify DSOs, Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation. | To work conform the framework of cascading measures, each System Operator shall notify only its own customers. Notification of underlayed DSOs, SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Still the question remains on how this will be done for new type A PGMs. |  |  | technical |  |  |  | Non-confidential
0005-96c6-b422-e961-4b5d | V1.0 for Public consultation version | 3 | 21 | 3 | - | 2014-11-28 15:51:16 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan ……….. | Each DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan ……….. | Why not all DSOs? | [6 empty] | Non-confidential
0005-969e-6602-e709-343e | V1.0 for Public consultation version | 3 | 21 | 3 | - | 2014-11-28 15:51:17 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | legal |  |  |  | Non-confidential
0005-9675-1228-126e-db80 | V1.0 for Public consultation version | 3 | 21 | 3 | - | 2014-12-03 11:14:54 | AXPO Group |  | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | see Comment | To work conform to the framework of cascading measures, each System Operator shall notify its own customers including underlayed DSOs. There is only ONE line of communication. |  |  | legal |  |  |  | Non-confidential
0005-e4a9-d360-0f70-ea58 | V1.0 for Public consultation version | 3 | 21 | 3 | - | 2014-12-08 17:09:33 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify DSOs, Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation. | To work conform the framework of cascading measures, each System Operator shall notify only its own customers. Notification of underlayed DSOs, SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Still the question remains on how this will be done for new type A PGMs. |  |  | technical |  |  |  | Non-confidential
0005-6fa1-8540-0f70-e472 | V1.0 for Public consultation version | 3 | 21 | 3 | - | 2014-12-08 17:09:35 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan ……….. | Each DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan ……….. | Why not all DSOs? | [6 empty] | Non-confidential
0005-4891-102e-0c50-e2e4 | V1.0 for Public consultation version | 3 | 21 | 3 | - | 2014-12-08 17:09:36 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2328 | V1.0 for Public consultation version | 3 | 21 | 3 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify other DSOs and Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation. , unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | To keep within the framework of cascading measures, each System Operator shall notify only underlying SOs. Notification of the SGUs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). DSOs are convinced that new type A PGMs should not be part of the NC ER, cf. explanation art. 8§4. |  |  | Technical
0005-e495-5e7a-d54d-2062 | V1.0 for Public consultation version | 3 | 21 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify DSOs, Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation. | To work conform the framework of cascading measures, each System Operator shall notify only its own customers. Notification of underlayed DSOs, SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Still the question remains on how this will be done for new type A PGMs.
0005-e495-5e7a-d54d-2063 | V1.0 for Public consultation version | 3 | 21 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan ……….. | Each DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan ……….. | Why not all DSOs?
0005-e495-5e7a-d54d-2064 | V1.0 for Public consultation version | 3 | 21 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC.
0005-e495-5e7a-d54d-2197 | V1.0 for Public consultation version | 3 | 21 | 3 |  | 2014-12-08 21:33 | Wilch | RWE | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify DSOs, Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation. | Each System Operator shall notify only its own customers. Notification of underlayed DSOs, SGUs and new type A PGMs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Still the question remains on how this will be done for new type A PGMs. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2198 | V1.0 for Public consultation version | 3 | 21 | 3 |  | 2014-12-08 21:33 | EDK | GFS | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan ……….. | Each DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan ……….. | Why not all DSOs? |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2199 | V1.0 for Public consultation version | 3 | 21 | 3 |  | 2014-12-08 21:33 | Eberhard | EnBW | final | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, unless the TSO has already notified the Significant Grid Users and new type A Power Generating Modules. | There are no further installations necessary. Either the Grid User has to fullfil the requirements of e.g. NC RfG or requirements of bilateral contracts or the installations are already agreed as stated in Article 5(2) of this NC. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1837 | V1.0 for Public consultation version | 3 | 21 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan which they have to implement on their installations, including the deadlines for implementation, ….. | Each notified DSO shall notify Significant Grid Users and new type A Power Generating Modules directly connected to its Distribution System the measures of the Restoration Plan Plan TO BE PROCURED FROM THEM which they have to implement on their installations, including the deadlines for implementation, ….. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-bd85-ac8c-0d18-22e6 | V1.0 for Public consultation version | 3 | 21 | 4 | - | 2014-12-08 17:09:37 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each notified DSO, Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and b) make available the measures implemented on its installations. | no text proposal (yet). | How will this be done in practice for new type A PGMs? This sounds unworkable, especially the confirmation. Even if the number of new type A PGMs being part of the restoration plan might be limited in the beginning, this number will rise in the future. Furthermore, by only picking out a number of new type A PGMs, there may be a risk of discrimination because of not treating all new type A PGMs in the same way. |  |  | technical |  |  |  | Non-confidential
0005-216e-8d30-e6a5-5d8a | V1.0 for Public consultation version | 3 | 21 | 4 | - | 2014-11-28 15:52:10 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each notified DSO, Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and b) make available the measures implemented on its installations. | no text proposal (yet). | How will this be done in practice for new type A PGMs? This sounds unworkable, especially the confirmation. Even if the number of new type A PGMs being part of the restoration plan might be limited in the beginning, this number will rise in the future. Furthermore, by only picking out a number of new type A PGMs, there may be a risk of discrimination because of not treating all new type A PGMs in the same way. |  |  | technical |  |  |  | Non-confidential
0005-e4d1-1246-1016-faad | V1.0 for Public consultation version | 3 | 21 | 4 | - | 2014-12-03 11:14:54 | AXPO Group |  | final | make available the measures implemented on its installations. | see Comment | It is uncelar what "make measures available" means. Available to whom? What exactly? Measurements and signals? |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2329 | V1.0 for Public consultation version | 3 | 21 | 4 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each notified DSO, Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and b) make available the measures implemented on its installations. | Each notified DSO and Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and b) make available the measures implemented on its installations. | DSOs are convinced that new type A PGMs should not be part of the NC ER, cf. explanation art. 8§4. |  |  | Technical
0005-e495-5e7a-d54d-1839 | V1.0 for Public consultation version | 3 | 21 | 4 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | make available the measures implemented on its installations | make available the measures implemented on its installations IN ACCORDANCE WITH THE PROCUREMENT ARRANGEMENTS ENTERED INTO WITH THE RELEVANT NETWORK OPERATOR | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-2065 | V1.0 for Public consultation version | 3 | 21 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each notified DSO, Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and b) make available the measures implemented on its installations. | no text proposal (yet). | How will this be done in practice for new type A PGMs? This sounds unworkable, especially the confirmation. Even if the number of new type A PGMs being part of the restoration plan might be limited in the beginning, this number will rise in the future. Furthermore, by only picking out a number of new type A PGMs, there may be a risk of discrimination because of not treating all new type A PGMs in the same way.
0005-e495-5e7a-d54d-2200 | V1.0 for Public consultation version | 3 | 21 | 4 |  | 2014-12-08 21:33 | Wilch | RWE | final | Each notified DSO, Significant Grid User and new type A Power Generating Module shall: a) implement the measures notified to them and confirm this implementation to the notifying Network Operator; and b) make available the measures implemented on its installations. | no text proposal (yet). | How will this be done in practice for new type A PGMs? This sounds unworkable, especially the confirmation. Even if the number of new type A PGMs being part of the restoration plan might be limited in the beginning, this number will rise in the future. Furthermore, by only picking out a number of new type A PGMs, there may be a risk of discrimination because of not treating all new type A PGMs in the same way. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2254 | V1.0 for Public consultation version | 3 | 21 | 11 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each TSO shall: a) notify DSOs the measures of the System Defense Plan which are to be implemented, on their installations and/or the installations of Significant Grid Users and new type A, Power Generating Modules connected to their Distribution System, including the deadlines for implementation; |  | Again - here we have notification only. A consumer/PV owner will be notified what they have to do by the TSO or by the DSO. This notification simply includes deadlines for compliance. There is no discussion of cost mitigation for example
0005-9689-2807-a36c-e6a6 | V1.0 for Public consultation version | 3 | 22 | 2 | - | 2014-12-07 12:51:42 | Herve MELJAC | EUR | final | Each DSO and Significant Grid User shall execute the Restoration Plan instructions issued by the TSO, according to Restoration Plan procedures. | Each DSO and Significant Grid User shall execute the Restoration Plan instructions issued by the TSO, according to Restoration Plan procedures, while respecting their technical, legal and operating permit constraints.. | SGUs ability to execute has to be taken into account. |  |  | legal |  |  |  | Non-confidential
0005-bd85-2915-23fb-b6c1 | V1.0 for Public consultation version | 3 | 22 | 2 | - | 2014-12-08 17:01:21 | Jasmina PIERRE | EdF | final | Each DSO and Significant Grid User shall execute the Restoration Plan instructions issued by the TSO, according to Restoration Plan procedures. | Each DSO and Significant Grid User shall execute the Restoration Plan instructions issued by the TSO, according to Restoration Plan procedures, while respecting their technical constraints. | It is essential all the instructions given by the TSO for execution respect the respective technical constraints and minimize related impacts for grid users. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-1841 | V1.0 for Public consultation version | 3 | 22 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each DSO and Significant Grid User shall execute the Restoration Plan instructions issued by the TSO, according to Restoration Plan procedures. | Each DSO and Significant Grid User shall execute the Restoration Plan instructions issued by the TSO, according to Restoration Plan procedures AND, IN THE CASE OF SIGNIFICANT GRID USERS, IN ACCORDANCE WITH THE PROCUREMENT ARRANGEMENTS ENTERED INTO WITH THE RELEVANT NETWORK OPERATOR. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-2066 | V1.0 for Public consultation version | 3 | 22 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Example: If the Power Plant, owned by party A, falls in island operation and the neighbour power plant, owned by party B, who has a black start contract, falls in blach out. It cannot be true that party A has to take the risks for grid restoration, where party B was payed for it during several years. These kind of situations must be covered.
0005-e495-5e7a-d54d-2201 | V1.0 for Public consultation version | 3 | 22 | 3 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Add new paragraph. | All measures of the Restoration Plan that are activated either automatically or manually shall be notified without delay to the NRAs and the concerned Member State(s) by the TSO. | The Restoration Plan is a key element of the NC ER and it is important, for the sake of openness and transparency, that any measure(s) activated is notified to NRAs and Member States immediately. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1843 | V1.0 for Public consultation version | 3 | 22 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Xyz | ALL MEASURED OF THE RESTORATION PLAN THAT ARE ACTIVATED EITHER AUTOMATICALLY OR MANUALLY SHALL BE NOTIFIED WITHOUT DELAY TO THE NRA(S) AND THE MEMBER STATE(S) BY THE TSO. | The Restoration Plan is a key element of the NC E&R and its important, in the interest of openness and transparency, that any measure(s) activated is notified to the NRAs and Member States immediately.
0005-2159-9cec-0c50-2d5a | V1.0 for Public consultation version | 3 | 22 | - | - | 2014-12-08 17:15:43 | Paul Doyle | ESB Generation & Wholesale Markets | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Example: If the Power Plant, owned by party A, falls in island operation and the neighbour power plant, owned by party B, who has a black start contract, falls in blach out. It cannot be true that party A has to take the risks for grid restoration, where party B was payed for it during several years. These kind of situations must be covered! |  |  | legal |  |  |  | Non-confidential
0005-6f66-a4a0-e6a5-d057 | V1.0 for Public consultation version | 3 | 22 | - | - | 2014-11-28 15:52:11 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Add new Article | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | Example: If the Power Plant, owned by party A, falls in island operation and the neighbour power plant, owned by party B, who has a black start contract, falls in blach out. It cannot be true that party A has to take the risks for grid restoration, where party B was payed for it during several years. These kind of situations must be covered! |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2202 | V1.0 for Public consultation version | 3 | 23 | 1 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | The Re-energisation procedure of the Restoration Plan shall contain a set of measures based on the strategies to be used by the TSOs. | The Re-energisation procedure of the Restoration Plan shall contain a set of measures based on the strategies to be used by the TSO. These strategies, which shall be subject to NRA approval, shall include (…) | The Restoration Plan is a key element of the NC ER and within this the re-energisation procedure is critical. This must be subject of the NRA approval. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1844 | V1.0 for Public consultation version | 3 | 23 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | The Re-energisation procedure of the Restoration Plan shall contain a set of measures based on the strategies to be used by the TSO. These strategies shall include | The Re-energisation procedure of the Restoration Plan shall contain a set of measures based on the strategies to be used by the TSO. These strategies, WHICH SHALL BE SUBMITTED BY THE TSO TO THE NRA(S) FOR APPROVAL, shall include | The Restoration Plan is a key element of the NC E&R and within this the re-energisation procedure is critical. Given this the strategies are the building block for this and MUST be subject to explicit NRA approval. If an NRA is unable / unwilling to do this then they should be able to ask ACER to do it on their behalf.
0005-bd85-1130-3dec-90e5 | V1.0 for Public consultation version | 3 | 24 | 1 | - | 2014-12-05 10:59:19 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final |  | new paragraph: In the ccordination with the TSO, DSO can start island operation in his own network | An important part of the Restoration Plan is the choice of the power sources capable of re-energisation located within the Responsibility Area. Each TSO needs to be able to re-energise its system using a Bottom-up Re-energisation Strategy if necessary. For this the TSO shall identify the power sources with the required capability in its Responsibility Area, and appoint the ones necessary to be able to complete the Bottom-up Re-energisation Strategy. Perhaps it makes sense that the TSO delegates some responsibilities to DSOs at the beginning of a bottom-up re-energisation with the aim that the DSOs shall independently take care for the regional re-energisation and thereby relieve the TSO in his parent tasks. These regional re-energized areas can be the starting point for the further restoration of the TSO |  |  | legal |  |  |  | Non-confidential
0005-96b1-c3fc-0de0-8831 | V1.0 for Public consultation version | 3 | 24 | 1 | - | 2014-12-08 17:15:46 | Paul Doyle | ESB Generation & Wholesale Markets | final | add new sub paragraph | d) the high priority grid users | Also high priority grid users (such as nuclear power plants) must be taken into account! |  |  | legal |  |  |  | Non-confidential
0005-4869-5025-26b7-2e4d | V1.0 for Public consultation version | 3 | 24 | 1 | - | 2014-12-08 17:01:21 | Jasmina PIERRE | EdF | final | 1. When activating the Re-energisation procedure, each TSO shall define on strategy to apply, taking into account: […] | 1. When activating the Re-energisation procedure, each TSO shall define on strategy to apply, taking into account: […] d) the "high priority grid users" pursuant to Article 32(10) [NC OS] | It is essential TSO to take into account specific needs of specific grid users in terms of the conditions for their disconnection and re-energizing. |  |  | technical |  |  |  | Non-confidential
0005-96c6-db50-e7d1-de56 | V1.0 for Public consultation version | 3 | 24 | 1 | - | 2014-11-28 15:52:12 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | add new sub paragraph | d) the high priority grid users | Also high priority grid users (such as nuclear power plants) must be taken into account! |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2067 | V1.0 for Public consultation version | 3 | 24 | 1 | d | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | add new sub paragraph | d) the high priority grid users | Also high priority grid users (such as nuclear power plants) must be taken into account.
0005-e495-5e7a-d54d-2203 | V1.0 for Public consultation version | 3 | 24 | 1 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | When activating the Re-energisation procedure, each TSO shall define on strategy to apply, taking into account (…) | When activating the Re-energisation procedure, each TSO shall define, subject to NRA approval, a strategy to apply, taking into account (…) | The Restoration Plan is a key element of the NC ER and within this the re-energisation procedure is critical. This must be subject of the NRA approval. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2244 | V1.0 for Public consultation version | 3 | 24 | 1 |  | 2014-12-08 12:24 | Wolfram Heckmann | Fraunhofer IWES | final | “b) expected duration of possible Re-energization strategies…” |  | DSOs with islanding capability should be informed about the expected duration to decide whether to start re-energization of their network area bottom-up.
0005-e495-5e7a-d54d-1846 | V1.0 for Public consultation version | 3 | 24 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | When activating the Re-energisation procedure, each TSO shall define on strategy to apply, taking into account | When activating the Re-energisation procedure, each TSO shall define on A strategy to apply, taking into account | Typo
0005-e495-5e7a-d54d-1848 | V1.0 for Public consultation version | 3 | 24 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | When activating the Re-energisation procedure, each TSO shall define on strategy to apply, taking into account | When activating the Re-energisation procedure, each TSO shall define, SUBJECT TO NRA APPROVAL, on A strategy to apply, taking into account | The Restoration Plan is a key element of the NC E&R and within this the re-energisation procedure is critical. Given this the strategies are the building block for this and MUST be subject to explicit NRA approval. If an NRA is unable / unwilling to do this then they should be able to ask ACER to do it on their behalf.
0005-4855-4eae-0de0-99ea | V1.0 for Public consultation version | 3 | 24 | 2 | - | 2014-12-08 17:15:47 | Paul Doyle | ESB Generation & Wholesale Markets | final | During Re-energisation, each TSO shall manage the connection of Demand and generation with the aim of maintaining the Frequency close to the Nominal Frequency with a maximum tolerance of the Maximum Steady-State Frequency Deviation. | During Re-energisation, each TSO shall manage the connection of Demand and generation with the aim of maintaining the Frequency close to the Nominal Frequency with a maximum tolerance of the Maximum Steady-State Frequency Deviation as specified in NC LFC&R Article 11 | The maximum frequency tolerance must be specified in line with NC LFC&R, Articles 11 |  |  | legal |  |  |  | Non-confidential
0005-bdd6-6602-e9c5-c314 | V1.0 for Public consultation version | 3 | 24 | 2 | - | 2014-11-28 15:52:13 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | During Re-energisation, each TSO shall manage the connection of Demand and generation with the aim of maintaining the Frequency close to the Nominal Frequency with a maximum tolerance of the Maximum Steady-State Frequency Deviation. | During Re-energisation, each TSO shall manage the connection of Demand and generation with the aim of maintaining the Frequency close to the Nominal Frequency with a maximum tolerance of the Maximum Steady-State Frequency Deviation as specified in NC LFC&R Article 11 | The maximum frequency tolerance must be specified in line with NC LFC&R, Articles 11 |  |  | legal |  |  |  | Non-confidential
0005-6f8d-ac6f-2926-12be | V1.0 for Public consultation version | 3 | 24 | 2 | - | 2014-12-08 16:38:48 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | During Re-energisation, each TSO shall manage the connection of Demand and generation with the aim of maintaining the Frequency close to the Nominal Frequency with a maximum tolerance of the Maximum Steady-State Frequency Deviation. | During Re-energisation, each TSO shall manage the connection of Demand and generation with the aim of maintaining the Frequency close to the Nominal Frequency with a maximum tolerance of the Maximum Steady-State Frequency Deviation as specified in NC LFC&R Article 11 | The maximum frequency tolerance must be specified in line with NC LFC&R, Articles 11 | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-2330 | V1.0 for Public consultation version | 3 | 24 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | During Re-energisation, each TSO shall manage the connection of Demand and generation with the aim of maintaining the Frequency close to the Nominal Frequency with a maximum tolerance of the Maximum Steady-State Frequency Deviation. | no text proposal. | Is this intended to be reactive 'monitoring' or proactive 'management'? Proactive management would be realistic for larger demand and generation carried out in coordination with the DSO. |  |  | Technical
0005-e495-5e7a-d54d-2068 | V1.0 for Public consultation version | 3 | 24 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | During Re-energisation, each TSO shall manage the connection of Demand and generation with the aim of maintaining the Frequency close to the Nominal Frequency with a maximum tolerance of the Maximum Steady-State Frequency Deviation. | During Re-energisation, each TSO shall manage the connection of Demand and generation with the aim of maintaining the Frequency close to the Nominal Frequency with a maximum tolerance of the Maximum Steady-State Frequency Deviation as specified in NC LFC&R Article 11 | The maximum frequency tolerance must be specified in line with NC LFC&R, Articles 11
0005-e495-5e7a-d54d-2331 | V1.0 for Public consultation version | 3 | 24 | 3 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | The TSO shall take into account the automatic connection of Demand and generation within its LFC Area in Frequency management. | no text proposal. | In order to do this the TSO will need to be aware of automatic connection of demand and generation - there would need to be some process for the relevant party to inform the TSO of such demand / generation. |  |  | Technical
0005-2159-104c-0ea8-256b | V1.0 for Public consultation version | 3 | 24 | 4 | - | 2014-12-08 17:15:49 | Paul Doyle | ESB Generation & Wholesale Markets | final | During Re-energisation, DSOs shall, after being consulted by the TSO, connect the amount of generation and Demand requested by the TSO. | During Re-energisation, DSOs shall, in coordination and collaboration with the TSO, connect the agreed part of their Network. | It is important to have a clear coordination and collaboration between the DSO and the TSO. Consultation (as described in art. 5) does not provide for this. The DSO is not able to predict the amount of generation or demand in parts of it's grid. |  |  | technical |  |  |  | Non-confidential
0005-6fa2-2f52-e835-cd93 | V1.0 for Public consultation version | 3 | 24 | 4 | - | 2014-11-28 15:52:13 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | During Re-energisation, DSOs shall, after being consulted by the TSO, connect the amount of generation and Demand requested by the TSO. | During Re-energisation, DSOs shall, in coordination and collaboration with the TSO, connect the agreed part of their Network. | It is important to have a clear coordination and collaboration between the DSO and the TSO. Consultation (as described in art. 5) does not provide for this. The DSO is not able to predict the amount of generation or demand in parts of it's grid. |  |  | technical |  |  |  | Non-confidential
0005-96c5-0071-2ab6-b2ce | V1.0 for Public consultation version | 3 | 24 | 4 | - | 2014-12-08 16:38:50 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | During Re-energisation, DSOs shall, after being consulted by the TSO, connect the amount of generation and Demand requested by the TSO. | During Re-energisation, DSOs shall, in coordination and collaboration with the TSO, connect the agreed part of their Network. | It is important to have a clear coordination and collaboration between the DSO and the TSO. Consultation (as described in art. 5) does not provide for this. The DSO is not able to predict the amount of generation or demand in parts of it's grid. | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-2332 | V1.0 for Public consultation version | 3 | 24 | 4 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | During Re-energisation, DSOs shall, after being consulted by the TSO, connect the amount of generation and Demand requested by the TSO. | During Re-energisation, DSOs shall, after being consulted by in coordination and collaboration with the TSO, connect the amount of generation and Demand requested by the TSO. | It is important to have a clear coordination and collaboration between the DSO and the TSO. Consultation (as described in art. 5) does not provide for this. It has also to be said that DSOs don't really have control over 'the amount of' generation or customers demand - all they can do is re-energise their network to connect customers (connect and disconnect MV lines). DSOs can make assumptions on the generation and demand that might be imposed on the transmission system as a consequence (there may also be some power restrictions imposed). |  |  | Technical
0005-e495-5e7a-d54d-2069 | V1.0 for Public consultation version | 3 | 24 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | During Re-energisation, DSOs shall, after being consulted by the TSO, connect the amount of generation and Demand requested by the TSO. | During Re-energisation, DSOs shall, in coordination and collaboration with the TSO, connect the agreed part of their Network. | It is important to have a clear coordination and collaboration between the DSO and the TSO. Consultation (as described in art. 5) does not provide for this. The DSO is not able to predict the amount of generation or demand in parts of it's grid.
0005-e495-5e7a-d54d-2204 | V1.0 for Public consultation version | 3 | 24 | 4 |  | 2014-12-08 21:33 | Wilch | RWE | final | During Re-energisation, DSOs shall, after being consulted by the TSO, connect the amount of generation and Demand requested by the TSO. | During Re-energisation, DSOs shall, in coordination and collaboration with the TSO, connect the agreed part of their Network. | It is important to have a clear coordination and collaboration between the DSO and the TSO. Consultation (as described in Art. 5) does not provide this. The DSO is not able to predict the amount of generation or demand in parts of it's grid. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1850 | V1.0 for Public consultation version | 3 | 24 | 4 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | During Re-energisation, DSOs shall, after being consulted by the TSO, connect the amount of generation and Demand requested by the TSO. | During Re-energisation, DSOs shall, after being consulted by the TSO, connect the amount of generation and / OR Demand requested by the TSO. | Typo
0005-96c5-c3df-2926-7a42 | V1.0 for Public consultation version | 3 | 24 | 5 | - | 2014-12-08 16:38:52 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | When considering the activation of Top-down Re-energisation Strategy, the TSO shall request neighbouring TSOs to support the Re-energisation. The requested TSO shall provide assistance for the Re-energisation, unless it would lead its system to Emergency or Blackout States. In this case, the requesting TSO shall use the Bottom-Up Re-energisation Strategy. | When considering the activation of Top-down Re-energisation Strategy, the TSO shall request all relevant neighbouring TSOs to support the Re-energisation. The requested TSO shall provide assistance for the Re-energisation, unless it would lead its system to Emergency or Blackout States. In this case, the requesting TSO shall use the Bottom-Up Re-energisation Strategy. | It must be clear that all Relevant TSOs have to be asked for support. | [6 empty] | Non-confidential
0005-2195-ac8c-0c50-173d | V1.0 for Public consultation version | 3 | 24 | 5 | - | 2014-12-08 17:15:51 | Paul Doyle | ESB Generation & Wholesale Markets | final | When considering the activation of Top-down Re-energisation Strategy, the TSO shall request neighbouring TSOs to support the Re-energisation. The requested TSO shall provide assistance for the Re-energisation, unless it would lead its system to Emergency or Blackout States. In this case, the requesting TSO shall use the Bottom-Up Re-energisation Strategy. | When considering the activation of Top-down Re-energisation Strategy, the TSO shall request all relevant neighbouring TSOs to support the Re-energisation. The requested TSO shall provide assistance for the Re-energisation, unless it would lead its system to Emergency or Blackout States. In this case, the requesting TSO shall use the Bottom-Up Re-energisation Strategy. | It must be clear that all Relevant TSOs have to be asked for support. |  |  | technical |  |  |  | Non-confidential
0005-215a-1800-e8fd-286f | V1.0 for Public consultation version | 3 | 24 | 5 | - | 2014-11-28 15:52:14 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | When considering the activation of Top-down Re-energisation Strategy, the TSO shall request neighbouring TSOs to support the Re-energisation. The requested TSO shall provide assistance for the Re-energisation, unless it would lead its system to Emergency or Blackout States. In this case, the requesting TSO shall use the Bottom-Up Re-energisation Strategy. | When considering the activation of Top-down Re-energisation Strategy, the TSO shall request all relevant neighbouring TSOs to support the Re-energisation. The requested TSO shall provide assistance for the Re-energisation, unless it would lead its system to Emergency or Blackout States. In this case, the requesting TSO shall use the Bottom-Up Re-energisation Strategy. | It must be clear that all Relevant TSOs have to be asked for support. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2333 | V1.0 for Public consultation version | 3 | 24 | 5 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | When considering the activation of Top-down Re-energisation Strategy, the TSO shall request neighbouring TSOs to support the Re-energisation. The requested TSO shall provide assistance for the Re-energisation, unless it would lead its system to Emergency or Blackout States. In this case, the requesting TSO shall use the Bottom-Up Re-energisation Strategy. | When considering the activation of Top-down Re-energisation Strategy, the TSO shall request all neighbouring TSOs to support the Re-energisation. The requested TSOs shall provide assistance for the Re-energisation, unless it would lead their system to Emergency or Blackout States. In this case, the requesting TSO shall use the Bottom-Up Re-energisation Strategy. | It must be clear that all TSOs have to be asked for support. |  |  | Technical
0005-e495-5e7a-d54d-2070 | V1.0 for Public consultation version | 3 | 24 | 5 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | When considering the activation of Top-down Re-energisation Strategy, the TSO shall request neighbouring TSOs to support the Re-energisation. The requested TSO shall provide assistance for the Re-energisation, unless it would lead its system to Emergency or Blackout States. In this case, the requesting TSO shall use the Bottom-Up Re-energisation Strategy. | When considering the activation of Top-down Re-energisation Strategy, the TSO shall request all relevant neighbouring TSOs to support the Re-energisation. The requested TSO shall provide assistance for the Re-energisation, unless it would lead its system to Emergency or Blackout States. In this case, the requesting TSO shall use the Bottom-Up Re-energisation Strategy. | It must be clear that all Relevant TSOs have to be asked for support.
0005-e495-5e7a-d54d-2205 | V1.0 for Public consultation version | 3 | 24 | 6 |  | 2014-12-08 21:33 | AG | RWE | final | Add new paragraph. | All costs resulting from actions and requirements mentioned in this Code will be handeled as system operational costs and as such be borne by the TSO. | There needs to be a clear reference to cost recovery to avoid the costs of providing support to another TSO in an Emergency, Black Start or Restoration State falling upon consumers in another TSO's area. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1852 | V1.0 for Public consultation version | 3 | 25 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | The Frequency management procedure of the Restoration Plan shall contain a set of measures aiming at restoring System Frequency back to Nominal Frequency. | Xyz | This is a new term and should be defined / set out in the definitions, if only (as a minimum) by reference to this Article.
0005-e495-5e7a-d54d-1854 | V1.0 for Public consultation version | 3 | 26 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | [title] Appointment of Frequency Leaders | Appointment AND OBLIGATIONS of Frequency Leaders | The title of the article should set out what’s expected – in this case its not just the appointment but also what the leader is being obliged to do.
0005-4855-4e91-2a52-8912 | V1.0 for Public consultation version | 3 | 26 | 4 | - | 2014-12-08 16:38:54 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | The TSO with the highest K-factor under operation as defined in Article 45 [NC LFCR] shall be appointed as the Frequency Leader, unless all TSOs of the Synchronised Region, or of the Synchronous Area, agree to appoint another TSO as the Frequency Leader. In that case, all TSOs of the Synchronised Region, or of the Synchronous Area, shall consider the following criteria: | The TSO with the highest K-factor under operation as defined in Article 45 [NC LFCR] shall be appointed as the Frequency Leader, unless all TSOs of the Synchronised Region, or of the Synchronous Area, agree to appoint another TSO as the Frequency Leader. In that case, all TSOs of the Synchronised Region, or of the Synchronous Area, shall consider the following criteria: | K-factor not included in definitions. Please define all terms used in the network code. | [6 empty] | Non-confidential
0005-bdd5-279e-0cb4-d58d | V1.0 for Public consultation version | 3 | 26 | 4 | - | 2014-12-08 17:15:53 | Paul Doyle | ESB Generation & Wholesale Markets | final | The TSO with the highest K-factor under operation as defined in Article 45 [NC LFCR] shall be appointed as the Frequency Leader, unless all TSOs of the Synchronised Region, or of the Synchronous Area, agree to appoint another TSO as the Frequency Leader. In that case, all TSOs of the Synchronised Region, or of the Synchronous Area, shall consider the following criteria: | The TSO with the highest K-factor under operation as defined in Article 45 [NC LFCR] shall be appointed as the Frequency Leader, unless all TSOs of the Synchronised Region, or of the Synchronous Area, agree to appoint another TSO as the Frequency Leader. In that case, all TSOs of the Synchronised Region, or of the Synchronous Area, shall consider the following criteria: | K-factor not included in definitions. Please define all terms used in the network code. |  |  | technical |  |  |  | Non-confidential
0005-9676-0860-e961-250d | V1.0 for Public consultation version | 3 | 26 | 4 | - | 2014-11-28 15:52:15 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The TSO with the highest K-factor under operation as defined in Article 45 [NC LFCR] shall be appointed as the Frequency Leader, unless all TSOs of the Synchronised Region, or of the Synchronous Area, agree to appoint another TSO as the Frequency Leader. In that case, all TSOs of the Synchronised Region, or of the Synchronous Area, shall consider the following criteria: | The TSO with the highest K-factor under operation as defined in Article 45 [NC LFCR] shall be appointed as the Frequency Leader, unless all TSOs of the Synchronised Region, or of the Synchronous Area, agree to appoint another TSO as the Frequency Leader. In that case, all TSOs of the Synchronised Region, or of the Synchronous Area, shall consider the following criteria: | K-factor not included in definitions. Please define all terms used in the network code. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2071 | V1.0 for Public consultation version | 3 | 26 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The TSO with the highest K-factor under operation as defined in Article 45 [NC LFCR] shall be appointed as the Frequency Leader, unless all TSOs of the Synchronised Region, or of the Synchronous Area, agree to appoint another TSO as the Frequency Leader. In that case, all TSOs of the Synchronised Region, or of the Synchronous Area, shall consider the following criteria: | The TSO with the highest K-factor under operation as defined in Article 45 [NC LFCR] shall be appointed as the Frequency Leader, unless all TSOs of the Synchronised Region, or of the Synchronous Area, agree to appoint another TSO as the Frequency Leader. In that case, all TSOs of the Synchronised Region, or of the Synchronous Area, shall consider the following criteria: | K-factor not included in definitions. Please define all terms used in the network code.
0005-e495-5e7a-d54d-2206 | V1.0 for Public consultation version | 3 | 26 | 4 |  | 2014-12-08 21:33 | Wilch | RWE | final | The TSO with the highest K-factor under operation as defined in Article 45 [NC LFCR] shall be appointed as the Frequency Leader, unless all TSOs of the Synchronised Region, or of the Synchronous Area, agree to appoint another TSO as the Frequency Leader. In that case, all TSOs of the Synchronised Region, or of the Synchronous Area, shall consider the following criteria: | The TSO with the highest K-factor under operation as defined in Article 45 [NC LFCR] shall be appointed as the Frequency Leader, unless all TSOs of the Synchronised Region, or of the Synchronous Area, agree to appoint another TSO as the Frequency Leader. In that case, all TSOs of the Synchronised Region, or of the Synchronous Area, shall consider the following criteria: | K-factor not included in definitions. Might be considered as a comment on Article 2. | 1 | 5 | Technical | Editorial
0005-e495-5e7a-d54d-2207 | V1.0 for Public consultation version | 3 | 26 | 5 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | When a TSO is appointed as Frequency Leader of a Synchronised Region, this TSO shall inform all other TSOs of the Synchronous Area of its appointment. | When a TSO is appointed as Frequency Leader of a Synchronised Region, this TSO shall inform all other TSOs, NRAs, DSOs and Significant Grid Users of the Synchronous Area of its appointment. | For the sake of openess and transparency, it's important that NRAs are fully informed about all actions taken during the System Restoration phase. Also other parties must be informed. Otherwise the DSOs and Significant Grid Users will not know which instructions to follow- those of the TSO (who is not the leader) or a neighbouring TSO, whom they do not deal with normally (but who is the leader). |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1855 | V1.0 for Public consultation version | 3 | 26 | 5 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | When a TSO is appointed as Frequency Leader of a Synchronised Region, this TSO shall inform all other TSOs of the Synchronous Area of its appointment. | When a TSO is appointed as Frequency Leader of a Synchronised Region, this TSO shall inform all other TSOs AND NRAS of the Synchronous Area of its appointment. | In the interest of openness and transparency its important that NRAs are fully informed about all actions taken during the system Restoration phase.
0005-e495-5e7a-d54d-1857 | V1.0 for Public consultation version | 3 | 26 | 5 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | When a TSO is appointed as Frequency Leader of a Synchronised Region, this TSO shall inform all other TSOs of the Synchronous Area of its appointment. | When a TSO is appointed as Frequency Leader of a Synchronised Region, this TSO shall inform all other TSOs NRAS, DSOS AND SIGNIFICANT GRID USERS of the Synchronous Area of its appointment. | Given the statements in Art 27(3) and Art 28 (3) about the Frequency Leader managing the manual activation of FRR and RR then if this involves them contacting parties such as DSOs or SGUs then those parties MUST be informed on the appointment of the Frequency Leader…. otherwise the DSO and / or SGU does not know whose instructions to follow – that from the TSO (who is not the leader) or a neighbouring TSO, whom they do not deal with normally (who is the leader).
0005-6f79-7770-a35d-ba9c | V1.0 for Public consultation version | 3 | 27 | 1 | - | 2014-12-04 14:21:44 | Dekinderen Eric | Genrator company | final | During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the manual activation of Frequency Restoration Reserves and Replacement Reserves. | During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the autonomous activation of Frequency Restoration Reserves and Replacement Reserves. | manaul activation at the demand of the Frquency Leader must remain possible |  |  | technical |  |  |  | Non-confidential
0005-9675-38f1-245f-ecc7 | V1.0 for Public consultation version | 3 | 27 | 1 | - | 2014-12-08 17:01:21 | Jasmina PIERRE | EdF | final | 1. During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the manual activation of Frequency Restoration Reserves and Replacement Reserves. | 1. During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the automatic activation of Frequency Restoration Reserves and Replacement Reserves. | Manual activation at the demand of the Frequency Leader should remain possible |  |  | technical |  |  |  | Non-confidential
0005-96b1-d37e-0ea8-f298 | V1.0 for Public consultation version | 3 | 27 | 1 | - | 2014-12-08 17:15:54 | Paul Doyle | ESB Generation & Wholesale Markets | final | During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the manual activation of Frequency Restoration Reserves and Replacement Reserves. | During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the autonomous activation of Frequency Restoration Reserves and Replacement Reserves. | manual activation at the demand of the Frequency Leader must remain possible |  |  | technical |  |  |  | Non-confidential
0005-96b2-1800-e76d-784c | V1.0 for Public consultation version | 3 | 27 | 1 | - | 2014-11-28 15:52:16 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the manual activation of Frequency Restoration Reserves and Replacement Reserves. | During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the autonomous activation of Frequency Restoration Reserves and Replacement Reserves. | manual activation at the demand of the Frequency Leader must remain possible |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2072 | V1.0 for Public consultation version | 3 | 27 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the manual activation of Frequency Restoration Reserves and Replacement Reserves. | During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the autonomous activation of Frequency Restoration Reserves and Replacement Reserves. | manual activation at the demand of the Frequency Leader must remain possible
0005-e495-5e7a-d54d-2073 | V1.0 for Public consultation version | 3 | 27 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the manual activation of Frequency Restoration Reserves and Replacement Reserves. |  | Article 27.1 establishes that mFRR and RR shall be suspended. And article 27.2, that the Frequency Leader shall define settings to be applied. This means that the Frequency Leader could change AGC parameters? Shouldn´t AGC (aFRR) be suspended too, until the Frequent Leader analyses the situation and provides proper instructions?
0005-e495-5e7a-d54d-2208 | V1.0 for Public consultation version | 3 | 27 | 1 |  | 2014-12-08 21:33 | EDK | GFS | final | During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the manual activation of Frequency Restoration Reserves and Replacement Reserves. | During system Restoration, when a Frequency Leader has been appointed according to Article 26(3), all TSOs of the Synchronous Area, with the exception of the Frequency Leader, shall suspend the autonomous activation of Frequency Restoration Reserves and Replacement Reserves. | Manual activation at the demand of the Frequency Leader must remain possible |  |  | Technical | Fundamental
0005-6fb5-38f0-a3c1-1839 | V1.0 for Public consultation version | 3 | 27 | 2 | - | 2014-12-04 14:24:25 | Dekinderen Eric | Genrator company | final | The Frequency Leader shall define, after consultation of the other TSOs of the Synchronous Area, on settings to be applied on the Load Frequency Control operated by each TSO of the Synchronous Area | NA | What is Load Frequency Control? Is this load shedding by frequency relays? When to apply the setting Can this not be defined in advance?? |  |  | technical |  |  |  | Non-confidential
0005-9689-75be-0c50-b72a | V1.0 for Public consultation version | 3 | 27 | 2 | - | 2014-12-08 17:15:56 | Paul Doyle | ESB Generation & Wholesale Markets | final | The Frequency Leader shall define, after consultation of the other TSOs of the Synchronous Area, on settings to be applied on the Load Frequency Control operated by each TSO of the Synchronous Area |  | It is not clear which settings are referred to in this clause. Clarity is required. |  |  | technical |  |  |  | Non-confidential
0005-e4be-a482-e6a5-a093 | V1.0 for Public consultation version | 3 | 27 | 2 | - | 2014-11-28 15:52:17 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The Frequency Leader shall define, after consultation of the other TSOs of the Synchronous Area, on settings to be applied on the Load Frequency Control operated by each TSO of the Synchronous Area |  | It is not clear which settings are referred to in this clause. Clarity is required. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2074 | V1.0 for Public consultation version | 3 | 27 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The Frequency Leader shall define, after consultation of the other TSOs of the Synchronous Area, on settings to be applied on the Load Frequency Control operated by each TSO of the Synchronous Area |  | It is not clear which settings are referred to in this clause. Clarity is required.
0005-e495-5e7a-d54d-2075 | V1.0 for Public consultation version | 3 | 27 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The Frequency Leader shall define, after consultation of the other TSOs of the Synchronous Area, on settings to be applied on the Load Frequency Control operated by each TSO of the |  | Article 27.1 establishes that mFRR and RR shall be suspended. And article 27.2, that the Frequency Leader shall define settings to be applied. This means that the Frequency Leader could change AGC parameters? Shouldn´t AGC (aFRR) be suspended too, until the Frequent Leader analyses the situation and provides proper instructions?
0005-e495-5e7a-d54d-2209 | V1.0 for Public consultation version | 3 | 27 | 2 |  | 2014-12-08 21:33 | EDK | GFS | final | The Frequency Leader shall define, after consultation of the other TSOs of the Synchronous Area, on settings to be applied on the Load Frequency Control operated by each TSO of the Synchronous Area |  | It is not clear which settings are referred to in this clause. Clarity is required. |  |  | Technical | Editorial
0005-969d-5024-a105-9972 | V1.0 for Public consultation version | 3 | 28 | 1 | - | 2014-12-04 14:24:58 | Dekinderen Eric | Genrator company | final | During system restoration, when a Frequency Leader has been appointed according to Article 26(2), all TSOs of each Synchronised Region, with the exception of the Frequency Leaders, shall suspend the manual activation of Frequency Restoration Reserves and Replacement Reserves. | During system restoration, when a Frequency Leader has been appointed according to Article 26(2), all TSOs of each Synchronised Region, with the exception of the Frequency Leaders, shall suspend the autonomous activation of Frequency Restoration Reserves and Replacement Reserves. | manaul activation at the demand of the Frquency Leader must remain possible |  |  | technical |  |  |  | Non-confidential
0005-2196-a4a0-e76d-c680 | V1.0 for Public consultation version | 3 | 28 | 1 | - | 2014-11-28 15:52:18 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | During system restoration, when a Frequency Leader has been appointed according to Article 26(2), all TSOs of each Synchronised Region, with the exception of the Frequency Leaders, shall suspend the manual activation of Frequency Restoration Reserves and Replacement Reserves. | During system Restoration, when a Frequency Leader has been appointed according to Article 26(2), all TSOs of each synchronised region, with the exception of the Frequency Leaders, shall suspend the autonomous activation of Frequency Restoration Reserves and Replacement Reserves. | manual activation at the demand of the Frequency Leader must remain possible |  |  | technical |  |  |  | Non-confidential
0005-bdad-2915-2526-605b | V1.0 for Public consultation version | 3 | 28 | 1 | - | 2014-12-08 17:02:04 | Jasmina PIERRE | EdF | final | 1. During system restoration, when a Frequency Leader has been appointed according to Article 26(2), all TSOs of each Synchronised Region, with the exception of the Frequency Leaders, shall suspend the manual activation of Frequency Restoration Reserves and Replacement Reserves. | 1. During system Restoration, when a Frequency Leader has been appointed according to Article 26(2), all TSOs of each synchronised region, with the exception of the Frequency Leaders, shall suspend the automatic activation of Frequency Restoration Reserves and Replacement Reserves. | Manual activation at the demand of the Frequency Leader should remain possible |  |  | technical |  |  |  | Non-confidential
0005-6f79-d360-0e44-bd7a | V1.0 for Public consultation version | 3 | 28 | 1 | - | 2014-12-08 17:15:58 | Paul Doyle | ESB Generation & Wholesale Markets | final | During system restoration, when a Frequency Leader has been appointed according to Article 26(2), all TSOs of each Synchronised Region, with the exception of the Frequency Leaders, shall suspend the manual activation of Frequency Restoration Reserves and Replacement Reserves. | During system Restoration, when a Frequency Leader has been appointed according to Article 26(2), all TSOs of each synchronised region, with the exception of the Frequency Leaders, shall suspend the autonomous activation of Frequency Restoration Reserves and Replacement Reserves. | manual activation at the demand of the Frequency Leader must remain possible |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2076 | V1.0 for Public consultation version | 3 | 28 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Synchronous Area. | During system Restoration, when a Frequency Leader has been appointed according to Article 26(2), all TSOs of each synchronised region, with the exception of the Frequency Leaders, shall suspend the autonomous activation of Frequency Restoration Reserves and Replacement Reserves. | manual activation at the demand of the Frequency Leader must remain possible
0005-6f8e-cb92-e6a5-e14d | V1.0 for Public consultation version | 3 | 29 | 1 | - | 2014-11-28 15:52:35 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | limits for maximum phase angle, frequency difference and voltage difference for closing lines. | limits for maximum phase angle, frequency difference and voltage difference for closing breakers to prevent overload and re-disconnection of the connection, used to re-synchronise, and to prevent any damages of equipment of connected Grid Users. | Breakers can be closed, lines can't. Limits must be specified! |  |  | legal |  |  |  | Non-confidential
0005-e4bd-1010-0c50-ae7a | V1.0 for Public consultation version | 3 | 29 | 1 | - | 2014-12-08 17:15:59 | Paul Doyle | ESB Generation & Wholesale Markets | final | limits for maximum phase angle, frequency difference and voltage difference for closing lines. | limits for maximum phase angle, frequency difference and voltage difference for closing breakers to prevent overload and re-disconnection of the connection, used to re-synchronise, and to prevent any damages of equipment of connected Grid Users. | Breakers can be closed, lines can't. Limits must be specified! |  |  | legal |  |  |  | Non-confidential
0005-e4a9-38d2-a1cd-b318 | V1.0 for Public consultation version | 3 | 29 | 1 | c | 2014-12-04 14:25:25 | Dekinderen Eric | Genrator company | final | limits for maximum phase angle, frequency difference and voltage difference for closing lines. | limits for maximum phase angle, frequency difference and voltage difference for connected synchroned regions | more general statement |  |  | technical |  |  |  | Non-confidential
0005-bdc1-75cc-d54d-8dbc | V1.0 for Public consultation version | 3 | 29 | 1 | c | 2014-12-08 23:56:25 | Gunnar Kaestle | Clausthal University of Technology | final | limits for maximum phase angle, frequency difference and voltage difference for closing lines | add recommended default values for these parameters | It's a very useful piece of information if the default values are given (even if they are eventually altered case by case) as it gives operators a hint how large the electromecanical impact will be during a synchronisation procedure when the breaker will be closed. |  |  | technical |  |  |  | Non-confidential
0005-e4bd-5e6b-2f68-f0cb | V1.0 for Public consultation version | 3 | 29 | 1 | c | 2014-12-08 18:18:38 | Thomas Willson |  | final | limits for maximum phase angle, frequency difference and voltage difference for closing lines | add recommended default values for these parameters | It's a very useful piece of information if the default values are given (even if they are eventually altered case by case) as it gives operators a hint how large the electromecanical impact will be during a synchronisation procedure when the breaker will be closed. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2077 | V1.0 for Public consultation version | 3 | 29 | 1 | c | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | limits for maximum phase angle, frequency difference and voltage difference for closing lines. | limits for maximum phase angle, frequency difference and voltage difference for closing breakers to prevent overload and re-disconnection of the connection, used to re-synchronise, and to prevent any damages of equipment of connected Grid Users. | Breakers can be closed, lines can't. Limits must be specified.
0005-e495-5e7a-d54d-2334 | V1.0 for Public consultation version | 3 | 29 | 1 | c | 2014-12-08 22:31 | Michael Wilch | RWE | final | limits for maximum phase angle, frequency difference and voltage difference for closing lines. | limits for maximum phase angle, frequency difference and voltage difference for closing lines breakers. | Breakers can be closed, lines can't. |  |  | Technical
0005-e495-5e7a-d54d-2078 | V1.0 for Public consultation version | 3 | 29 | 3 | d | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | be able to control the Voltage at potential Resynchronisation Points. | be able to control the Voltage angle and amplitude at potential Resynchronisation Points. | Make clear that voltage angle as well as amplitude must be controllable.
0005-e4d2-3f2e-e8fd-e333 | V1.0 for Public consultation version | 3 | 29 | - | - | 2014-11-28 15:52:35 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | be able to control the Voltage at potential Resynchronisation Points. | be able to control the Voltage angle and amplitude at potential Resynchronisation Points. | Make clear that voltage angle as well as amplitude must be controllable! |  |  | technical |  |  |  | Non-confidential
0005-6f8d-c3c0-0ea8-977e | V1.0 for Public consultation version | 3 | 29 | - | - | 2014-12-08 17:16:47 | Paul Doyle | ESB Generation & Wholesale Markets | final | be able to control the Voltage at potential Resynchronisation Points. | be able to control the Voltage angle and amplitude at potential Resynchronisation Points. | Make clear that voltage angle as well as amplitude must be controllable! |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2210 | V1.0 for Public consultation version | 3 | 30 | 4 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | When a TSO is appointed as Resynchronisation Leader of a pair of Synchronised Region, this TSO shall inform all other TSOs of the Synchronous Area of its appointment. | When a TSO is appointed as Resynchronisation Leader of a pair of Synchronised Region, this TSO shall inform all other TSOs, NRAs and market participants of the Synchronous Area of its appointment. | or the sake of openess and transparency, it's important that NRAs are fully informed about all actions taken during the System Restoration phase. Also other parties must be informed. Otherwise the DSOs and Significant Grid Users will not know which instructions to follow- those of the TSO (who is not the leader) or a neighbouring TSO, whom they do not deal with normally (but who is the leader). |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1859 | V1.0 for Public consultation version | 3 | 30 | 4 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | When a TSO is appointed as Resynchronisation Leader of a pair of Synchronised Regions, this TSO shall inform all other TSOs of the Synchronous Area of its appointment. | When a TSO is appointed as Resynchronisation Leader of a pair of Synchronised Regions, this TSO shall inform all other TSOs AND NRAS of the Synchronous Area of its appointment. | In the interest of openness and transparency its important that NRAs are fully informed about all actions taken during the system Restoration phase.
0005-2182-db6e-e9c5-e0c9 | V1.0 for Public consultation version | 3 | 31 | 1 | - | 2014-11-28 15:52:36 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Prior to Resynchronisation, the Resynchronisation Leader shall: a) define, after consultation of the Frequency Leaders of the involved Synchronised Regions: i. maximum difference between Frequencies of the two Synchronised Regions; ii. maximum Active and Reactive Power exchange; and iii. settings to be applied on the Load Frequency Control. | Remove this article here. It must be part of the Restoration Plan. | those values should in advance be defined in the restoration plan, not at the moment of a resynchronisation |  |  | technical |  |  |  | Non-confidential
0005-e495-00ba-d3bd-f920 | V1.0 for Public consultation version | 3 | 31 | 1 | - | 2014-12-08 23:56:25 | Gunnar Kaestle | Clausthal University of Technology | final | i. maximum difference between frequencies of the two synchronised regions | remove clause i. | redundancy alert: frequency difference is already defined in 29(1)c |  |  | technical |  |  |  | Non-confidential
0005-4855-c3c0-0d7b-42fb | V1.0 for Public consultation version | 3 | 31 | 1 | - | 2014-12-08 17:16:49 | Paul Doyle | ESB Generation & Wholesale Markets | final | Prior to Resynchronisation, the Resynchronisation Leader shall: a) define, after consultation of the Frequency Leaders of the involved Synchronised Regions: i. maximum difference between Frequencies of the two Synchronised Regions; ii. maximum Active and Reactive Power exchange; and iii. settings to be applied on the Load Frequency Control. | Remove this article here. It must be part of the Restoration Plan. | those values should in advance be defined in the restoration plan, not at the moment of a resynchronisation |  |  | technical |  |  |  | Non-confidential
0005-bd85-7752-a35d-4f81 | V1.0 for Public consultation version | 3 | 31 | 1 | a | 2014-12-04 14:26:41 | Dekinderen Eric | Genrator company | final | i. maximum difference between Frequencies of the two Synchronised Regions; ii. maximum Active and Reactive Power exchange; and iii. settings to be applied on the Load Frequency Control. | Dedicated paragraph | All those values should be defined in advance, not at the moment of a resynchronisation |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2079 | V1.0 for Public consultation version | 3 | 31 | 1 | a | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Prior to Resynchronisation, the Resynchronisation Leader shall: a) define, after consultation of the Frequency Leaders of the involved Synchronised Regions: i. maximum difference between Frequencies of the two Synchronised Regions; ii. maximum Active and Reactive Power exchange; and iii. settings to be applied on the Load Frequency Control. | Remove this article here. It must be part of the Restoration Plan. | those values should in advance be defined in the restoration plan, not at the moment of a resynchronisation
0005-e495-5e7a-d54d-1861 | V1.0 for Public consultation version | 3 | 31 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Frequency Leaders shall inform all TSOs within their Synchronised Regions of the planned Resynchronisation. | Frequency Leaders shall inform all TSOs NRAS AND MARKET PARTICIPANTS within their Synchronised Regions of the planned Resynchronisation. | In the interest of openness and transparency its important that NRAs are fully informed about all actions taken during the system Restoration phase. In addition to NRAs as this resynchronisation is a major step to restoring the market(s) its important that market participants are informed as well.
0005-bd99-11c2-a03d-18c4 | V1.0 for Public consultation version | 4 | 32 | 1 | - | 2014-12-04 14:27:03 | Dekinderen Eric | Genrator company | final | See Eurelectric proposal | See Eurelectric proposal | See Eurelectric proposal |  |  | legal |  |  |  | Non-confidential
0005-bdad-c591-2652-5afa | V1.0 for Public consultation version | 4 | 32 | 1 | - | 2014-12-08 17:07:35 | Jasmina PIERRE | EdF | final | 1. The settlement rules and principles defined in Chapter 5 of [NC Electricity Balancing] shall be applicable during Emergency State. | 1. The settlement rules and principles defined in Chapter 5 of [NC Electricity Balancing] shall be applicable during mid-scale Emergency State. They shall not be applicable during a large-scale Emergency State or Blackout State as defined under Article [32 bis]. Cost recovery should be done according to the principles defined in Article [36] where the TSO(s) is acting as a central dispatcher and passing through the costs in accordance with the specific rules set out in Article [36]. | EDF wishes to insist on the importance of further developing provisions related to “Market Interactions” (Chapter 4) in order to ensure TSO’s can manage their responsibilities while preserving, as long as possible, the efficient functioning of markets throughout the EU. Current ENTSO-E proposals on this issues (Chapter 4 of current draft NC ER) need to be complemented before being submitted to public consultation. Consequently, EDF welcomes ENTSO-E’s intention (publically announced during ENTSO-E’s workshop in 12/11) to launch an additional public consultation to cover this specific issue and will provide its detailed contribution to it. |  |  | technical |  |  |  | Non-confidential
0005-6fa1-5fe3-2396-4be2 | V1.0 for Public consultation version | 4 | 32 | 2 | - | 2014-12-08 17:07:35 | Jasmina PIERRE | EdF | final | 2. For each TSO in Emergency State which does not suspend market activities in accordance with this Chapter, NC Electricity Balancing, CACM, NC FCA and chapter 7 of NC OPS shall be applicable. | 2. For each TSO in a mid-scale Emergency State which does not suspend market activities in accordance with Article [32 bis] of this Chapter, NC Electricity Balancing, CACM, NC FCA and chapter 7 of NC OPS shall be applicable. | EDF wishes to insist on the importance of further developing provisions related to “Market Interactions” (Chapter 4) in order to ensure TSO’s can manage their responsibilities while preserving, as long as possible, the efficient functioning of markets throughout the EU. Current ENTSO-E proposals on this issues (Chapter 4 of current draft NC ER) need to be complemented before being submitted to public consultation. Consequently, EDF welcomes ENTSO-E’s intention (publically announced during ENTSO-E’s workshop in 12/11) to launch an additional public consultation to cover this specific issue and will provide its detailed contribution to it. |  |  | technical |  |  |  | Non-confidential
0005-e4a9-610b-6d98-f2e1 | V1.0 for Public consultation version | 4 | 32 | - | - | 2014-12-04 09:25:30 | Steve Wilkin | ELEXON Limited | final |  | See comment (on the whole of Chapter 4 not just Article 32). | Comment on the whole of Chapter 4 (starting from Article 32 but including Artilcles 33, 34, 35, 36 as well): We realise that ENTSO-E has not finalised the drafting of Chapter 4 on market interactions and that it is still undergoing change and that the current wording is a holding statement. Therefore we wholeheartedly support, what we understand to be, ENTSO-E's plan to consult on the final version of the ENTSO-E draft of Chapter 4. As this is such an important Chapter, it is essential that there is a public consultation on the final version of the proposed ENTSO-E text before it is sent to ACER. |  |  | legal |  |  |  | Non-confidential
0005-2145-0223-258a-27c2 | V1.0 for Public consultation version | 4 | 32 | - | - | 2014-12-08 17:07:34 | Jasmina PIERRE | EdF | final | (new) | Atricle 32 bis : Market Activities Suspension Triggers 1. During an Emergency State or Blackout State, the two following criteria shall both be met to trigger the suspension of market activities procedure as defined under Article [33] and Article [34]: a. The TSO(s) cannot any longer use contracts to solve grid issues (i.e. redispatching, balancing contracts, FCR, FRR, RR, [..…]) because of lack of time and/or lack of resources both on generation side or on and demand side; and b. Unvoluntary Load shedding is activated manually or automatically above the threshold defined in paragraph 2 of this Article. The market(s) remain suspended until the restoration of the market(s) as described in Article [35]. 2. The TSO(s) and NEMO(s) of the concerned Capacity Calculation Region shall develop in good faith the threshold level for the suspension of market activities for a defined area based on the non-voluntary load shedding ration of customers defined in Article [33.1]. The TSO(s) and NEMO(s) shall involve stakeholders in the development of the definition of this threshold level and defined area and shall consult stakeholders prior to submitting the proposed threshold level and defined area to the relevant NRA(s) for approval within [xxx] months of [xxxx]. If approval is required from more than one NRA and those NRAs cannot agree then ACER shall within [xxxx] determine the matter. 3. When a mid-scale Emergency State as defined under Article [32 ter.2] lasts for more than [xxx] hours, it shall automatically be deemed a large-scale Emergency State or Blackout State as defined under Article [32 ter.1]. | EDF wishes to insist on the importance of further developing provisions related to “Market Interactions” (Chapter 4) in order to ensure TSO’s can manage their responsibilities while preserving, as long as possible, the efficient functioning of markets throughout the EU. Current ENTSO-E proposals on this issues (Chapter 4 of current draft NC ER) need to be complemented before being submitted to public consultation. Consequently, EDF welcomes ENTSO-E’s intention (publically announced during ENTSO-E’s workshop in 12/11) to launch an additional public consultation to cover this specific issue and will provide its detailed contribution to it. |  |  | technical |  |  |  | Non-confidential
0005-e4bd-2915-25ee-f3dc | V1.0 for Public consultation version | 4 | 32 | - | - | 2014-12-08 17:07:33 | Jasmina PIERRE | EdF | final | (new) | Atricle 32ter Types of Emergency State or Blackout State 1. When criteria 1.a and 1.b under Article [32 bis] are both met, a large-scale Emergency State or Blackout State shall be declared by the TSO. Each TSO shall notify the market and NRAs that they will initiate the suspension of market activities procedure as defined by Article [33] and by Article [34]. When market activities are suspended, the settlement rules and principles defined in Chapter 5 of [NC Electricity Balancing] shall not be applicable and the TSO shall act as a central dispatcher (i.e. take over dispatch of plants and decide on load shedding) as defined under Article [32]. 2. When criteria 1.a. and 1.b under Article [32 bis] are not met but a non-voluntary load shedding ratio of customers does occur, a mid-scale Emergency State shall be declared by the TSO. The threshold level to reach such a state shall be based on a load shedding ratio and shall be defined for each country by the Relevant TSO(s) and approved by the NRA within [xxx] months of [xxxx]. In this case, market activities are not suspended: NC Electricity Balancing, CACM, NC FCA and chapter 7 of NC OPS shall be applicable as defined under Article [32]. | EDF wishes to insist on the importance of further developing provisions related to “Market Interactions” (Chapter 4) in order to ensure TSO’s can manage their responsibilities while preserving, as long as possible, the efficient functioning of markets throughout the EU. Current ENTSO-E proposals on this issues (Chapter 4 of current draft NC ER) need to be complemented before being submitted to public consultation. Consequently, EDF welcomes ENTSO-E’s intention (publically announced during ENTSO-E’s workshop in 12/11) to launch an additional public consultation to cover this specific issue and will provide its detailed contribution to it. |  |  | technical |  |  |  | Non-confidential
0005-4891-008e-0f0b-475c | V1.0 for Public consultation version | 4 | 32 | - | - | 2014-12-08 17:16:51 | Paul Doyle | ESB Generation & Wholesale Markets | final | [NOTE FOR THE PUBLIC CONSULTATION: this article aims at stating the requirements from other NC that apply in Emergency and/or Restoration States. It has to be further elaborated.] For example: | Work out this article before Public Consultation! | The article is not available for the Public Consultation. THIS IS NOT ACCEPTABLE for the public consultation of a European regulation made by one stake holder (ENTSO-E)! |  |  | legal |  |  |  | Non-confidential
0005-9675-8540-0ea7-c3a7 | V1.0 for Public consultation version | 4 | 32 | - | - | 2014-12-08 17:16:52 | Paul Doyle | ESB Generation & Wholesale Markets | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal |  |  | legal |  |  |  | Non-confidential
0005-e4a9-1142-929c-3426 | V1.0 for Public consultation version | 4 | 32 | - | - | 2014-12-05 11:33:50 | Agnieszka Panek |  | final | [NOTE FOR THE PUBLIC CONSULTATION: this article aims at stating the requirements from other NC that apply in Emergency and/or Restoration States. It has to be further elaborated.] | ?? | The article is not available for the Public Consultation. THIS IS NOT ACCEPTABLE . It should be the object of separate public consultation |  |  | legal |  |  |  | Non-confidential
0005-4892-1800-e961-4b2f | V1.0 for Public consultation version | 4 | 32 | - | - | 2014-11-28 15:52:36 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | [NOTE FOR THE PUBLIC CONSULTATION: this article aims at stating the requirements from other NC that apply in Emergency and/or Restoration States. It has to be further elaborated.] For example: | Work out this article before Public Consultation! | The article is not available for the Public Consultation. THIS IS NOT ACCEPTABLE for the public consultation of a European regulation made by one stake holder (ENTSO-E)! |  |  | legal |  |  |  | Non-confidential
0005-6fb6-b45e-e76d-fd4a | V1.0 for Public consultation version | 4 | 32 | - | - | 2014-11-28 15:52:37 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10. |  |  | legal |  |  |  | Non-confidential
0005-bd85-4e9e-d2f5-9023 | V1.0 for Public consultation version | 4 | 32 | - | - | 2014-12-08 23:56:25 | Gunnar Kaestle | Clausthal University of Technology | final | this article aims at stating the requirements from other NC | delete or rephrase article 32 | As commonly understood, each NC is valid by it own after it has passed the comitology procedure. So it is redundant information to repeat which requirements of other NC are still valid. The interesting information is which NCs are temporarily suspended during Emergency or Restoration, but this is written in the following articles 33ff. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2080 | V1.0 for Public consultation version | 4 | 32 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | [NOTE FOR THE PUBLIC CONSULTATION: this article aims at stating the requirements from other NC that apply in Emergency and/or Restoration States. It has to be further elaborated.] For example: | Work out this article before Public Consultation! | The article is not available for the Public Consultation. All relevant information should be included in the document. This is a formal public consultation on the code and a consultation can be organised in an appropriate manner only when all information is available for stakeholders.
0005-e495-5e7a-d54d-2081 | V1.0 for Public consultation version | 4 | 32 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10.
0005-e495-5e7a-d54d-1863 | V1.0 for Public consultation version | 4 | 32 |  |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Xyz | Xyz | Following the statement from ENTSOe at the 12th November Workshop in Brussels that Chapter 4 will be subject to a later, specific, consultation from mid December to mid January (2015) we refrain from making any comment on this particular Article. However, we reserve our right to submit comments on this particular Article, after December 8th, if that promised consultation by ENTSOe does not take place.
0005-96c5-c572-a169-a9f0 | V1.0 for Public consultation version | 4 | 33 | 1 | - | 2014-12-04 14:27:20 | Dekinderen Eric | Genrator company | final | See Eurelectric proposal | See Eurelectric proposal | See Eurelectric proposal |  |  | legal |  |  |  | Non-confidential
0005-2181-5025-23fa-6de0 | V1.0 for Public consultation version | 4 | 33 | 1 | - | 2014-12-08 17:07:35 | Jasmina PIERRE | EdF | final | 1. During Emergency and Blackout States, if deemed necessary, each TSO shall be entitled to totally or partially suspend any of the following market activities or any combination thereof: a) full or partial operation of the single day-ahead coupling and its results, as described in Articles 45 and 46 [CACM]; b) operation of the single intraday coupling and its results, as described in Articles 56 and 57 [CACM]; c) any complementary regional auctions, as described in Article 60 [CACM]; d) operation of the Forward Capacity Allocation, as described in Articles 43, 44 and 45 [NC FCA]; e) submission by Balancing Service Provider of Balancing Capacity and Balancing Energy bids , as described in Article 23 [NC EB]; f) provision by Balance Responsible Party of a balanced Position in day ahead and the provision of change of its Position, as described in Article 24(4) to 24(7) [NC EB]; and/or g) provision of schedules, as described in Article 53(1) and 53(2) [NC OPS]. | 1. If the TSO observes indications of potential upcoming emergency situation already in the day-ahead and in the intra-day markets, the markets activities should continue as long as possible (i.e. markets should have the possibility to amend the situation as close as possible to real time (i.e. up to H-1)). The TSO shall notify, without delay, the other TSO(s) of the concerned Capacity Region, NEMO(s) and NRA(s) of any anticipated emergency from its perspective. During a large-scale Emergency State or Blackout States as defined under Article [32 ter] , each TSO shall be required to suspend any of the following market activities or any combination thereof: a) full or partial operation of the single day-ahead coupling and its results, as described in Articles 45 and 46 [CACM]; b) operation of the single intraday coupling and its results, as described in Articles 56 and 57 [CACM]; c) any complementary regional auctions, as described in Article 60 [CACM]; d) operation of the Forward Capacity Allocation, as described in Articles 43, 44 and 45 [NC FCA]; e) submission by Balancing Service Provider of Balancing Capacity and Balancing Energy bids , as described in Article 23 [NC EB]; f) provision by Balance Responsible Party of a balanced Position in day ahead and the provision of change of its Position, as described in Article 25(4) [NC EB], and/or ; g) provision of schedules, as described in Article 53(1) and 53(2) [NC OPS]. | EDF wishes to insist on the importance of further developing provisions related to “Market Interactions” (Chapter 4) in order to ensure TSO’s can manage their responsibilities while preserving, as long as possible, the efficient functioning of markets throughout the EU. Current ENTSO-E proposals on this issues (Chapter 4 of current draft NC ER) need to be complemented before being submitted to public consultation. Consequently, EDF welcomes ENTSO-E’s intention (publically announced during ENTSO-E’s workshop in 12/11) to launch an additional public consultation to cover this specific issue and will provide its detailed contribution to it. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2335 | V1.0 for Public consultation version | 4 | 33 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | During Emergency and Blackout States, if deemed necessary, each TSO shall be entitled to totally or partially suspend any of the following market activities or any combination thereof: | no text proposal. | Please clarify which party takes the 'deemed necessary' decision. Is it the TSO? |  |  | Legal
0005-9675-d513-2396-d697 | V1.0 for Public consultation version | 4 | 33 | 2 | - | 2014-12-08 17:07:33 | Jasmina PIERRE | EdF | final | 2. When suspending any of the above mentioned market activities or any combination thereof, each TSO shall consult the other TSOs and NEMOs of the concerned Capacity Calculation Region. Each NEMO shall inform its Market Participants. | 2. When suspending any of the above mentioned market activities or any combination thereof, each TSO shall consult the other TSO(s) and NEMO(s) of the concerned Capacity Calculation Region. Each TSO shall notify the other TSO(s), NEMO(s) and NRA(s) of the concerned Capacity Calculation Region without delay where the TSO has suspended the market activities in accordance with this Chapter. Each NEMO shall without delay notify its Market Participants of any suspension of market activities it is notified of by a TSO. | EDF wishes to insist on the importance of further developing provisions related to “Market Interactions” (Chapter 4) in order to ensure TSO’s can manage their responsibilities while preserving, as long as possible, the efficient functioning of markets throughout the EU. Current ENTSO-E proposals on this issues (Chapter 4 of current draft NC ER) need to be complemented before being submitted to public consultation. Consequently, EDF welcomes ENTSO-E’s intention (publically announced during ENTSO-E’s workshop in 12/11) to launch an additional public consultation to cover this specific issue and will provide its detailed contribution to it. |  |  | technical |  |  |  | Non-confidential
0005-2181-d61d-6e60-7a68 | V1.0 for Public consultation version | 4 | 33 | 2 | - | 2014-12-04 09:26:29 | Steve Wilkin | ELEXON Limited | final | When suspending any of the above mentioned market activities or any combination thereof, each TSO shall consult the other TSOs and NEMOs of the concerned Capacity Calculation Region. Each NEMO shall inform its Market Participants. | When suspending any of the above mentioned market activities or any combination thereof, each TSO shall consult the other TSOs and NEMOs of the concerned Capacity Calculation Region. Where relevant, cach TSO shall also notify any third party to whom any of its TSO functions has been assigned or delegated pursuant to the Network Code on Electricity Balancing. Each NEMO shall inform its Market Participants and any third party shall inform its Balance Responsible Parties and/or other relevant participants. | This does not take account of the role of non-TSO market operators, settlement administrators or other third parties who might have been tasked under the Balancing Network Code with some TSO activities including market administration. NEMOs are unlikely to be the only market operators who need to notify their participants. Market Participants as formally defined may also be too narrow a definition to cover all parties, for example those who are Balancing Service Providers or Balance Responsible Parties? |  |  | legal |  |  |  | Non-confidential
0005-2195-857c-0c4f-6be1 | V1.0 for Public consultation version | 4 | 33 | - | - | 2014-12-08 17:16:53 | Paul Doyle | ESB Generation & Wholesale Markets | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal |  |  | legal |  |  |  | Non-confidential
0005-9676-7d72-e8fd-6964 | V1.0 for Public consultation version | 4 | 33 | - | - | 2014-11-28 15:52:38 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2082 | V1.0 for Public consultation version | 4 | 33 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10.
0005-e495-5e7a-d54d-1864 | V1.0 for Public consultation version | 4 | 33 |  |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Xyz | Xyz | Following the statement from ENTSOe at the 12th November Workshop in Brussels that Chapter 4 will be subject to a later, specific, consultation from mid December to mid January (2015) we refrain from making any comment on this particular Article. However, we reserve our right to submit comments on this particular Article, after December 8th, if that promised consultation by ENTSOe does not take place.
0005-216d-0241-23fa-9b4e | V1.0 for Public consultation version | 4 | 34 | 1 | - | 2014-12-08 17:07:33 | Jasmina PIERRE | EdF | final | 1. During Emergency and Blackout States, if deemed necessary, each TSO shall be entitled to totally or partially suspend at least one of the following TSO processes or any combination thereof: a) determination of Cross Zonal Capacities; b) real time execution of Availability Plans, as described in Article 44 [NC OPS]; c) agreed upon updates to the Year Ahead Availability Plans when these are related to the time period of the Emergency States, as described in Article 41 [NC OPS]; d) any of the processes and activities as described in Articles 31 and 32 [NC LFCR], upon request of the Frequency Leader when appointed. | 1. During a large-scale Emergency State or Blackout State as defined under Article [32 ter], each TSO shall be required to totally or proportionally to the magnitude of the incident suspend at least one of the following TSO processes or any combination thereof: a) determination of Cross Zonal Capacities; b) real time execution of Availability Plans, as described in Article 44 [NC OPS]; c) agreed upon updates to the Year Ahead Availability Plans when these are related to the time period of the Emergency States, as described in Article 41 [NC OPS]; d) any of the processes and activities as described in Articles 31 and 32 [NC LFCR], upon request of the Frequency Leader when appointed. | EDF wishes to insist on the importance of further developing provisions related to “Market Interactions” (Chapter 4) in order to ensure TSO’s can manage their responsibilities while preserving, as long as possible, the efficient functioning of markets throughout the EU. Current ENTSO-E proposals on this issues (Chapter 4 of current draft NC ER) need to be complemented before being submitted to public consultation. Consequently, EDF welcomes ENTSO-E’s intention (publically announced during ENTSO-E’s workshop in 12/11) to launch an additional public consultation to cover this specific issue and will provide its detailed contribution to it. |  |  | technical |  |  |  | Non-confidential
0005-4891-d512-a295-376e | V1.0 for Public consultation version | 4 | 34 | 1 | - | 2014-12-04 14:27:37 | Dekinderen Eric | Genrator company | final | See Eurelectric proposal | See Eurelectric proposal | See Eurelectric proposal |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2336 | V1.0 for Public consultation version | 4 | 34 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | During Emergency and Blackout States, if deemed necessary, each TSO shall be entitled to totally or partially suspend at least one of the following TSO processes or any combination thereof: | no text proposal. | Please clarify which party takes the 'deemed necessary' decision. Is it the TSO? |  |  | Legal
0005-2195-5025-25ee-e518 | V1.0 for Public consultation version | 4 | 34 | - | - | 2014-12-08 17:07:33 | Jasmina PIERRE | EdF | final | (new) | 2. When suspending any of the above mentioned market activities or any combination thereof, each TSO shall consult the other TSO(s) and NEMO(s) of the concerned Capacity Calculation Region. Each TSO shall notify the other TSO(s), NEMO(s) and NRA(s) of the concerned Capacity Calculation Region without delay where the TSO has suspended the market activities in accordance with this Chapter. Each NEMO shall without delay notify its Market Participants of any suspension of market activities it is notified of by a TSO. | EDF wishes to insist on the importance of further developing provisions related to “Market Interactions” (Chapter 4) in order to ensure TSO’s can manage their responsibilities while preserving, as long as possible, the efficient functioning of markets throughout the EU. Current ENTSO-E proposals on this issues (Chapter 4 of current draft NC ER) need to be complemented before being submitted to public consultation. Consequently, EDF welcomes ENTSO-E’s intention (publically announced during ENTSO-E’s workshop in 12/11) to launch an additional public consultation to cover this specific issue and will provide its detailed contribution to it. |  |  | technical |  |  |  | Non-confidential
0005-9689-d39c-0cb3-a911 | V1.0 for Public consultation version | 4 | 34 | - | - | 2014-12-08 17:16:55 | Paul Doyle | ESB Generation & Wholesale Markets | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal |  |  | legal |  |  |  | Non-confidential
0005-e496-6602-e8fd-659f | V1.0 for Public consultation version | 4 | 34 | - | - | 2014-11-28 15:52:39 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2083 | V1.0 for Public consultation version | 4 | 34 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10.
0005-e495-5e7a-d54d-1865 | V1.0 for Public consultation version | 4 | 34 |  |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Xyz | Xyz | Following the statement from ENTSOe at the 12th November Workshop in Brussels that Chapter 4 will be subject to a later, specific, consultation from mid December to mid January (2015) we refrain from making any comment on this particular Article. However, we reserve our right to submit comments on this particular Article, after December 8th, if that promised consultation by ENTSOe does not take place.
0005-6fb5-787b-6ec4-c2e5 | V1.0 for Public consultation version | 4 | 35 | 1 | - | 2014-12-04 09:27:46 | Steve Wilkin | ELEXON Limited | final |  | See comment. | Market Party is not a defined term in this Network Code or in the ENTSO-E Glossary of definitions. But perhaps it should be a new term. Market Participant may be too narrow and not cover all parties to whom this Article should apply? |  |  | legal |  |  |  | Non-confidential
0005-969d-39fb-7054-8366 | V1.0 for Public consultation version | 4 | 35 | 1 | - | 2014-12-04 09:28:30 | Steve Wilkin | ELEXON Limited | final | Each Market Party shall follow the instructions it receives from a TSO for the restoration of market activities, respecting if any the conditions and timeframe set by the TSOs in its instruction. Each NEMO shall inform its Market Participants. | Each Market Party shall follow the instructions it receives from a TSO, or from any third party to whom any of its TSO functions has been assigned or delegated pursuant to the Network Code on Electricity Balancing, for the restoration of market activities, respecting if any the conditions and timeframe set by the TSOs or third party in its instruction. Each NEMO shall inform its Market Participants and any third party shall inform its Balance Responsible Parties and/or other relevant participants. | This does not take account of the role of non-TSO market operators, settlement administrators or other third parties who might have been tasked under the Balancing Network Code with some TSO activities including market administration. NEMOs are unlikely to be the only market operators who need to notify their participants. Market Participants as formally defined may also be too narrow a definition to cover all parties, for example those who are Balancing Service Providers or Balance Responsible Parties? |  |  | legal |  |  |  | Non-confidential
0005-2159-2933-25ee-feef | V1.0 for Public consultation version | 4 | 35 | 1 | - | 2014-12-08 17:07:34 | Jasmina PIERRE | EdF | final | 1. Each Market Party shall follow the instructions it receives from a TSO for the restoration of market activities, respecting if any the conditions and timeframe set by the TSOs in its instruction. Each NEMO shall inform its Market Participants. | 1. The market is restored when the TSO(s) declare that the market can take over again (i.e. [xxx], e.g. 90% of the forecasted consumption within the TSO’s control area is realised) and only after: a. Market Participants have been duly notified at least [xxxx] time in advance in order to permit them to resume their responsibility; b. All required communication tools between involved market parties and power exchanges are properly functioning; c. (Commercial) Imports and exports between markets are properly functioning, i.e. be nominated again in both importing and exporting market. The TSO(s) will develop, after consulting the NEMO(s) and Market Participants, the details of what tasks and actions are expected from all parties; including the TSO(s), NEMOs and Market Participants, during the process of restoration of market activities. These stages will include:- a. Notification of the suspension of market activities by the TSO(s) according to Article [33] paragraph [3]; b. Notification of the time and date of the suspension of market activities by the TSO(s); c. Update(s) on the re-energisation of the network by the TSO(s); d. Update(s) on the return of the market systems by the NEMO(s); e. Notification of the return of the market systems by the NEMO(s); f. Notification of the restoration of the network back to Normal State by the TSO(s); g. Consultation by the TSO(s) and the NEMO(s) with Market Participants or its appointed panel on the proposed time and date for the return to normal market activities; h. Approval by the NRA(s) of the proposed time and date for the return to normal market activities where practicable where the TSO(s) and Market Participants cannot agree; i. Notification by the TSO(s) of the time and date when market activities will (re)commence; and j. Confirmation by the TSO(s) and NEMO(s) that market activities have (re)commenced. The TSO(s) will provide updates on the process of restoration of market activities, without delay, to the NRAs and the NEMO(s) (who shall without delay inform all Market Participants of these updates). | EDF wishes to insist on the importance of further developing provisions related to “Market Interactions” (Chapter 4) in order to ensure TSO’s can manage their responsibilities while preserving, as long as possible, the efficient functioning of markets throughout the EU. Current ENTSO-E proposals on this issues (Chapter 4 of current draft NC ER) need to be complemented before being submitted to public consultation. Consequently, EDF welcomes ENTSO-E’s intention (publically announced during ENTSO-E’s workshop in 12/11) to launch an additional public consultation to cover this specific issue and will provide its detailed contribution to it. |  |  | technical |  |  |  | Non-confidential
0005-9689-86d4-a231-f3ea | V1.0 for Public consultation version | 4 | 35 | 1 | - | 2014-12-04 14:27:52 | Dekinderen Eric | Genrator company | final | See Eurelectric proposal | See Eurelectric proposal | See Eurelectric proposal |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2084 | V1.0 for Public consultation version | 4 | 35 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | 2. As soon as the TSO is back to Normal State it shall restart the activities and processes it suspended according to Article 33 and Article 34 and inform the concerned Scheduling Agents and NEMOs. |  | What happens if the state goes from Emergency to Alert prior to Normal?
0005-e4d1-5043-26b6-81fa | V1.0 for Public consultation version | 4 | 35 | 4 | - | 2014-12-08 17:07:34 | Jasmina PIERRE | EdF | final | 4. When only part of a Capacity Calculation Region is back to Normal State, the TSOs of this Capacity Calculation Region shall be entitled to launch a partial market coupling, after consultation of the Coordinated Capacity Calculator and the NEMOs. | 4. When only part of a Capacity Calculation Region is back to Normal State, the TSO(s) of this Capacity Calculation Region shall be entitled to launch a partial market coupling, after consultation with the Coordinated Capacity Calculator, the NEMO(s) and Market Participants and the approval from the relevant NRA(s) where practicable and where the TSO(s) and Market Participants cannot agree. Cross-border exchanges with markets still under (large) emergency phase or blackout phase should be managed by the TSO(s) (i.e. TSO to be in the middle for exporting (or importing) to the markets where the market is still suspended). | EDF wishes to insist on the importance of further developing provisions related to “Market Interactions” (Chapter 4) in order to ensure TSO’s can manage their responsibilities while preserving, as long as possible, the efficient functioning of markets throughout the EU. Current ENTSO-E proposals on this issues (Chapter 4 of current draft NC ER) need to be complemented before being submitted to public consultation. Consequently, EDF welcomes ENTSO-E’s intention (publically announced during ENTSO-E’s workshop in 12/11) to launch an additional public consultation to cover this specific issue and will provide its detailed contribution to it. |  |  | technical |  |  |  | Non-confidential
0005-487d-5e30-0ddf-a262 | V1.0 for Public consultation version | 4 | 35 | - | - | 2014-12-08 17:16:57 | Paul Doyle | ESB Generation & Wholesale Markets | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal |  |  | legal |  |  |  | Non-confidential
0005-2196-3f10-e709-6106 | V1.0 for Public consultation version | 4 | 35 | - | - | 2014-11-28 15:52:40 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2085 | V1.0 for Public consultation version | 4 | 35 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10.
0005-e495-5e7a-d54d-1866 | V1.0 for Public consultation version | 4 | 35 |  |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Xyz | Xyz | Following the statement from ENTSOe at the 12th November Workshop in Brussels that Chapter 4 will be subject to a later, specific, consultation from mid December to mid January (2015) we refrain from making any comment on this particular Article. However, we reserve our right to submit comments on this particular Article, after December 8th, if that promised consultation by ENTSOe does not take place.
0005-bd99-5025-2652-c240 | V1.0 for Public consultation version | 4 | 36 | 1 | - | 2014-12-08 17:07:34 | Jasmina PIERRE | EdF | final | 1. When the system is in Emergency State, the settlement rules and principles defined in Chapter 5 of [NC Electricity Balancing] shall apply. 2. When the system is in Blackout and Restoration States, the settlement shall be ruled by national legislation. | 1. As defined in Article [32], settlement rules and principles shall differ depending on the type of Emergency State or Blackout State experienced as defined under Article [33]. 2. In case of a mid-scale Emergency State as defined under Article [2], additional efforts required from the BRP(s) on the balancing market shall be remunerated according to the settlement rules and principles defined in Chapter 5 of [NC Electricity Balancing] as defined in Article [32]. 3. In case of a large-scale Emergency State or Blackout State as defined under Article [33]: a. The settlement rules and principles defined in Chapter 5 of [NC Electricity Balancing] shall not be applicable as defined under Article [32] and shall be defined in a methodology to be proposed by the TSO(s) and approved by the NRA(s) [xxx] months after the enforcement of this network code. The TSO(s) shall involve all relevant stakeholders in the development of the methodology. b. The methodology shall stipulate that: i. The TSO(s) shall compensate generators for all costs they have reasonably incurred based on a pre-defined price formula including generators’ start costs, fuel cost, CO2 costs and operating costs; ii. Those costs to be recovered shall be shared between the involved stakeholders (excluding the generators being compensated) , following principles decided on a case by case basis by the NRA(s); iii. Double payments or earnings shall be avoided to the extent possible. | EDF wishes to insist on the importance of further developing provisions related to “Market Interactions” (Chapter 4) in order to ensure TSO’s can manage their responsibilities while preserving, as long as possible, the efficient functioning of markets throughout the EU. Current ENTSO-E proposals on this issues (Chapter 4 of current draft NC ER) need to be complemented before being submitted to public consultation. Consequently, EDF welcomes ENTSO-E’s intention (publically announced during ENTSO-E’s workshop in 12/11) to launch an additional public consultation to cover this specific issue and will provide its detailed contribution to it. |  |  | technical |  |  |  | Non-confidential
0005-bdd5-c572-a231-4f7c | V1.0 for Public consultation version | 4 | 36 | 1 | - | 2014-12-04 13:49:53 | Dekinderen Eric | Genrator company | final | See Eurelectric proposal | See Eurelectric proposal | See Eurelectric proposal |  |  | technical |  |  |  | Non-confidential
0005-6fa1-855e-0beb-c645 | V1.0 for Public consultation version | 4 | 36 | - | - | 2014-12-08 17:16:59 | Paul Doyle | ESB Generation & Wholesale Markets | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal |  |  | legal |  |  |  | Non-confidential
0005-2182-cb92-e899-de92 | V1.0 for Public consultation version | 4 | 36 | - | - | 2014-11-28 15:52:41 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2086 | V1.0 for Public consultation version | 4 | 36 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | See Eurelectric proposal | See Eurelectric proposal | We support the Eurelectric Proposal as discussed in the bilateral meetings on 20/09 and 25/10.
0005-e495-5e7a-d54d-1867 | V1.0 for Public consultation version | 4 | 36 |  |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Xyz | Xyz | Following the statement from ENTSOe at the 12th November Workshop in Brussels that Chapter 4 will be subject to a later, specific, consultation from mid December to mid January (2015) we refrain from making any comment on this particular Article. However, we reserve our right to submit comments on this particular Article, after December 8th, if that promised consultation by ENTSOe does not take place.
0005-e495-5e7a-d54d-2211 | V1.0 for Public consultation version | 4 | 32-36 |  |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Chapter 4 on Market Interactions | See the justification. | We understand (following the statement made at the ENTSO-E Stakeholder Workshop of 12 November and the information published on the ENTSO-E website) that Chapter 4 will be subject to separate & specific consultation from mid-December until mid-January. Therefore, we refrain from making any particular comment on this particular chapter for the time being. However, we reserve our right to submit comments on this Chapter in case the announced consultation does not take place. We expect that Chapter 4 will cover issues such as: triggers for suspension, the NRA approval of parameters for suspension, the process and mechanisms during suspension and the process for reinstatement of market rules. |  |  | Legal | Fundamental
0005-4891-c590-a0a1-4c7c | V1.0 for Public consultation version | 5 | 37 | 1 | - | 2014-12-04 13:54:09 | Dekinderen Eric | Genrator company | final | from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions | To erase "Type A" | Asking this information from all type A or type B SGU is an impossible task |  |  | technical |  |  |  | Non-confidential
0005-2181-c5d8-1336-94b6 | V1.0 for Public consultation version | 5 | 37 | 1 | - | 2014-12-03 11:19:41 | AXPO Group |  | final | from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: … | see Comment | As already stated for the Restoration Plan, new Type A Power Generating Modules (i.e. renewable energy sources) shall be excluded in the entire code. They are unsuitable for emergency and restoration situations. Their production is unpredictable. They cannot be utilized in a controlled manner. Prior to the utilization of new Type A Power Generating Modules in emergency and restoration situations it is necessary to collect experiences on a local level. If the penetration of renewables in a grid area is significant, then their step-wise reconnection to the grid has to be addressed. This has to be accomplished within a concept called "return of production", like the concept of "return of load" on the load side. Further, the immense number of decentralized, small Type A Power Generating Modules excludes a detailed gathering of information. To collect detailed data from hundredthousands of Type A modules in a short period makes no sense. Even the time interval for the collection of the data is not specified in the article. It is unthinkable that there will be information exchange during an emergency or restoration phase between a TSO and owners of uncounted new Type A Power Generating Modules. |  |  | technical |  |  |  | Non-confidential
0005-e4d1-4ecb-c867-f838 | V1.0 for Public consultation version | 5 | 37 | 1 | - | 2014-12-08 19:51:15 | Roland Tual | SEDC | final | b) from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: i. current status of the installation; ii. operational limits; iii. Full Activation Time and time to increase generation; and iv. time critical processes. | [8 empty] | confidential
0005-4891-d39c-0beb-4cfc | V1.0 for Public consultation version | 5 | 37 | 1 | - | 2014-12-08 17:17:01 | Paul Doyle | ESB Generation & Wholesale Markets | final | from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: | from Significant Grid Users, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: | Is it realistic to require, collect and assess the immense amount of informations from all type A Power Generating Modules? |  |  | technical |  |  |  | Non-confidential
0005-e4a9-373e-0e43-b5f7 | V1.0 for Public consultation version | 5 | 37 | 1 | - | 2014-12-08 17:17:02 | Paul Doyle | ESB Generation & Wholesale Markets | final | from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: i. current status of the installation; ii. operational limits; iii. Full Activation Time and time to increase generation; and iv. time critical processes. |  | How will Type A do this? ENTSO-E should elaborate what it actually expects several million Type A generators to do under these circumstances. Via aggregator? Why here? The characteristics (operational limits / activation time and time critical processes) have to be known upfront |  |  | technical |  |  |  | Non-confidential
0005-e4e6-db32-e709-bf9a | V1.0 for Public consultation version | 5 | 37 | 1 | - | 2014-11-28 15:52:42 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: | from Significant Grid Users, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: | Is it realistic to require, collect and assess the immense amount of informations from all type A Power Generating Modules? |  |  | technical |  |  |  | Non-confidential
0005-487e-8d12-e961-d176 | V1.0 for Public consultation version | 5 | 37 | 1 | - | 2014-11-28 15:52:43 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: i. current status of the installation; ii. operational limits; iii. Full Activation Time and time to increase generation; and iv. time critical processes. |  | How will Type A do this? ENTSO-E should elaborate what it actually expects several million Type A generators to do under these circumstances. Via aggregator? Why here? The characteristics (operational limits / activation time and time critical processes) have to be known upfront |  |  | technical |  |  |  | Non-confidential
0005-6fb5-28be-3acc-2a7f | V1.0 for Public consultation version | 5 | 37 | 1 | a | 2014-12-05 11:02:48 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | In addition to the provisions of Articles 16 to 29 [NC OS], each TSO shall request the following information: a) from DSOs, information about at least: i. existing part of their Network in Island Operation; ii. ability to synchronize parts of their Network in Island Operation; and iii. capability to start Island Operation. | In addition to the provisions of Articles 16 to 29 [NC OS], each TSO shall request the following information: a) from DSOs, information about: i. existing part of their Network in Island Operation; ii. ability to synchronize parts of their Network in Island Operation; and iii. capability to start Island Operation. | There should be a limited number of points to be obligatory. If "At least" is used, the information must be limited to relevant topics | 1 | 1 | legal |  |  |  | Non-confidential
0005-e4a9-0240-a231-372d | V1.0 for Public consultation version | 5 | 37 | 1 | a | 2014-12-04 13:52:21 | Dekinderen Eric | Genrator company | final | iii. capability to start Island Operation. | to erase | Islanding is not common practice at DSOs |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2337 | V1.0 for Public consultation version | 5 | 37 | 1 | a | 2014-12-08 22:31 | Michael Wilch | RWE | final | i. existing part of their Network in Island Operation; ii. ability to synchronize parts of their Network in Island Operation; and iii. capability to start Island Operation. | i. existing part of their Network in controlled Island Operation; ii. ability to synchronize parts of their Network in controlled Island Operation; and iii. capability to start controlled Island Operation. | It seems better to use 'controlled' island operation. |  |  | Technical
0005-e4e5-d530-a1cd-d852 | V1.0 for Public consultation version | 5 | 37 | 1 | b | 2014-12-04 13:55:25 | Dekinderen Eric | Genrator company | final | ii. operational limits; iii. Full Activation Time and time to increase generation; and iv. time critical processes | To insert in a dedicated paragraph | The characteristics (operational limits / activation time and time critical processes) have to be known upfront |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2087 | V1.0 for Public consultation version | 5 | 37 | 1 | b | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: | from Significant Grid Users, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: | Is it realistic to require, collect and assess the immense amount of informations from all type A Power Generating Modules?
0005-e495-5e7a-d54d-2088 | V1.0 for Public consultation version | 5 | 37 | 1 | b | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: i. current status of the installation; ii. operational limits; iii. Full Activation Time and time to increase generation; and iv. time critical processes. |  | How will Type A do this? ENTSO-E should elaborate what it actually expects several million Type A generators to do under these circumstances. Via aggregator? Why here? The characteristics (operational limits / activation time and time critical processes) have to be known upfront
0005-e495-5e7a-d54d-2213 | V1.0 for Public consultation version | 5 | 37 | 1 | b | 2014-12-08 21:33 | AG | RWE | final | from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: (…) | from Significant Grid Users, directly or through an aggregator or a DSO, that are identified in Restoration Plan as providing procured services to the relevant Network Operator, information about at least the following conditions: | Significant concerns about the practicality of obtaining this information from all Type A generators. Do the TSOs and DSOs have the capability to handle this data and do it in a timeframe that makes it of actual & operational use by the TSOs. Also the link between this information and REMIT obligations should be carefully considered. This is a market sensitive information that could put either the parties bound by REMIT and/ or the requesting TSOs in breach of those obligations. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2338 | V1.0 for Public consultation version | 5 | 37 | 1 | b | 2014-12-08 22:31 | Michael Wilch | RWE | final | from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: i. current status of the installation; ii. operational limits; iii. Full Activation Time and time to increase generation; and iv. time critical processes. | from Significant Grid Users connected to the Transmission Network directly and from Significant Grid Users connected to the Distribution Network and Type A Power Generating Modules, directly or through an aggregator or a the DSO, that are identified in Restoration Plan, information about at least the following conditions: i. current status of the installation; ii. operational limits; iii. Full Activation Time and time to increase generation; and iv. time critical processes. | DSOs are convinced that new type A PGMs should not be part of the NC ER, cf. explanation art. 8§4. Information of the SGUs connected to the Distribution Systems only by the DSO. Cf. DSO's point of view regarding information and communication channels (NC OS). Why are aggregators here mentioned? Aggregators are market parties and as market is phased out during restoration, they've got no stake. |  |  | Technical
0005-e495-5e7a-d54d-1875 | V1.0 for Public consultation version | 5 | 37 | 1 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan, information about at least the following conditions: | from Significant Grid Users and Type A Power Generating Modules, directly or through an aggregator or a DSO, that are identified in Restoration Plan AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR, information about at least the following conditions: | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan ” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-1877 | V1.0 for Public consultation version | 5 | 37 | 1 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | each TSO shall request the following information:….. i. current status of the installation; ii. operational limits; iii. Full Activation Time and time to increase generation; and iv. time critical processes. | xyz | For those parties bound by the REMIT (and soon the Transparency Regulation) providing this information could either place them and / or the TSO in breach of those obligations as the information the TSO is seeking here would be market sensitive. If the TSO acted upon this privileged information it could breach EU law.
0005-e495-5e7a-d54d-2212 | V1.0 for Public consultation version | 5 | 37 | 1 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | In addition to the provisions of Articles 16 to 29 [NC OS], each TSO shall request the following information: (…) | In addition to the provisions of Article 16 to 29 [NC OS], each TSO in Emergency, Blackout or Restoration State may request the following information (…) | As currently written, this allows the TSOs to seek this information during Normal or Alert State. If this information was required for those two states then it should have been set out in the other NCs (but not in the NC ER) |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2245 | V1.0 for Public consultation version | 5 | 37 | 1 |  | 2014-12-08 12:24 | Wolfram Heckmann | Fraunhofer IWES | final | “b) …, directly or through an aggregator or a DSO, …” |  | This needs specific requirements for dispatch centers and communication also of aggregators dealing with emergencies or black-out situations.
0005-e495-5e7a-d54d-1868 | V1.0 for Public consultation version | 5 | 37 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | In addition to the provisions of Articles 16 to 29 [NC OS], each TSO shall request the following information: | In addition to the provisions of Articles 16 to 29 [NC OS], EACH TSO IN EMERGENCY, BLACKOUT OR RESTROATION STATE shall MAY request the following information: | As written this allows the TSO to seek this information during Normal or Alert State. If this information was required for those two states then it should have been set out in the other relevant NCs and not NC E&R.
0005-e495-5e7a-d54d-1870 | V1.0 for Public consultation version | 5 | 37 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | i. current status of the installation; ii. operational limits; iii. Full Activation Time and time to increase generation; and iv. time critical processes. | Xyz | Has the practicality of obtaining this information from all Type A generators (a) been considered and (b) have the TSO and DSOs the capability to (1) handle this date and (2) do so in a timeframe that makes it of actual use, operationally, by the TSO?! If not then delete the obligation. Note Type A generators information is not obtained from aggregators as this is defined (in NC DCC) as being linked only to demand (not generation).
0005-e4d1-373e-0d7b-53c8 | V1.0 for Public consultation version | 5 | 37 | 2 | - | 2014-12-08 17:17:32 | Paul Doyle | ESB Generation & Wholesale Markets | final | to directly connected TSOs, information about at least: | to directly connected TSOs, DSOs, Significant Grid Users and NRA, information about at least: | Information is also necessary for other parties! |  |  | legal |  |  |  | Non-confidential
0005-9676-8d4e-e6a5-b6be | V1.0 for Public consultation version | 5 | 37 | 2 | - | 2014-11-28 15:53:01 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | to directly connected TSOs, information about at least: | to directly connected TSOs, DSOs, Significant Grid Users and NRA, information about at least: | Information is also necessary for other parties! |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2089 | V1.0 for Public consultation version | 5 | 37 | 2 | a | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | to directly connected TSOs, information about at least: | to directly connected TSOs, DSOs, Significant Grid Users and NRA, information about at least: | Information is also necessary for other parties.
0005-e495-5e7a-d54d-2214 | V1.0 for Public consultation version | 5 | 37 | 2 | a | 2014-12-08 21:33 | AG | RWE | final | to directly connected TSOs, information about at least: | to directly connected TSOs, DSOs, Significant Grid Users and NRA, information about at least: | Information is also necessary for other parties. |  |  | Technical | Fundamental
0005-2195-869c-3c5c-52e1 | V1.0 for Public consultation version | 5 | 37 | 3 | - | 2014-12-05 11:03:39 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | All TSO shall exchange between each other information in Emergency, Blackout or Restoration State and define additional information if necessary including at least… | All TSO shall exchange between each other and towards relevant DSOs information in Emergency, Blackout or Restoration State and define additional information if necessary including at least… | for emergency/restoration relevant DSOs need information | 1 | 2 | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2090 | V1.0 for Public consultation version | 5 | 37 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | All TSO shall exchange between each other information in Emergency, Blackout or Restoration State and define additional information if necessary including at least: a) Active and Reactive Power time limits at Interconnectors; and b) potential problems making assistance for Active Power necessary. | All TSO shall exchange between each other information in Emergency, Blackout or Restoration State and define additional information if necessary including at least: a) Active and Reactive Power time limits at Interconnectors; and b) potential problems making assistance for Active Power necessary. The language used for cross border communication will be English. TSOs shall ensure that their employees are skilled in English communication. | Make sure that communication between TSOs of different member states will be possible. English should be the language for cross border communication.
0005-e4d1-60ed-6e60-513c | V1.0 for Public consultation version | 5 | 37 | 4 | - | 2014-12-04 09:29:10 | Steve Wilkin | ELEXON Limited | final | a) Nominated Electricity Market Operators, who shall make this information available to Market Participants, according to Article 33; | a) Nominated Electricity Market Operators, who shall make this information available to Market Participants, according to Article 33; [NEW] b) any third parties to whom any of its TSO functions has been assigned or delegated pursuant to the Network Code on Electricity Balancing, who shall make this information available to its Balance Responsible Parties and/or other relevant participants. [THEN RE-LABEL paragraph b) as c) and c) as d).] | This does not take account of the role of non-TSO market operators, settlement administrators or other third parties who might have been tasked under the Balancing Network Code with some TSO activities including market administration. NEMOs are unlikely to be the only market operators who need to notify their participants. Market Participants as formally defined may also be too narrow a definition to cover all parties, for example those who are Balancing Service Providers or Balance Responsible Parties? |  |  | legal |  |  |  | Non-confidential
0005-6fb5-2933-2526-d605 | V1.0 for Public consultation version | 5 | 37 | 4 | - | 2014-12-08 17:01:15 | Jasmina PIERRE | EdF | final | Each TSO who is in Emergency, Blackout or Restoration State shall inform at least the following parties: a) Nominated Electricity Market Operators, who shall make this information available to Market Participants, according to Article 33; b) DSOs and Significant Grid Users; and c) its National Regulatory Authorities, or when explicitly foreseen in national law, other relevant national authorities. | Each TSO who is in large-scale Emergency, Blackout or Restoration State shall inform at least the following parties: a) Nominated Electricity Market Operators, who shall make this information available to Market Participants, according to Article 33; b) DSOs and Significant Grid Users; and c) its National Regulatory Authorities, or when explicitly foreseen in national law, other relevant national authorities. TSO needs to notify all market players about potential upcoming emergency situations that may lead to larger degradation and market suspension | Market suspension should be limited to larger degradation with a significant part of the load to be curtailed (“large-scale” emergency situations in opposite to “mid-scale” situations). Ahead in real-time (Day-head or Intra-Day timescales), TSO may anticipate potential upcoming situations with major risk that market based resources (activated up to H-1 trough intra-day and balancing markets) will not be sufficient to prevent from entering into emergency state. Although impacts are uncertain, TSO still need to notify all market players about such exceptional situations that may lead to larger degradation and market suspension. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2216 | V1.0 for Public consultation version | 5 | 37 | 4 | b | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | DSOs and Significant Grid Users | DSOs, Significant Grid Users and Type A Power Generating Modules identified in Restoration Plan as providing procured services to the relevant Network Operator | If the TSO does not inform Type A generators, how they how are they to know they are, according to the Code, to meet obligations in the Restoration Plan? |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1883 | V1.0 for Public consultation version | 5 | 37 | 4 | B | 2014-12-08 13:31 | Garth Graham | SSE |  | DSOs and Significant Grid Users | DSOs, and Significant Grid Users AND TYPE A POWER GENERATING MODULES IDENTIFIED IN RESTORATION PLAN AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR | If the TSO does not inform Type A generators then how are they to know they are, according to the Code, to meet obligations in the Restoration Plan? Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-2215 | V1.0 for Public consultation version | 5 | 37 | 4 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO who is in Emergency, Blackout or Restoration State shall inform at least the following parties: (…) | Each TSO who is in Emergency, Blackout or Restoration State shall inform at least the following parties of which state they are in: (…) | It is not clear what the TSOs are informing the parties of. |  |  | Technical | Editorial
0005-e495-5e7a-d54d-1881 | V1.0 for Public consultation version | 5 | 37 | 4 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO who is in Emergency, Blackout or Restoration State shall inform at least the following parties: | Each TSO who is in Emergency, Blackout or Restoration State shall inform at least the following parties of WHICH STATE THEY ARE IN: | Its not clear what the TSOs are informing parties of.
0005-e495-5e7a-d54d-2339 | V1.0 for Public consultation version | 5 | 37 | 5 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | - | Each TSO shall inform DSOs and Significant Grid Users identified in the System Defence Plan or Restoration Plan as soon as possible about necessary and planned measures for operation and restoration in Emergency, Blackout and Restoration state. a) DSOs shall be provided with real-time information about at least: i. Current status and forecast data for the Observability area of the DSO; ii. Limits of active power, reactive power, step changer and breaker position and available short circuit current at the network interconnection; iii. Information on the current status and schedules of PGMs at the DSO’s grid, if not available to the DSO directly; iv. All necessary information for cascaded measures. b) Significant Grid Users involved in the Restoration Plan shall be provided by the relevant TSO with information about at least: i. Ability and plans to re-energize couplings; ii. Scheduled measures which require cooperation of the Significant Grid User. | Article 37 provides requirements on data requests of the TSO from other Grid Users and data exchanges between TSOs. The only information other Grid Users receive from TSOs is general information on the overall system state in article 37(4). From the DSO’s point of view, this is not sufficient to provide an optimized restoration. In Emergency, Restoration and Blackout state, DSOs and SGUs need information of the current status and planned measures of the TSO which might affect them directly. Only if such information is exchanged as soon as possible, DSOs and SGUs can support restoration to their best endeavours. Operation of the Distribution System becomes more and more complex with the growth of distributed generation. Complex solutions of the DSO (load flow calculations, forecasts) need information about the status and planned schedule of TSO’s assets and generators. For example, if the TSO experiences problems and informs early enough, the DSO can avoid planned switching measures in its grid which might affect the TSO in a negative way. During restoration, early information of the DSO and SGU on re-energization and planned measures gives the DSO/SGU time and opportunity to prepare expected measures (e.g. preparatory measures like disconnecting lines for staged reconnection to avoid high load steps). This will accelerate restoration and therefore save costs. Observability area of the DSO: could be defined here as the area that englobes the first/neighbouring mesh of the Transmission System to the node where the coupling transformer is connected. The idea of information to the DSO as described here should perhaps also be introduced in the NC OS, since additionnal information to the DSOs might also be useful not only in the Emergency, Blackout and Restoration state. |  |  | Technical
0005-e495-5e7a-d54d-2091 | V1.0 for Public consultation version | 5 | 37 | 5 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | new clause | Each TSO shall inform concerned DSOs and Significant Grid Users as soon as possible about necessary and planned measures for operation and restoration in Emergency, Blackout and Restoration state. a) DSOs shall be provided with real-time information about at least: i. Close range of the Transmission System (current status and forecast); ii. Limits of active power, reactive power, step changer and breaker position and available short circuit current at the network interconnection; iii. Information on the current status and schedules of PGMs at the DSO’s grid, if not available to the DSO; iv. All necessary information for cascaded measures. b) Significant Grid Users and Power Generation Modules of Type A involved in the Restoration Plan shall be provided by the relevant TSO with information about at least: i. Ability and plans to re-energize couplings; ii. Scheduled measures which require cooperation of the Significant Grid User. | Article 37 provides requirements on data requests of the TSO from other Grid Users and data exchanges between TSOs. The only information other Grid Users receive from TSOs is general information on the overall system state in article 37(4). From the DSO’s point of view, this is not sufficient to provide an optimized restoration. In Emergency, Restoration and Blackout state, DSOs and SGUs need information of the current status and planned measures of the TSO which might affect them directly. Only if such information is exchanged as soon as possible, DSOs and SGUs can support restoration to their best endeavours. Operation of the Distribution System becomes more and more complex with the growth of distributed generation. Complex solutions of the DSO (load flow calculations, forecasts) need information about the status and planned schedule of TSO’s assets and generators. For example, if the TSO experiences problems and informs early enough, the DSO can avoid planned switching measures in its grid which might affect the TSO in a negative way. During restoration, early information of the DSO and SGU on re-energization and planned measures gives the DSO/SGU time and opportunity to prepare expected measures (e.g. preparatory measures like disconnecting lines for staged reconnection to avoid high load steps). This will accelerate restoration and therefore save costs.
0005-2196-0860-e899-9232 | V1.0 for Public consultation version | 5 | 37 | - | - | 2014-11-28 15:51:08 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | new clause | Each TSO shall inform concerned DSOs and Significant Grid Users as soon as possible about necessary and planned measures for operation and restoration in Emergency, Blackout and Restoration state. a) DSOs shall be provided with real-time information about at least: i. Close range of the Transmission System (current status and forecast); ii. Limits of active power, reactive power, step changer and breaker position and available short circuit current at the network interconnection; iii. Information on the current status and schedules of PGMs at the DSO’s grid, if not available to the DSO; iv. All necessary information for cascaded measures. b) Significant Grid Users and Power Generation Modules of Type A involved in the Restoration Plan shall be provided by the relevant TSO with information about at least: i. Ability and plans to re-energize couplings; ii. Scheduled measures which require cooperation of the Significant Grid User. | Article 37 provides requirements on data requests of the TSO from other Grid Users and data exchanges between TSOs. The only information other Grid Users receive from TSOs is general information on the overall system state in article 37(4). From the DSO’s point of view, this is not sufficient to provide an optimized restoration. In Emergency, Restoration and Blackout state, DSOs and SGUs need information of the current status and planned measures of the TSO which might affect them directly. Only if such information is exchanged as soon as possible, DSOs and SGUs can support restoration to their best endeavours. Operation of the Distribution System becomes more and more complex with the growth of distributed generation. Complex solutions of the DSO (load flow calculations, forecasts) need information about the status and planned schedule of TSO’s assets and generators. For example, if the TSO experiences problems and informs early enough, the DSO can avoid planned switching measures in its grid which might affect the TSO in a negative way. During restoration, early information of the DSO and SGU on re-energization and planned measures gives the DSO/SGU time and opportunity to prepare expected measures (e.g. preparatory measures like disconnecting lines for staged reconnection to avoid high load steps). This will accelerate restoration and therefore save costs. |  |  | technical |  |  |  | Non-confidential
0005-48a5-c3c1-7eb6-b122 | V1.0 for Public consultation version | 5 | 37 | - | - | 2014-12-08 16:38:51 | Rothermann Philippe |  | final |  |  | Since there are switsches whose state ist not transmitted to the SCADA, DSOs are not able to ensure in any case that there are no islands. Please note that Ssmall DSO's are do not even possessing a SCADA. The text should say, that the DSO only inform about what he can seeis able to detect. | [6 empty] | Non-confidential
0005-2195-75dc-0e43-acaf | V1.0 for Public consultation version | 5 | 37 | - | - | 2014-12-08 17:17:33 | Paul Doyle | ESB Generation & Wholesale Markets | final | new clause | Each TSO shall inform concerned DSOs and Significant Grid Users as soon as possible about necessary and planned measures for operation and restoration in Emergency, Blackout and Restoration state. a) DSOs shall be provided with real-time information about at least: i. Close range of the Transmission System (current status and forecast); ii. Limits of active power, reactive power, step changer and breaker position and available short circuit current at the network interconnection; iii. Information on the current status and schedules of PGMs at the DSO’s grid, if not available to the DSO; iv. All necessary information for cascaded measures. b) Significant Grid Users and Power Generation Modules of Type A involved in the Restoration Plan shall be provided by the relevant TSO with information about at least: i. Ability and plans to re-energize couplings; ii. Scheduled measures which require cooperation of the Significant Grid User. | Article 37 provides requirements on data requests of the TSO from other Grid Users and data exchanges between TSOs. The only information other Grid Users receive from TSOs is general information on the overall system state in article 37(4). From the DSO’s point of view, this is not sufficient to provide an optimized restoration. In Emergency, Restoration and Blackout state, DSOs and SGUs need information of the current status and planned measures of the TSO which might affect them directly. Only if such information is exchanged as soon as possible, DSOs and SGUs can support restoration to their best endeavours. Operation of the Distribution System becomes more and more complex with the growth of distributed generation. Complex solutions of the DSO (load flow calculations, forecasts) need information about the status and planned schedule of TSO’s assets and generators. For example, if the TSO experiences problems and informs early enough, the DSO can avoid planned switching measures in its grid which might affect the TSO in a negative way. During restoration, early information of the DSO and SGU on re-energization and planned measures gives the DSO/SGU time and opportunity to prepare expected measures (e.g. preparatory measures like disconnecting lines for staged reconnection to avoid high load steps). This will accelerate restoration and therefore save costs. |  |  | technical |  |  |  | Non-confidential
0005-6f65-c572-a35d-3315 | V1.0 for Public consultation version | 5 | 38 | 1 | - | 2014-12-04 13:57:12 | Dekinderen Eric | Genrator company | final | At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | At least one of these communication channels shall have backup power supply for 20 up to 24 hours, be prioritised and not use public communication channel. | It is not done to specify only a minimum vlaue; also a maximum value has to be defined |  |  | technical |  |  |  | Non-confidential
0005-2159-9dd0-3b94-f126 | V1.0 for Public consultation version | 5 | 38 | 1 | - | 2014-12-05 11:04:33 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. Additional costs shall be approved by the NRA. Costs for significant grid users must be refunded, based on national regulation. | Approved costs are refunded to DSOs and TSOs, for significant grid users there must be a refundation. | 1 | 5 | legal |  |  |  | Non-confidential
0005-9675-ade4-a03d-0c30 | V1.0 for Public consultation version | 5 | 38 | 1 | - | 2014-12-04 13:56:36 | Dekinderen Eric | Genrator company | final | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. | to define by ENTSOE | This requirment will block a lot of type B wind farms for their participation in the System Defence Plan because they are unmanned. Is ENTSOE aware of this? |  |  | technical |  |  |  | Non-confidential
0005-6fa2-2f70-e6a5-423c | V1.0 for Public consultation version | 5 | 38 | 1 | - | 2014-11-28 15:51:09 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans at their disposal. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. The described voice communication equipment will be put at their disposal by the Relevant TSO. Costs will be borne by the relevant TSO. | The described equipment is only there for system services. Uniformity of the equipment must prevent lots of different types of equipment (in the TSO control room). All using the same type also limits possible roots for disturbance of the whole communication chain. |  |  | technical |  |  |  | Non-confidential
0005-2196-db6e-e76d-8476 | V1.0 for Public consultation version | 5 | 38 | 1 | - | 2014-11-28 15:51:10 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. |  | This requirment will block a lot of type B wind farms for their participation in the System Defence Plan because they are unmanned. Is ENTSOE aware of this? |  |  | technical |  |  |  | Non-confidential
0005-215a-db6e-e76d-c551 | V1.0 for Public consultation version | 5 | 38 | 1 | - | 2014-11-28 15:51:11 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | At least one of these communication channels shall, for the purposes of this code, have backup power supply for a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. This communication channel shall be prioritised and not use any public communication channel. | Use of the term 'at least' allows the TSO to specify a value without any limit in excess of 24hours. This is not the intention nor is it acceptable. |  |  | technical |  |  |  | Non-confidential
0005-bdc1-ae4a-10de-a507 | V1.0 for Public consultation version | 5 | 38 | 1 | - | 2014-12-03 11:19:41 | AXPO Group |  | final | Original text of issue 13.10.2014 | see Comment | Only one voice channel is required. It is NOT possible to exchange all the information required by article 37 by only one channel and by voice only. At least one secure data channel, next to the voice channel, is needed. In Article 37 a wide range of data is demanded by the TSO. But here in Article 38 the only required communication infrastructure is for voice only. The demand of data is useless if a functional transport path is not also demanded. |  |  | technical |  |  |  | Non-confidential
0005-2195-38b5-2332-1e7d | V1.0 for Public consultation version | 5 | 38 | 1 | - | 2014-12-08 17:01:16 | Jasmina PIERRE | EdF | final | 1. Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | 1. Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. All costs related to requested redundant communcation channels shall be borne by the relevant TSO. | Foreseeing redundant (voice) communication channels and measures to ensure the extended (>24h) availability of critical tools and facilities are evenly costs that are not incurred by market parties which have not been identified in the System Defense and Restoration Plans. In order to ensure the neutrality of the requirements of the System Defense and Restoration Plans upon the competitive position of the identified significant grid users (power plants and industrial consumers) these costs should also be borne by the TSO instructing these requirements. This should be added in the arrangements of a proper contractual or legal framework. |  |  | technical |  |  |  | Non-confidential
0005-e495-4ecc-0ddf-b861 | V1.0 for Public consultation version | 5 | 38 | 1 | - | 2014-12-08 17:09:25 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans at their disposal. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. The described voice communication equipment will be put at their disposal by the Relevant TSO. Costs will be borne by the relevant TSO. | The described equipment is only there for system services. Uniformity of the equipment must prevent lots of different types of equipment (in the TSO control room). All using the same type also limits possible roots for disturbance of the whole communication chain. |  |  | technical |  |  |  | Non-confidential
0005-e4e5-d360-0d7b-c151 | V1.0 for Public consultation version | 5 | 38 | 1 | - | 2014-12-08 17:09:26 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. |  | This requirment will block a lot of type B wind farms for their participation in the System Defence Plan because they are unmanned. Is ENTSOE aware of this? |  |  | technical |  |  |  | Non-confidential
0005-6f8d-4e90-0cb3-f70f | V1.0 for Public consultation version | 5 | 38 | 1 | - | 2014-12-08 17:09:27 | Paul Doyle | ESB Generation & Wholesale Markets | final | At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | At least one of these communication channels shall, for the purposes of this code, have backup power supply for a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. This communication channel shall be prioritised and not use any public communication channel. | Use of the term 'at least' allows the TSO to specify a value without any limit in excess of 24hours. This is not the intention nor is it acceptable. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2340 | V1.0 for Public consultation version | 5 | 38 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | no text proposal. | This provision may introduce a high cost, as it implies that all the SGU (generators in MV) will have to pay for a second channel. If the channel is direct to TSO we might end up with: channel to TSO + redundant channel + channel to DSO. The identification of SGUs (connected to distribution networks) taking part in system defense and restoration plans, must be based on a CBA which should take into account all these new requirements on voice communication channel redundancy. Also, the question can also be asked why we need voice communication. If type A PGMs stay in the code (and we definitely suggest to delete them - see our arguments in art. 8§4), how will this be done for type A PGMs? This is just unfeasible (it will already be difficult for type B PGMs). |  |  | Technical
0005-e495-5e7a-d54d-2092 | V1.0 for Public consultation version | 5 | 38 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans at their disposal. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. The described voice communication equipment will be put at their disposal by the Relevant TSO. Costs will be borne by the relevant TSO. | The described equipment is only there for system services. Uniformity of the equipment must prevent lots of different types of equipment (in the TSO control room). All using the same type also limits possible roots for disturbance of the whole communication chain.
0005-e495-5e7a-d54d-2093 | V1.0 for Public consultation version | 5 | 38 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. |  | This requirment will block a lot of type B wind farms for their participation in the System Defence Plan because they are unmanned. Is ENTSOE aware of this?
0005-e495-5e7a-d54d-2094 | V1.0 for Public consultation version | 5 | 38 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | At least one of these communication channels shall, for the purposes of this code, have backup power supply for a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. This communication channel shall be prioritised and not use any public communication channel. | Use of the term 'at least' allows the TSO to specify a value without any limit in excess of 24hours. This is not the intention nor is it acceptable.
0005-e495-5e7a-d54d-2217 | V1.0 for Public consultation version | 5 | 38 | 1 |  | 2014-12-08 21:33 | EDK | GFS | final | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | Each TSO, DSO and Type D Power Generation Module, identified in the System Defence Plan or Restoration Plan (…) | It is impractical and unreasonable to expect domestic or even small and medium generators to have a redundant voice communication channel and that it has at least 24 hours backup. These users rely solely on public voice communication channels (landlines and mobiles). |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1885 | V1.0 for Public consultation version | 5 | 38 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO, DSO and Significant Grid User, identified in the System Defence Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | Each TSO, DSO and Significant Grid User TYPE D GENERATOR , identified in the ………shall have at least one redundant voice communication channel to exchange the necessary information for System Defence and Restoration Plans. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | Given the SGU definition it is impractical to expect domestic, or even SMEs to have a redundant voice communication channel and that it have at least 24 hours backup. These users rely on public voice communication channels such as landlines and mobile network. It is wholly unreasonable, and impractical to oblige SGUs in this way.
0005-e495-5e7a-d54d-1887 | V1.0 for Public consultation version | 5 | 38 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | …… identified in the System Defence Plan or Restoration Plan, shall have at least ……. | …… identified in the System Defence Plan or Restoration Plan AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR, shall have at least …….. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-1889 | V1.0 for Public consultation version | 5 | 38 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | …... At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | …... At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. A SIGNIFICANT GRID USER MAY USE THE DEROGATION AND APPEAL PROCESS SET OUT IN THE NC RFG OR NC DC (AS APPROPRIATE) IF THEY BELIEVE THE OBLIGATIONS SET OUT IN THIS ARTICLE 38 PROPOSED BY THE TSO ARE TO ONEROUS. | A right of derogation and appeal (to the NRA) is required.
0005-6fb5-00bd-4abb-c211 | V1.0 for Public consultation version | 5 | 38 | - | - | 2014-12-08 20:11:09 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | A residential consumer providing any form of demand response could be forced to install a black-out proof direct communication line with the DSO. This will in turn require them to purchase back-up generation in order to be able to ensure communication capability. It is unclear how these costs are to be paid for. This requirement is unrealistic and prohibitively expensive, and therefore can not be fulfilled by any residential consumer. |  |  | legal |  |  |  | Non-confidential
0005-9675-00ab-c8cb-e454 | V1.0 for Public consultation version | 5 | 38 | - | - | 2014-12-08 19:51:15 | Roland Tual | SEDC | final | Each TSO, DSO and Significant Grid User, identified in the System Defense Plan or Restoration Plan, shall have at least one redundant voice communication channel to exchange the necessary information for System Defense and Restoration Plans. At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritized and not use public communication channel. | [8 empty] | confidential
0005-6fa1-28cc-e35a-e87b | V1.0 for Public consultation version | 5 | 39 | 1 | - | 2014-12-08 16:39:19 | Markus Hemmer | EnBW | final | Each TSO shall make available critical tools and facilities defined in Article 8(15) [NC OS] for at least 24 hours in case of loss of primary power supply. | Each TSO shall, for the purposes of this code, make available critical tools and facilities as defined in Article 8(15) [NC OS]. These tools and facilities shall also in case of loss of primary power supply remain available during a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. | Use of the term 'at least' allows the TSO to specify a value without any limit in excess of 24hours. This is not the intention nor is it acceptable. The maximum restoration time for Critical Grid Users is less than 24 hours. Installing back up power supply for 24 hours and more leads only to useless costs. |  |  | technical |  |  |  | Non-confidential
0005-bd85-ac50-0beb-84b9 | V1.0 for Public consultation version | 5 | 39 | 1 | - | 2014-12-08 17:09:29 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall make available critical tools and facilities defined in Article 8(15) [NC OS] for at least 24 hours in case of loss of primary power supply. | Each TSO shall, for the purposes of this code, make available critical tools and facilities as defined in Article 8(15) [NC OS]. These tools and facilities shall also in case of loss of primary power supply remain available during a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. | Use of the term 'at least' allows the TSO to specify a value without any limit in excess of 24hours. This is not the intention nor is it acceptable. The maximum restoration time for Critical Grid Users is less than 24 hours. Installing back up power supply for 24 hours and more leads only to useless costs. |  |  | technical |  |  |  | Non-confidential
0005-bdd6-cbb0-e961-17ee | V1.0 for Public consultation version | 5 | 39 | 1 | - | 2014-11-28 15:51:12 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall make available critical tools and facilities defined in Article 8(15) [NC OS] for at least 24 hours in case of loss of primary power supply. | Each TSO shall, for the purposes of this code, make available critical tools and facilities as defined in Article 8(15) [NC OS]. These tools and facilities shall also in case of loss of primary power supply remain available during a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. | Use of the term 'at least' allows the TSO to specify a value without any limit in excess of 24hours. This is not the intention nor is it acceptable. The maximum restoration time for Critical Grid Users is less than 24 hours. Installing back up power supply for 24 hours and more leads only to useless costs. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2095 | V1.0 for Public consultation version | 5 | 39 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall make available critical tools and facilities defined in Article 8(15) [NC OS] for at least 24 hours in case of loss of primary power supply. | Each TSO shall, for the purposes of this code, make available critical tools and facilities as defined in Article 8(15) [NC OS]. These tools and facilities shall also in case of loss of primary power supply remain available during a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. | Use of the term 'at least' allows the TSO to specify a value without any limit in excess of 24hours. This is not the intention nor is it acceptable. The maximum restoration time for Critical Grid Users is less than 24 hours. Installing back up power supply for 24 hours and more leads only to useless costs.
0005-e495-5e7a-d54d-2218 | V1.0 for Public consultation version | 5 | 39 | 1 |  | 2014-12-08 21:33 | EDK | GFS | final | At least one of these communication channels shall have backup power supply for at least 24 hours, be prioritised and not use public communication channel. | At least one of these communication channels shall, for the purposes of this code, have backup power supply for a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. This communication channel shall be prioritised and not use any public communication channel. | Use of the term 'at least' allows the TSO to specify a value without any limit in excess of 24hours. This is not the intention nor is it acceptable. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2219 | V1.0 for Public consultation version | 5 | 39 | 1 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO shall make available critical tools and facilities defined in Article 8(15) [NC OS] for at least 24 hours in case of loss of primary power supply. | Each TSO shall, for the purposes of this code, make available critical tools and facilities as defined in Article 8(15) [NC OS]. These tools and facilities shall also in case of loss of primary power supply remain available during a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. | Use of the term 'at least' allows the TSO to specify a value without any limit in excess of 24 hours (3 days, 1 week, 1 month???). The maximum restoration time for Critical Grid Users is less than 24 hours. Installing back up power supply for 24 hours and more leads only to unjustified costs. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1891 | V1.0 for Public consultation version | 5 | 39 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | [title] Facilities | TOOLS AND Facilities | This article refers to both tools and facilities so the title of the article should reflect this.
0005-e4d1-86f2-a35d-7c69 | V1.0 for Public consultation version | 5 | 39 | 2 | - | 2014-12-04 13:58:31 | Dekinderen Eric | Genrator company | final | Each DSO and Significant Grid User, identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | Each DSO and Significant Grid User, identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for 20 up to 24 hours in case of loss of primary power supply. | According to the current nuclear regulation, all Belgian nuclear power plants are obliged to shut down completely when the external network is not available during 24 hours. It is the interest of all to impose a maximum blackout for less than 24 hours |  |  | legal |  |  |  | Non-confidential
0005-969d-ad7e-e616-df99 | V1.0 for Public consultation version | 5 | 39 | 2 | - | 2014-12-08 16:39:19 | Markus Hemmer | EnBW | final | Each DSO and Significant Grid User, identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | Each DSO and Significant Grid User, identified in the Restoration Plan shall, for the purposes of this code, make available critical tools and facilities used in the Restoration Plan. These tools and facilities shall also in case of loss of primary power supply remain available during a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. | The time to have power supply should be ajar to that of e.g. nuclear power stations in its control area, since if there is a longer blackout than 24 h, TSO is the only one who has an overall view. use of the term 'at least' allows the TSO to specify a value without limit in excess of 24hours. This is not the intention nor is it acceptable. |  |  | technical |  |  |  | Non-confidential
0005-e495-2780-0cb3-48a3 | V1.0 for Public consultation version | 5 | 39 | 2 | - | 2014-12-08 17:09:31 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each DSO and Significant Grid User, identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | Each DSO and Significant Grid User, identified in the Restoration Plan shall, for the purposes of this code, make available critical tools and facilities used in the Restoration Plan. These tools and facilities shall also in case of loss of primary power supply remain available during a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. | The time to have power supply should be ajar to that of e.g. nuclear power stations in its control area, since if there is a longer blackout than 24 h, TSO is the only one who has an overall view. use of the term 'at least' allows the TSO to specify a value without limit in excess of 24hours. This is not the intention nor is it acceptable. |  |  | technical |  |  |  | Non-confidential
0005-e4bd-5e31-7d26-92a9 | V1.0 for Public consultation version | 5 | 39 | 2 | - | 2014-12-08 16:38:52 | Rothermann Philippe |  | final |  |  | What means "shall make available … for at least 24 hours" for our substations? Do we have to upgrade the batteries's in our substations? | [6 empty] | Non-confidential
0005-bd99-c447-a1dc-4056 | V1.0 for Public consultation version | 5 | 39 | 2 | - | 2014-12-07 12:51:42 | Herve MELJAC | EUR | final | Each DSO and Significant Grid User, identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | to be defined | The scope of critical tools and facilities of this requirement should be defined more clearly. |  |  | legal |  |  |  | Non-confidential
0005-bd9a-663e-e76d-223a | V1.0 for Public consultation version | 5 | 39 | 2 | - | 2014-11-28 15:51:13 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each DSO and Significant Grid User, identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | Each DSO and Significant Grid User, identified in the Restoration Plan shall, for the purposes of this code, make available critical tools and facilities used in the Restoration Plan. These tools and facilities shall also in case of loss of primary power supply remain available during a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. | The time to have power supply should be ajar to that of e.g. nuclear power stations in its control area, since if there is a longer blackout than 24 h, TSO is the only one who has an overall view. use of the term 'at least' allows the TSO to specify a value without limit in excess of 24hours. This is not the intention nor is it acceptable. |  |  | technical |  |  |  | Non-confidential
0005-487d-50a8-12d2-be1f | V1.0 for Public consultation version | 5 | 39 | 2 | - | 2014-12-03 11:19:41 | AXPO Group |  | final | Original text of issue 13.10.2014 | see Comment | A time frame alone is not sufficient. Obviously high voltage switches and other grid control devices need a certain amount of energy to turn them on and off. Rather than defining a time frame of 24 hours it would be more effective to define an "amount of stored energy" which a substation has to keep available. This is essential for planning a substation. According to a prerequisite of "energy which to be kept available independently by a substation" the necessary electrical batteries or other forms of energy storage can be designed. A prerequisite of 24 hours only is not enough. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2342 | V1.0 for Public consultation version | 5 | 39 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each DSO and Significant Grid User, identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | no text proposal. | What is precisely meant by 'tools' and 'facilities', because this will determine which DSO 'installations' and 'technical equipment' will have to be upgraded, and finally what costs may be expected. Is there a need for having the same autonomy all over Europe immediately? A suggestion could be to start on a National level and to aim within X years to the same autonomy. A CBA to justify the 24 hours seems appropriate. Current technical guidelines in Germany require backup power for DSO assets for only 8 to 12 hours. Retrofitting all assets in Germany will on its own induce costs as high as 330 million EURO. |  |  | Technical
0005-e495-5e7a-d54d-2096 | V1.0 for Public consultation version | 5 | 39 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each DSO and Significant Grid User, identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | Each DSO and Significant Grid User, identified in the Restoration Plan shall, for the purposes of this code, make available critical tools and facilities used in the Restoration Plan. These tools and facilities shall also in case of loss of primary power supply remain available during a minimum time, between 8 and 24 hours, to be agreed between the TSO and the involved party. | The time to have power supply should be ajar to that of e.g. nuclear power stations in its control area, since if there is a longer blackout than 24 h, TSO is the only one who has an overall view. Use of the term 'at least' allows the TSO to specify a value without limit in excess of 24hours. This is not the intention nor is it acceptable.
0005-e495-5e7a-d54d-2220 | V1.0 for Public consultation version | 5 | 39 | 2 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each DSO and Significant Grid User, identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | Each DSO and Type D Power Park Module, identified in the Restoration Plan shall, for the purposes of this code (...) | It is impractical and unreasonable to expect domestic or even small and medium generators to make available critical tools and facilities for at least 24 hour backup. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2341 | V1.0 for Public consultation version | 5 | 39 | 2 |  | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each DSO and Significant Grid User, identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | no text proposal. | Primary power supply is not defined in the glossary. |  |  | Technical
0005-e495-5e7a-d54d-1892 | V1.0 for Public consultation version | 5 | 39 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each DSO and Significant Grid User, identified ….., shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | Each DSO and Significant Grid User TYPE D GENERATOR, identified ……, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | Given the SGU definition it is impractical to expect domestic, or even SMEs to make available critical tools and facilities for at least 24 hours backup. Would the personnel writing this code expect, themselves or other family members at home, to do this?!
0005-e495-5e7a-d54d-1893 | V1.0 for Public consultation version | 5 | 39 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | ……identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | ……identified in the Restoration Plan, AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-1894 | V1.0 for Public consultation version | 5 | 39 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | ……identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | ……identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply.A SIGNIFICANT GRID USER MAY USE THE DEROGATION AND APPEAL PROCESS SET OUT IN THE NC RFG OR NC DC (AS APPROPRIATE) IF THEY BELIEVE THE OBLIGATIONS SET OUT IN THIS ARTICLE 38 PROPOSED BY THE TSO ARE TO ONEROUS. | A right of derogation and appeal (to the NRA) is required.
0005-6fa1-019e-e3be-c093 | V1.0 for Public consultation version | 5 | 39 | 3 | - | 2014-12-08 16:39:19 | Markus Hemmer | EnBW | final | Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities defined in Article 8(15) [NC OS]. Each TSO shall ensure backup power supply for its backup control room for at least 24 hours in case of loss of primary power supply. | Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities defined in Article 8(15) [NC OS]. Each TSO shall ensure backup power supply for its backup control room for at least 72 hours in case of loss of primary power supply. | The time to have power supply should be ajar to that of e.g. nuclear power station, since if there is a longer blackout than 24 h, TSO is the only one who has an overall view. |  |  | technical |  |  |  | Non-confidential
0005-216d-9cec-0f6f-f824 | V1.0 for Public consultation version | 5 | 39 | 3 | - | 2014-12-08 17:09:32 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities defined in Article 8(15) [NC OS]. Each TSO shall ensure backup power supply for its backup control room for at least 24 hours in case of loss of primary power supply. | Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities defined in Article 8(15) [NC OS]. Each TSO shall ensure backup power supply for its backup control room for at least 24 hours in case of loss of primary power supply. | The time to have power supply should be ajar to that of e.g. nuclear power stations in its control area, since if there is a longer blackout than 24 h, TSO is the only one who has an overall view. |  |  | technical |  |  |  | Non-confidential
0005-4856-2f70-e899-4ddf | V1.0 for Public consultation version | 5 | 39 | 3 | - | 2014-11-28 15:51:14 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities defined in Article 8(15) [NC OS]. Each TSO shall ensure backup power supply for its backup control room for at least 24 hours in case of loss of primary power supply. | Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities defined in Article 8(15) [NC OS]. Each TSO shall ensure backup power supply for its backup control room for at least 24 hours in case of loss of primary power supply. | The time to have power supply should be ajar to that of e.g. nuclear power stations in its control area, since if there is a longer blackout than 24 h, TSO is the only one who has an overall view. |  |  | technical |  |  |  | Non-confidential
0005-e4e5-38d3-258a-66a2 | V1.0 for Public consultation version | 5 | 39 | 3 | - | 2014-12-08 17:01:16 | Jasmina PIERRE | EdF | final | 3. Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities defined in Article 8(15) [NC OS]. Each TSO shall ensure backup power supply for its backup control room for at least 24 hours in case of loss of primary power supply. | 3. Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities defined in Article 8(15) [NC OS]. Each TSO shall ensure backup power supply for its backup control room for at least 72 hours in case of loss of primary power supply. | If there is a longer blackout than 24 h, TSO should keep an overall view required to esnure system restoration. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2097 | V1.0 for Public consultation version | 5 | 39 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities defined in Article 8(15) [NC OS]. Each TSO shall ensure backup power supply for its backup control room for at least 24 hours in case of loss of primary power supply. | Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities defined in Article 8(15) [NC OS]. Each TSO shall ensure backup power supply for its backup control room for at least 24 hours in case of loss of primary power supply. | The time to have power supply should be ajar to that of all high priority Significant Grid Users in its control area, since if there is a longer blackout than 24 h, TSO is the only one who has an overall view.
0005-bd85-4fb0-3bf8-feb1 | V1.0 for Public consultation version | 5 | 39 | 5 | - | 2014-12-05 11:04:55 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Substations which are necessary for restoration shall be operational in case of loss of primary power supply, allowing the use of critical tools and facilities of TSOs and DSOs. | Substations which are necessary for restoration shall be operational in case of loss of primary power supply, allowing the use of critical tools and facilities of TSOs and DSOs. Additional costs shall be approved by the NRA. Costs for significant grid users must be refunded, based on national regulation. | Approved costs are refunded to DSOs and TSOs, for significant grid users there must be a refundation. | 1 | 5 | legal |  |  |  | Non-confidential
0005-e4e5-9ccf-7d26-c68a | V1.0 for Public consultation version | 5 | 39 | 5 | - | 2014-12-08 16:38:52 | Rothermann Philippe |  | final |  |  | Please define in detail what “operational” means | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-2343 | V1.0 for Public consultation version | 5 | 39 | 5 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Substations which are necessary for restoration shall be operational in case of loss of primary power supply, allowing the use of critical tools and facilities of TSOs and DSOs. | no text proposal. | This is a very general high level requirement suggesting that many/some substations should have resilient power supplies. This seems OK for main substations, but does this extend to substations connecting SGUs? In this case, this requirements goes far beyond state-of-art. We would expect a CBA to justify it. |  |  | Technical
0005-e495-5e7a-d54d-1896 | V1.0 for Public consultation version | 5 | 39 | 5 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Substations which are necessary for restoration shall be operational in case of loss of primary power supply, allowing the use of critical tools and facilities of TSOs and DSOs. | TSOS AND DSOS Substations which are necessary for restoration shall be operational in case of loss of primary power supply, allowing the use of critical tools and facilities of TSOs and DSOs. | It should be made clear that the substations in question only relate to TSO and DSO substations.
0005-e495-5e7a-d54d-1898 | V1.0 for Public consultation version | 5 | 39 | 5 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | …… which are necessary for restoration shall be operational in case of loss of primary power supply, allowing the use of critical tools and facilities of TSOs and DSOs. | …. which are necessary for restoration shall be operational FOR AT LEAST 24 HOURS in case of loss of primary power supply, allowing the use of critical tools and facilities of TSOs and DSOs. | Given the references in Art 38(1), Art 39 (1), (2) and (3) it is bizarre that no timeframe is set out in this paragraph (5).
0005-6f65-ac61-4ddb-e51f | V1.0 for Public consultation version | 5 | 39 | - | - | 2014-12-08 20:11:09 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | It is unclear what is meant here and what would be required for a residential consumer under this article. Would this involve staying at home or at work for 24 hours? This article illustrates again that these requirements are not meant to be fulfilled by households. Residential consumers should therefore be explicitly excluded from the application of this network code. |  |  | legal |  |  |  | Non-confidential
0005-bd99-d37d-c79f-141a | V1.0 for Public consultation version | 5 | 39 | - | - | 2014-12-08 19:51:15 | Roland Tual | SEDC | final | Each DSO and Significant Grid User, identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. | [8 empty] | confidential
0005-e495-5e7a-d54d-2262 | V1.0 for Public consultation version | 5 | 39 |  |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each DSO and Significant Grid User, identified in the Restoration Plan, shall make available critical tools and facilities used in Restoration Plan for at least 24 hours in case of loss of primary power supply. |  | It is unclear what is meant here and what would be required of a smaller consumer under this article? Do they give up control to the DSO so that the DSO can control their appliances? (If smaller consumers are not under consideration for this measure - why are they included?)
0005-6f79-76ec-e35a-4ffb | V1.0 for Public consultation version | 6 | 40 | 1 | - | 2014-12-08 16:39:19 | Markus Hemmer | EnBW | final | Each TSO shall periodically assess the proper functioning of equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. [...] | delete | The proper functioning is assessed in comissioning test. As long as there are no technical constraints the proper functioning is granted. Else this would lead to extremes cossts for Grid Users and an extreme loss of EOH for their equipment. |  |  | technical |  |  |  | Non-confidential
0005-96c5-d360-0d17-8e34 | V1.0 for Public consultation version | 6 | 40 | 1 | - | 2014-12-08 17:09:34 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall periodically assess the proper functioning of equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. | Each TSO shall periodically assess the proper functioning of it's own equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. | Make sure that also the TSO's equipment is tested. |  |  | legal |  |  |  | Non-confidential
0005-6fb5-9d55-a0b0-23b1 | V1.0 for Public consultation version | 6 | 40 | 1 | - | 2014-12-07 12:51:42 | Herve MELJAC | EUR | final | Each TSO shall periodically assess the proper functioning of equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. | Each TSO shall periodically assess the proper functioning of equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC] and in coordination with the implicated DSO or SGU. | Use of coordination ensures that an agreement is found between parties on the means to periodically assess capability. |  |  | legal |  |  |  | Non-confidential
0005-6f66-569e-ea29-3f13 | V1.0 for Public consultation version | 6 | 40 | 1 | - | 2014-11-28 15:51:15 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall periodically assess the proper functioning of equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. | Each TSO shall periodically assess the proper functioning of it's own equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. | Make sure that also the TSO's equipment is tested. |  |  | legal |  |  |  | Non-confidential
0005-6fb5-026a-10de-db82 | V1.0 for Public consultation version | 6 | 40 | 1 | - | 2014-12-03 11:11:00 | AXPO Group |  | final | Original text of issue 13.10.2014 | The TSO has also to be tested. By an independent authority. | Not only the capabilities of DSO's and SGU's need proof of compliance but also the capabilities of the TSO's themselves. Who is going to test them? |  |  | legal |  |  |  | Non-confidential
0005-2145-d37d-c867-8a05 | V1.0 for Public consultation version | 6 | 40 | 1 | - | 2014-12-08 19:51:16 | Roland Tual | SEDC | final | Each TSO shall periodically assess the proper functioning of equipment and capabilities contributing to the System Defense Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defense Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. 4. The test is deemed passed when it fulfills the criteria defined by the Relevant Network Operator. As long as a test fails to fulfill these criteria, the TSO, DSO and Significant Grid User shall repeat the test. | [8 empty] | confidential
0005-bd99-0223-2652-2c1f | V1.0 for Public consultation version | 6 | 40 | 1 | - | 2014-12-08 17:01:17 | Jasmina PIERRE | EdF | final | Each TSO shall periodically assess the proper functioning of equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. | Each TSO shall periodically assess the proper functioning of its own equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. | Need for clarification to make sure that the TSO's equipment is also tested. |  |  | technical |  |  |  | Non-confidential
0005-6f8d-279f-8046-cee7 | V1.0 for Public consultation version | 6 | 40 | 1 | - | 2014-12-08 16:38:54 | Rothermann Philippe |  | final |  |  | Are there also test's of the TSO? | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-2098 | V1.0 for Public consultation version | 6 | 40 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall periodically assess the proper functioning of equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. | Each TSO shall periodically assess the proper functioning of it's own equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. | Make sure that also the TSO's equipment is tested.
0005-e495-5e7a-d54d-2222 | V1.0 for Public consultation version | 6 | 40 | 1 |  | 2014-12-08 21:33 | AG | RWE | final | Each TSO shall periodically assess the proper functioning of equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. | Each NRA shall periodically assess the proper functioning of it's own equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. | TSOs should not test themselves. If NRA is unable or unwilling to perform this task, they can delegate this task to a third, qualified party (e.g. an independent auditor). |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2265 | V1.0 for Public consultation version | 6 | 40 | 1 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each TSO shall periodically assess the proper functioning of equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally, each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, in accordance with Article 35(2) [NC RfG], Article 38(2) [NC DC], and Article 65(1) and (2) [NC HVDC]. |  | Who will (independetly) assess the emergency plan ?
0005-e495-5e7a-d54d-1902 | V1.0 for Public consultation version | 6 | 40 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall periodically assess the proper functioning of equipment and capabilities contributing to the System Defence Plan and the Restoration Plan. Additionally | Each TSO NRA shall periodically assess the proper functioning of equipment and capabilities OF THE TSO contributing to the System Defence Plan and the Restoration Plan. Additionally | It is not acceptable for the TSO to ‘mark their own homework’. The incident, in November 2006, which gave rise to the need for NC E&R, arose from the actions / inactions of TSOs. Stakeholders and consumers across the 28 Member States need to have confidence in the System Defence Plan and the Restoration Plan. Relying upon the TSOs to assess their own proper function and contribution would be wrong. The TSO has a clear conflict of interest. If the NRA is unable or unwilling themselves to perform this task they can either appoint independent auditors to do it on their behalf or ask ACER to do it on behalf of the NRA.
0005-e495-5e7a-d54d-1904 | V1.0 for Public consultation version | 6 | 40 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | ….each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s capabilities that are used in the System Defence Plan or in the Restoration Plan, …. | ….each TSO shall periodically verify the compliance of the DSO’s and Significant Grid User’s AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR, capabilities that are used in the System Defence Plan or in the Restoration Plan, …. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-6fa1-c4ee-e422-ef19 | V1.0 for Public consultation version | 6 | 40 | 2 | - | 2014-12-08 16:39:20 | Markus Hemmer | EnBW | final | Each TSO shall define a test plan, identifying the TSOs, DSOs and Significant Grid Users capabilities and equipment used in System Defence Plan or in Restoration Plan that have to be tested, [...] | delete | The proper functioning is assessed in comissioning test. As long as there are no technical constraints the proper functioning is granted. Else this would lead to extremes cossts for Grid Users and an extreme loss of EOH for their equipment. |  |  | technical |  |  |  | Non-confidential
0005-6f8d-10b5-a0b0-467e | V1.0 for Public consultation version | 6 | 40 | 2 | - | 2014-12-07 12:51:43 | Herve MELJAC | EUR | final | Each TSO shall define a test plan, identifying the TSOs, DSOs and Significant Grid Users capabilities and equipment used in System Defence Plan or in Restoration Plan that have to be tested, and the periodicity and conditions of the tests, in consultation with the DSO and the Significant Grid User, and following minimum requirements set forth in Article 41, Article 42 and Article 43. The test shall follow the methodology described in [NC RfG], [NC DC] and [NC HVDC] for the corresponding tested capability. | Each TSO shall define a test plan, identifying the TSOs, DSOs and Significant Grid Users capabilities and equipment used in System Defence Plan or in Restoration Plan that have to be tested, and the periodicity and conditions of the tests, in coordination with the DSO and the Significant Grid User, and following minimum requirements set forth in Article 41, Article 42 and Article 43. The test shall follow the methodology described in [NC RfG], [NC DC] and [NC HVDC] for the corresponding tested capability. | Use of coordination ensures that an agreement is found between parties, while consultation can lead to a unilateral TSO decision which can be harmful to SGUs. |  |  | legal |  |  |  | Non-confidential
0005-4891-8711-245e-2715 | V1.0 for Public consultation version | 6 | 40 | 2 | - | 2014-12-08 17:01:17 | Jasmina PIERRE | EdF | final | 2. Each TSO shall define a test plan, identifying the TSOs, DSOs and Significant Grid Users capabilities and equipment used in System Defence Plan or in Restoration Plan that have to be tested, and the periodicity and conditions of the tests, in consultation with the DSO and the Significant Grid User, and following minimum requirements set forth in Article 41, Article 42 and Article 43. The test shall follow the methodology described in [NC RfG], [NC DC] and [NC HVDC] for the corresponding tested capability. | 2. Each TSO shall define a test plan, identifying the TSOs, DSOs and Significant Grid Users capabilities and equipment used in System Defence Plan or in Restoration Plan that have to be tested, and the periodicity and conditions of the tests, in coordination with the DSO and the Significant Grid User, and following minimum requirements set forth in Article 41, Article 42 and Article 43. The test shall follow the methodology described in [NC RfG], [NC DC] and [NC HVDC] for the corresponding tested capability. | The consultation process proposed by ENTSO-E would lead the final decision to TSO without possible recourse from others parties if their constraints are not duly considered. It is essential all the instructions given by the TSO for execution respect the technical constraints and minimize related impacts and costs for grid users. ENTSO-E proposals should be reinforced and foresee a final neutral decision from relevant NRA in case no agreement is reached (reference to coordination process defined in article 5). |  |  | technical |  |  |  | Non-confidential
0005-6f79-277f-2fcc-a527 | V1.0 for Public consultation version | 6 | 40 | 2 | - | 2014-12-08 18:18:38 | Thomas Willson |  | final | Each TSO shall define a test plan, …, in consultation with the DSO and the Significant Grid User | Rephrase accordingly to 4(3) [NC RfG] | The clause with the test plan definition can be interpreted as a non-exhaustive requirement. The NC RfG uses a widely accepted wording in Art 4(3) to define these requirements after the NC has been put into force. The same wording should be used here. |  |  | legal |  |  |  | Non-confidential
0005-6fb5-105a-d615-369f | V1.0 for Public consultation version | 6 | 40 | 2 | - | 2014-12-08 23:56:25 | Gunnar Kaestle | Clausthal University of Technology | final | Each TSO shall define a test plan, …, in consultation with the DSO and the Significant Grid User | Rephrase accordingly to 4(3) [NC RfG] | The clause with the test plan definition can be interpreted as a non-exhaustive requirement. The NC RfG uses a widely accepted wording in Art 4(3) to define these requirements after the NC has been put into force. The same wording should be used here. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2344 | V1.0 for Public consultation version | 6 | 40 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall define a test plan, identifying the TSOs, DSOs and Significant Grid Users capabilities and equipment used in System Defence Plan or in Restoration Plan that have to be tested, and the periodicity and conditions of the tests, in consultation with the DSO and the Significant Grid User, and following minimum requirements set forth in Article 41, Article 42 and Article 43. The test shall follow the methodology described in [NC RfG], [NC DC] and [NC HVDC] for the corresponding tested capability. | Each TSO shall define a test plan, identifying the TSOs, DSOs and Significant Grid Users capabilities and equipment used in System Defence Plan or in Restoration Plan that have to be tested, and the periodicity and conditions of the tests, in consultation coordination with the DSO and in consultation the Significant Grid User, and following minimum requirements set forth in Article 41, Article 42 and Article 43. The test shall follow the methodology described in [NC RfG], [NC DC] and [NC HVDC] for the corresponding tested capability. | Cf. remarks art. 8§1.
0005-e495-5e7a-d54d-1906 | V1.0 for Public consultation version | 6 | 40 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall define a test plan, identifying ….. | Each TSO shall SUBMIT TO THE NRA FOR APPROVAL a test plan, identifying ….. | NRA approval is required to avoid this test plan being over onerous on parties or not going far enough to ensure the plans are robust. If the NRA is unable or unwilling themselves to perform this task they can appoint CER to do it on their behalf.
0005-e495-5e7a-d54d-1908 | V1.0 for Public consultation version | 6 | 40 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | …… identifying the TSOs, DSOs and Significant Grid Users capabilities and equipment used in System Defence Plan or in Restoration Plan that have to be tested, and the periodicity and conditions of the tests, in consultation with the DSO and the Significant Grid User, and | …… identifying the TSOs, DSOs and Significant Grid Users AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR, capabilities and equipment used in System Defence Plan or in Restoration Plan that have to be tested, and the periodicity and conditions of the tests, in consultation with the DSO and the Significant Grid User, AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR, and | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-2345 | V1.0 for Public consultation version | 6 | 40 | 3 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO, DSO and Significant Grid User shall ensure that Operational Security is not endangered during the test. | Each TSO, DSO and Significant Grid User shall ensure that Operational Security is not endangered during the test. The impact on all Grid Users due to the test will be as minimal as possible. | The code should also clearly state that the inconvenience for grid users due to testing should be as little as possible. |  |  | Technical
0005-e495-5e7a-d54d-2221 | V1.0 for Public consultation version | 6 | 40 | 3 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities defined in Article 8(15) [NC OS]. Each TSO shall ensure backup power supply for its backup control room for at least 24 hours in case of loss of primary power supply. | Each TSO shall have at least one geographically separate backup control room. The backup control room shall include at least the critical tools and facilities defined in Article 8(15) [NC OS]. Each TSO shall ensure backup power supply for its backup control room for at least 24 hours in case of loss of primary power supply. | The time to have power supply should be ajar to that of all high priority Significant Grid Users in its control area, since if there is a longer blackout than 24 h, TSO is the only one who has an overall view. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1910 | V1.0 for Public consultation version | 6 | 40 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO, DSO and Significant Grid User shall ensure that Operational Security is not endangered during the test. | Each TSO, DSO and Significant Grid User PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR, shall ensure that Operational Security is not endangered during the test. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-2223 | V1.0 for Public consultation version | 6 | 40 | 4 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | The test is deemed passed when it fulfills the criteria defined by the Relevant Network Operator (…) | The test is deemed passed when it fulfills the criteria defined by the NRA (…) | TSOs should not test themselves. If NRA is unable or unwilling to perform this task, they can delegate this task to a third, qualified party (e.g. an independent auditor). |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1912 | V1.0 for Public consultation version | 6 | 40 | 4 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | The test is deemed passed when it fulfils the criteria defined by the Relevant Network Operator. As long as a test fails to fulfil these criteria, the TSO, DSO and Significant Grid User shall repeat the test. | The test is deemed passed when it fulfils the criteria defined by the Relevant Network Operator NRA. As long as a test fails to fulfil these criteria, the TSO, DSO and Significant Grid User shall repeat the test. | Its very nice of the Relevant Network Operator to define the test that they themselves have to meet…..however this is like being allowed to set your own exam questions and then answer it yourself….and mark the paper. The incident, in November 2006, which gave rise to the need for NC E&R, arose from the actions / inactions of TSOs. Stakeholders and consumers across the 28 Member States need to have confidence in the System Defence Plan and the Restoration Plan. Relying upon the Relevant Network Operator to set the test criteria would be wrong. The Relevant Network Operator has a clear conflict of interest. If the NRA is unable or unwilling themselves to perform this task they can either appoint independent auditors to do it on their behalf or ask ACER to do it on behalf of the NRA.
0005-e495-5e7a-d54d-2346 | V1.0 for Public consultation version | 6 | 40 | 5 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | - | The TSO, DSO and the Significant Grid User will not be liable for possible interruptions of other Grid Users during tests, for which a clear motivation can be delivered. These interruptions will not affect the quality of service reporting of the TSO and the DSO. | If DSOs and TSOs can motivate that the tests (e.g. relay testing by the DSO) will inevitably cause some discomfort at grid users' level, this should be considered as a 'force majeure' in the sense that neither DSOs and TSOs will be reliable for possible interruptions, nor will this have an impact on their quality of service reporting. |  |  | Legal
0005-e495-5e7a-d54d-2099 | V1.0 for Public consultation version | 6 | 40 | 5 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Add new Article | All costs for the tests described in Articles 40, 41, 42, 43, 44, 45, 46, 48 and 49 are system operation costs and shall as such be borne by the relevant TSO. | All these tests are only usefull for security of system services. Addressing the costs to the TSO results in limiting costs by testing only what realy makes sense and that costs shall be assessed by the NRA.
0005-e495-5e7a-d54d-2224 | V1.0 for Public consultation version | 6 | 40 | 5 |  | 2014-12-08 21:33 | AG | RWE | final | Add new Article | All costs for the tests described in Articles 40, 41, 42, 43, 44, 45, 46, 48 and 49 are system operation costs and shall as such be borne by the relevant TSO. | All these tests are only usefull for security of system services. Addressing the costs to the TSO results in limiting costs by testing only what realy makes sense and that costs shall be assessed by the NRA. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2100 | V1.0 for Public consultation version | 6 | 40 | 6 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Add new Article | Market participants shall be given notice of these periodic assessments. Practical limitations such as times to carry out testing and the physical capability of the plant shall be considered. | Market participants must be given reasonable notice of these periodic assessments and account should be taken of practical times to carry out testing including the physical capability of the plant and the costs.
0005-bdc1-9cb1-2a51-3f33 | V1.0 for Public consultation version | 6 | 40 | - | - | 2014-12-08 16:38:47 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Add new Article | Market participants shall be given notice of these periodic assessments. Practical limitations such as times to carry out testing and the physical capability of the plant shall be considered. | Market participants must be given reasonable notice of these periodic assessments and account should be taken of practical times to carry out testing including the physical capability of the plant and the costs. |  |  | technical |  |  |  | Non-confidential
0005-e4bd-5e4e-0d7b-1e6f | V1.0 for Public consultation version | 6 | 40 | - | - | 2014-12-08 17:09:35 | Paul Doyle | ESB Generation & Wholesale Markets | final | Add new Article | All costs for the tests described in Articles 40, 41, 42, 43, 44, 45, 46, 48 and 49 are system operation costs and shall as such be borne by the relevant TSO. | All these tests are only usefull for security of system services. Addressing the costs to the TSO results in limiting costs by testing only what realy makes sense and that costs shall be assessed by the NRA. |  |  | legal |  |  |  | Non-confidential
0005-487d-105d-4caf-3241 | V1.0 for Public consultation version | 6 | 40 | - | - | 2014-12-08 20:11:09 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | Households could be forced to undergo annual testing procedures. This procedure will be repeated until they succeed in fulfilling the requirements. Again the cost impact and the inconvenience of this system to consumers is not considered at all. Consumer rights to privacy, safety related issues and social welfare are not mentioned either. |  |  | legal |  |  |  | Non-confidential
0005-6f8e-663e-e8fd-9190 | V1.0 for Public consultation version | 6 | 40 | - | - | 2014-11-28 15:51:16 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Add new Article | All costs for the tests described in Articles 40, 41, 42, 43, 44, 45, 46, 48 and 49 are system operation costs and shall as such be borne by the relevant TSO. | All these tests are only usefull for security of system services. Addressing the costs to the TSO results in limiting costs by testing only what realy makes sense and that costs shall be assessed by the NRA. |  |  | legal |  |  |  | Non-confidential
0005-6fb5-0223-2652-a12c | V1.0 for Public consultation version | 6 | 40 | - | - | 2014-12-08 17:01:18 | Jasmina PIERRE | EdF | final | (new) | All costs for the tests described in Articles 40, 41, 42, 43, 44, 45, 46, 48 and 49 are system operation costs and shall as such be borne by the relevant TSO. | TSOs shall bear all the costs incurred by grid users for (i) the actions/measures carried out upon TSO request; (ii) additional and redundant (voice) communication channels; (iii) measures to ensure the extended (>24h) availability of critical tools and facilities and (iv) for “compliance testing” of equipment and procedures required to ensure reliability of prepared System Defense and Restoration Plans. In particular, "compliance testing" costs should be borne by the relevant TSO. It is required to incentivize TSO to minimize these costs (limiting tests to what realy makes sense) and prevent form any discrimination between grid users in compétition through the markets. These costs shall be assessed by the NRA. |  |  | technical |  |  |  | Non-confidential
0005-e4d1-8710-a3c1-5877 | V1.0 for Public consultation version | 6 | 41 | 1 | - | 2014-12-04 14:01:20 | Dekinderen Eric | Genrator company | final | Each Power Generating Module with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at least every three years, following the methodology described in Article 39(5) [NC RfG]. | Each Power Generating Module with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, every three years, following the methodology described in Article 39(5) [NC RfG]. | to erase "at least" |  |  | technical |  |  |  | Non-confidential
0005-6fb5-d361-29ed-613a | V1.0 for Public consultation version | 6 | 41 | 1 | - | 2014-12-08 16:38:48 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Each Power Generating Module with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at least every three years, following the methodology described in Article 39(5) [NC RfG]. | Each Power Generating Module contracted for Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at an interval to be defined in the contract between three and five years, following the methodology described in Article 39(5) [NC RfG]. | Only PGMs contracted for Blackstart capability should be tested. The interval should be no less than 3 years and no greater than 5 years, and shall be covered under the contract. | [6 empty] | Non-confidential
0005-96b1-386c-e486-5c9b | V1.0 for Public consultation version | 6 | 41 | 1 | - | 2014-12-08 16:39:20 | Markus Hemmer | EnBW | final | Each Power Generating Module with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at least every three years, following the methodology described in Article 39(5) [NC RfG]. | delete | The proper functioning is assessed in comissioning test. The test period of this service is agreed in a contract if the TSOs decides to buy this capabillity. As long as there are no technical constraints the proper functioning is granted. Else this would lead to extremes cossts for Grid Users and an extreme loss of EOH for their equipment. |  |  | technical |  |  |  | Non-confidential
0005-bd85-c3c0-0d17-c2e8 | V1.0 for Public consultation version | 6 | 41 | 1 | - | 2014-12-08 17:09:36 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each Power Generating Module with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at least every three years, following the methodology described in Article 39(5) [NC RfG]. | Each Power Generating Module contracted for Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at an interval to be defined in the contract between three and five years, following the methodology described in Article 39(5) [NC RfG]. | Only PGMs contracted for Blackstart capability should be tested. The interval should be no less than 3 years and no greater than 5 years, and shall be covered under the contract. |  |  | technical |  |  |  | Non-confidential
0005-96b2-a4be-e9c5-968b | V1.0 for Public consultation version | 6 | 41 | 1 | - | 2014-11-28 15:51:17 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each Power Generating Module with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at least every three years, following the methodology described in Article 39(5) [NC RfG]. | Each Power Generating Module contracted for Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at an interval to be defined in the contract between three and five years, following the methodology described in Article 39(5) [NC RfG]. | Only PGMs contracted for Blackstart capability should be tested. The interval should be no less than 3 years and no greater than 5 years, and shall be covered under the contract. |  |  | technical |  |  |  | Non-confidential
0005-2145-2998-126e-d9ad | V1.0 for Public consultation version | 6 | 41 | 1 | - | 2014-12-03 11:11:00 | AXPO Group |  | final | Each Power Generating Module with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at least every three years, following the methodology described in Article 39(5) [NC RfG]. | see Comment | The test interval shall not be defined by the network code but on national level due to the different structure of the power generation infrastructure. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2347 | V1.0 for Public consultation version | 6 | 41 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each Power Generating Module with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at least every three years, following the methodology described in Article 39(5) [NC RfG]. | no text proposal. | Why is the time period for frequency of testing in the NC; should be decided on National basis - the periodicity is to be agreed (not imposed) in Art 40.2. |  |  | Technical
0005-e495-5e7a-d54d-2101 | V1.0 for Public consultation version | 6 | 41 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each Power Generating Module with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at least every three years, following the methodology described in Article 39(5) [NC RfG]. | Each Power Generating Module contracted for Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at an interval to be defined in the contract between three and five years, following the methodology described in Article 39(5) [NC RfG]. | Only PGMs contracted for Blackstart capability should be tested. The interval should be no less than 3 years and no greater than 5 years, and shall be covered under the contract.
0005-e495-5e7a-d54d-1913 | V1.0 for Public consultation version | 6 | 41 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each Power Generating Module with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, | Each Power Generating Module with WHICH HAS CONTRACTED WITH THE RELEVANT NETWORK OPERATOR TO PROVIDE Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, | As written currently this is in direct contravention of the RfG which states that providing black start is not mandatory.
0005-bd85-5f5e-e292-d323 | V1.0 for Public consultation version | 6 | 41 | 2 | - | 2014-12-08 16:39:20 | Markus Hemmer | EnBW | final | Each Significant Grid User which is a Type C and D Power Generating Module and which is identified in a Restoration Plan [...] | delete | The proper functioning is assessed in comissioning test. The test period of this service is agreed in a contract if the TSOs decides to buy this capabillity. As long as there are no technical constraints the proper functioning is granted. Else this would lead to extremes cossts for Grid Users and an extreme loss of EOH for their equipment. |  |  | technical |  |  |  | Non-confidential
0005-9675-c447-a04c-761e | V1.0 for Public consultation version | 6 | 41 | 2 | - | 2014-12-07 12:51:43 | Herve MELJAC | EUR | final | Each Significant Grid User which is a Type C and D Power Generating Module and which is identified in a Restoration Plan shall perform tripping to houseload test after any modernisation of the equipment having an impact on its Houseload Operation capability, or after two unsuccessful consecutive tripping in real operation, following the methodology described in Article 39(6) [NC RfG]. | Each Significant Grid User which is a Type C and D Power Generating Module and which is identified in a Restoration Plan shall perform tripping to houseload test after any modernisation of the equipment having an impact on its Houseload Operation capability, or after two unsuccessful consecutive tripping in real operation, following the methodology described in Article 39(6) [NC RfG], in coordination with the relevant TSO. | In certain cases, voluntarily switching to house-load of a SGU means voluntarily having the system suffer its reference incident, hence creating a large frequency disturbance. Hence agreement has to be found to conduct such a test. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-1915 | V1.0 for Public consultation version | 6 | 41 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each Significant Grid User which is a Type C and D Power Generating Module and which is identified ….. | Each Significant Grid User which is a NEW Type C and D Power Generating Module and which is identified ….. | As written currently this is in direct contravention of the RfG. The obligation in the RfG only applies to new generators or those for whom a CBA has been undertaken (and found to be in favour of the generator providing that capability as the least cost provider).
0005-e495-5e7a-d54d-1917 | V1.0 for Public consultation version | 6 | 41 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each Significant Grid User which is a Type C and D Power Generating Module and which is identified in a Restoration Plan shall perform | Each Significant Grid User which is a Type C and D Power Generating Module and which is identified in a Restoration Plan AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR shall perform | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-2225 | V1.0 for Public consultation version | 6 | 41 | 6 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Add new Article | Market participants shall be given notice of these periodic assessments. Practical limitations such as times to carry out testing and the physical capability of the plant shall be considered. | Market participants must be given reasonable notice of these periodic assessments and account should be taken of practical times to carry out testing including the physical capability of the plant and the costs. |  |  | Technical | Fundamental
0005-487d-103c-d54d-64ff | V1.0 for Public consultation version | 6 | 41 | - | - | 2014-12-08 23:56:25 | Gunnar Kaestle | Clausthal University of Technology | final | General Principles for testing: reproducible results and specific test conditions | No item for the NC ER, but for the experts from the drafting team: As the NC ER as well as the NC DCC gives only a general framework on compliance testing, ENTSO-E experts should contribute to amendments of IEC and CENELEC standards which cover (frequency) relays and describe elaborately tests for conformance assessment. | In order to present reproducible test procedures for compliance assessment, additional technical documents are needed. |  |  | technical |  |  |  | Non-confidential
0005-96c5-d35f-3030-ad6b | V1.0 for Public consultation version | 6 | 41 | - | - | 2014-12-08 18:18:38 | Thomas Willson |  | final | General Principles for testing: reproducible results and specific test conditions | No item for the NC ER, but for the experts from the drafting team: As the NC ER as well as the NC DCC gives only a general framework on compliance testing, ENTSO-E experts should contribute to amendments of IEC and CENELEC standards which cover (frequency) relays and describe elaborately tests for conformance assessment. | In order to present reproducible test procedures for compliance assessment, additional technical documents are needed. |  |  | technical |  |  |  | Non-confidential
0005-e4a9-866e-e2f6-55a9 | V1.0 for Public consultation version | 6 | 42 | 1 | - | 2014-12-08 16:39:20 | Markus Hemmer | EnBW | final | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan and/or Restoration Plan […] | delete | The proper functioning is assessed in comissioning test. As long as there are no technical constraints the proper functioning is granted. Else this would lead to extremes cossts for Grid Users and an extreme loss of EOH for their equipment. |  |  | technical |  |  |  | Non-confidential
0005-e4e5-853f-c79f-d28b | V1.0 for Public consultation version | 6 | 42 | 1 | - | 2014-12-08 19:51:16 | Roland Tual | SEDC | final | Each Demand Facility providing Demand Side Response, which is identified in System Defense Plan and/or Restoration Plan shall perform demand modification test, at least every year, following the methodology described in Article 44(1) [NC DC]. Each Demand Facility providing Demand Side Response, which is identified in System Defense Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. | [8 empty] | confidential
0005-6f65-120a-1335-8f61 | V1.0 for Public consultation version | 6 | 42 | 1 | - | 2014-12-03 11:11:00 | AXPO Group |  | final | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan and/or Restoration Plan shall perform demand modification test, at least every year, following the methodology described in Article 44(1) [NC DC]. | see Comment | If private households provide DSR, the testing will be impossible. The test interval (here 1 year) shall not be defined by the network code but on national level. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2348 | V1.0 for Public consultation version | 6 | 42 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan and/or Restoration Plan shall perform demand modification test, at least every year, following the methodology described in Article 44(1) [NC DC]. | no text proposal. | Why is the time period for frequency of testing in the NC; should be decided on National basis - the periodicity is to be agreed (not imposed) in Art 40.2. |  |  | Technical
0005-e495-5e7a-d54d-2226 | V1.0 for Public consultation version | 6 | 42 | 1 |  | 2014-12-08 21:33 | Eberhard | EnBW | final | Each Power Generating Module with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at least every three years, following the methodology described in Article 39(5) [NC RfG]. | Each Power Generating Module contracted for Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at an interval to be defined in the contract between three and five years, following the methodology described in Article 39(5) [NC RfG]. | Only PGMs contracted for Blackstart capability should be tested. The interval should be no less than 3 years and no greater than 5 years, and shall be covered under the contract. As currently drafted this provision contains a clear contradition with the NC RfG which states that providing Black Start capability is not madatory. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1919 | V1.0 for Public consultation version | 6 | 42 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan and/or Restoration Plan shall perform | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan and/or Restoration Plan AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR shall perform | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-6fb5-374c-d3bd-383c | V1.0 for Public consultation version | 6 | 42 | 2 | - | 2014-12-08 23:56:25 | Gunnar Kaestle | Clausthal University of Technology | final | Low Frequency Demand Disconnection test in 42(2) vs Low Frequency Demand Disconnection *relay* test in 44 | align Art 42 with Art 44 | It seems that the same test (every 5 years) is meant, refering to DCC 20(1)+(2) |  |  | technical |  |  |  | Non-confidential
0005-bdc1-4eaf-29ed-30f5 | V1.0 for Public consultation version | 6 | 42 | 2 | - | 2014-12-08 16:38:50 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. After any modernisation of the equipment having an impact on its Demand Side Response capability, or after two unsuccessful Responses in real operation, the test shall be done again. | Bring it in line with Article 41.2. | [6 empty] | Non-confidential
0005-bdc1-8540-0d7b-fb77 | V1.0 for Public consultation version | 6 | 42 | 2 | - | 2014-12-08 17:09:38 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. After any modernisation of the equipment having an impact on its Demand Side Response capability, or after two unsuccessful Responses in real operation, the test shall be done again. | Bring it in line with Article 41.2. |  |  | legal |  |  |  | Non-confidential
0005-4855-86aa-e616-fae3 | V1.0 for Public consultation version | 6 | 42 | 2 | - | 2014-12-08 16:39:20 | Markus Hemmer | EnBW | final | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, [...] | delete | The proper functioning is assessed in comissioning test. As long as there are no technical constraints the proper functioning is granted. Else this would lead to extremes cossts for Grid Users and an extreme loss of EOH for their equipment. |  |  | technical |  |  |  | Non-confidential
0005-6f8e-b45e-e961-cf4f | V1.0 for Public consultation version | 6 | 42 | 2 | - | 2014-11-28 15:52:06 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. After any modernisation of the equipment having an impact on its Demand Side Response capability, or after two unsuccessful Responses in real operation, the test shall be done again. | Bring it in line with Article 41.2. |  |  | legal |  |  |  | Non-confidential
0005-4869-5025-245e-53af | V1.0 for Public consultation version | 6 | 42 | 2 | - | 2014-12-08 17:01:18 | Jasmina PIERRE | EdF | final | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. After any modernisation of the equipment having an impact on its Demand Side Response capability, or after two unsuccessful responses in real operation, the test shall be done again. | Need for precision regarding Demand Facility providing Demand Side Response. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2349 | V1.0 for Public consultation version | 6 | 42 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. | no text proposal. | Why is the time period for frequency of testing in the NC; should be decided on National basis - the periodicity is to be agreed (not imposed) in Art 40.2.
0005-e495-5e7a-d54d-2102 | V1.0 for Public consultation version | 6 | 42 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. After any modernisation of the equipment having an impact on its Demand Side Response capability, or after two unsuccessful Responses in real operation, the test shall be done again. | Bring it in line with Article 41.2.
0005-e495-5e7a-d54d-2227 | V1.0 for Public consultation version | 6 | 42 | 2 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each Significant Grid User which is a Type C and D Power Generating Module and which is identified (…) | Each Significant Grid User which is a new Type C and Type D Power Generating Module. | As currently drafted this provisions contains a clear contradiction with the NC RfG. NC RfG applies solely to new generators or, exceptionnaly, to the existing ones provided that a CBA has been undertaken and found to be in favor of the generator providing that capability as the least cost provider. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-2228 | V1.0 for Public consultation version | 6 | 42 | 2 |  | 2014-12-08 21:33 | AG | RWE | final | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. | To be deleted- see the justification. | How can all the households (or any other demand sites) who provide demand side response actually test their response to low frequency? |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1921 | V1.0 for Public consultation version | 6 | 42 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR, shall perform | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-1923 | V1.0 for Public consultation version | 6 | 42 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each Demand Facility providing Demand Side Response, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection test at least every five years, | Xyz | How, practically, can all the domestic homes (or indeed any other demand site) who provide demand side response ACTUALLY test their response to low frequency?! Have the ramifications of this for TSO, DSOs and end consumers across the 28 Member States been considered?!
0005-2159-3731-4ddb-76b4 | V1.0 for Public consultation version | 6 | 42 | - | - | 2014-12-08 20:11:09 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | The tests will consist in annual testing and disconnection every 5 years. Again the consumer's safety is an issue here. It is unclear how this will be paid for or what rights the customer will have under this plan - or how to mitigate the danger most consumers may face if their systems are turned off. Consumer rights and needs are ignored and no provisions for their safety or wellbeing are developed. This provision is unacceptable without any proper structure in place to ensure consumer protection. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2266 | V1.0 for Public consultation version | 6 | 42 | 1,2 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | Each Demand Facility providing Demand Side Response, which is identified in System Defense Plan and/or Restoration Plan shall perform demand modification test, at least every year, following the methodology described in Article 44(1) [NC DC]. Each Demand Facility providing Demand Side Response, which is identified in System Defense Plan, shall perform Low Frequency Demand Disconnection test at least every five years, following the methodology described in Article 43(1)(d) [NC DC]. |  | The tests will be annual testing and disconnection every 5 years. The customer's safety is an issue here. It is unclear how this will be paid for or what rights the customer will have under this plan. Particularly as national governments will not be consulted and NRAs will only be informed (If small consumers are not under consideration for this measure - why are they included?)
0005-2159-868c-e486-fc30 | V1.0 for Public consultation version | 6 | 43 | 1 | - | 2014-12-08 16:39:21 | Markus Hemmer | EnBW | final | Each HVDC System with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at least every three years, following the methodology described in Article 67(11) [NC HVDC] | delete | The proper functioning is assessed in comissioning test. The test period of this service is agreed in a contract if the TSOs decides to buy this capabillity. As long as there are no technical constraints the proper functioning is granted. Else this would lead to extremes cossts for Grid Users and an extreme loss of EOH for their equipment. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2350 | V1.0 for Public consultation version | 6 | 43 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each HVDC System with Black Start capability, which is identified in a Restoration Plan, shall perform Black Start Capability test, at least every three years, following the methodology described in Article 67(11) [NC HVDC]. | no text proposal. | Why is the time period for frequency of testing in the NC; should be decided on National basis - the periodicity is to be agreed (not imposed) in Art 40.2. |  |  | Technical
0005-e495-5e7a-d54d-2103 | V1.0 for Public consultation version | 6 | 43 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Add new Article | Each HVDC which is contracted for Black Start shall perform the Black Start test after any modernisation of the equipment having an impact on its Black Start capability following the methodology described in NC HVDC. | Bring it in line with Article 41.2.
0005-e4a9-7735-2332-5983 | V1.0 for Public consultation version | 6 | 43 | - | - | 2014-12-08 17:01:18 | Jasmina PIERRE | EdF | final | (new) | Each HVDC system which is contracted for Black Start shall perform the Black Start test after any modernisation of the equipment having an impact on its Black Start capability following the methodology described in NC HVDC. | Need for precision regarding HVDC systems. |  |  | technical |  |  |  | Non-confidential
0005-2195-75bf-2795-76f1 | V1.0 for Public consultation version | 6 | 43 | - | - | 2014-12-08 16:38:52 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Add new Article | Each HVDC which is contracted for Black Start shall perform the Black Start test after any modernisation of the equipment having an impact on its Black Start capability following the methodology described in NC HVDC. | Bring it in line with Article 41.2. | [6 empty] | Non-confidential
0005-2145-c3c0-0cb3-283d | V1.0 for Public consultation version | 6 | 43 | - | - | 2014-12-08 17:15:44 | Paul Doyle | ESB Generation & Wholesale Markets | final | Add new Article | Each HVDC which is contracted for Black Start shall perform the Black Start test after any modernisation of the equipment having an impact on its Black Start capability following the methodology described in NC HVDC. | Bring it in line with Article 41.2. |  |  | legal |  |  |  | Non-confidential
0005-bd9a-a482-e8fd-c7e0 | V1.0 for Public consultation version | 6 | 43 | - | - | 2014-11-28 15:52:10 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Add new Article | Each HVDC which is contracted for Black Start shall perform the Black Start test after any modernisation of the equipment having an impact on its Black Start capability following the methodology described in NC HVDC. | Bring it in line with Article 41.2. |  |  | legal |  |  |  | Non-confidential
0005-6fa1-76fc-3d88-6812 | V1.0 for Public consultation version | 6 | 44 | 1 | - | 2014-12-05 11:05:43 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | Each Distribution System Operator, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection relays testing, at least every five years, following the methodology described in Article 41(1)(e) [NC DC]. | Each Distribution System Operator, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection relays testing, at least every five years, following the methodology described in Article 41(1)(e) [NC DC].The test procedures shall not or minimally impact customers, and be defined in detail on national level. | The test procedures must not have impact on customers, and be defined in detail on national level. | 1 | 3 | legal |  |  |  | Non-confidential
0005-4855-855f-29ed-34b1 | V1.0 for Public consultation version | 6 | 44 | 1 | - | 2014-12-08 16:38:54 | RENAUD Charlotte | Eurelectric WG Thermal / VGB Powertech | final | Each Distribution System Operator, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection relays testing, at least every five years, following the methodology described in Article 41(1)(e) [NC DC]. | Each TSO and each Distribution System Operator, which is identified in a System Defence Plan, shall perform testing, maintenance and replacement of his Low Frequency Demand Disconnection Relays and systems to maintain the probability of failure on demand below one failure per 1000 demands. It is the own responsibility of the TSO and DSO to comply. However, testing of the complete loops shall be performed at least every three years following the methodology described in Article 41(1)(e) [NC DC]. | Due to historical development, several hundreds of LFDD-relays are installed and in operation at distribution networks all over Europe. These relays use different technologies (mechanical, analogue, digital). They are in operation since different time periods so far and provide different expectancy of life time. The broad variety of relays requires different testing periods and maintenance procedures. Defining a common inspection period for many different types and models of relays will rise costs without providing any proven benefit. The proposed one-size-fits-all approach by ENTSO-E therefore doesn’t reflect the current situation and misses the socio-economic optimum. A graded, matched concept of testing and maintenance, which guarantees a specified minimum availability fits much better and must not be prohibited by the network code. Also TSO relays must be tested. The testing frequency of these important low frequency protection relays, which are the last possibility to prevent a global Black Out, must be sufficient to maintain SIL level 3 (IEC 61508) for the complete underfrequency protection circuit. | [6 empty] | Non-confidential
0005-e4a9-5e30-0beb-be76 | V1.0 for Public consultation version | 6 | 44 | 1 | - | 2014-12-08 17:15:45 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each Distribution System Operator, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection relays testing, at least every five years, following the methodology described in Article 41(1)(e) [NC DC]. | Each TSO and each Distribution System Operator, which is identified in a System Defence Plan, shall perform testing, maintenance and replacement of his Low Frequency Demand Disconnection Relays and systems to maintain the probability of failure on demand below one failure per 1000 demands. It is the own responsibility of the TSO and DSO to comply. However, testing of the complete loops shall be performed at least every three years following the methodology described in Article 41(1)(e) [NC DC]. | Due to historical development, several hundreds of LFDD-relays are installed and in operation at distribution networks all over Europe. These relays use different technologies (mechanical, analogue, digital). They are in operation since different time periods so far and provide different expectancy of life time. The broad variety of relays requires different testing periods and maintenance procedures. Defining a common inspection period for many different types and models of relays will rise costs without providing any proven benefit. The proposed one-size-fits-all approach by ENTSO-E therefore doesn’t reflect the current situation and misses the socio-economic optimum. A graded, matched concept of testing and maintenance, which guarantees a specified minimum availability fits much better and must not be prohibited by the network code. Also TSO relays must be tested. The testing frequency of these important low frequency protection relays, which are the last possibility to prevent a global Black Out, must be sufficient to maintain SIL level 3 (IEC 61508) for the complete underfrequency protection circuit. |  |  | technical |  |  |  | Non-confidential
0005-6f66-a4be-e961-19c4 | V1.0 for Public consultation version | 6 | 44 | 1 | - | 2014-11-28 15:52:11 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each Distribution System Operator, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection relays testing, at least every five years, following the methodology described in Article 41(1)(e) [NC DC]. | Each TSO and each Distribution System Operator, which is identified in a System Defence Plan, shall perform testing, maintenance and replacement of his Low Frequency Demand Disconnection Relays and systems to maintain the probability of failure on demand below one failure per 1000 demands. It is the own responsibility of the TSO and DSO to comply. However, testing of the complete loops shall be performed at least every three years following the methodology described in Article 41(1)(e) [NC DC]. | Due to historical development, several hundreds of LFDD-relays are installed and in operation at distribution networks all over Europe. These relays use different technologies (mechanical, analogue, digital). They are in operation since different time periods so far and provide different expectancy of life time. The broad variety of relays requires different testing periods and maintenance procedures. Defining a common inspection period for many different types and models of relays will rise costs without providing any proven benefit. The proposed one-size-fits-all approach by ENTSO-E therefore doesn’t reflect the current situation and misses the socio-economic optimum. A graded, matched concept of testing and maintenance, which guarantees a specified minimum availability fits much better and must not be prohibited by the network code. Also TSO relays must be tested. The testing frequency of these important low frequency protection relays, which are the last possibility to prevent a global Black Out, must be sufficient to maintain SIL level 3 (IEC 61508) for the complete underfrequency protection circuit. |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2351 | V1.0 for Public consultation version | 6 | 44 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each Distribution System Operator, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection relays testing, at least every five years, following the methodology described in Article 41(1)(e) [NC DC]. | Each Distribution System Operator, which is identified in System Defence Plan, shall perform testing, maintenance and replacement of Low Frequency Demand Disconnection relays on its own responsibility, at least every five years,. Testing shall be performed following the methodology described in Article 41(1)(e) [NC DC]. | DSOs are convinced there is no need to change current practice and define a common inspection period for many different types and models of relays. This approach will only rise increase costs without providing any proven benefit. Why impose compliance testing of DSO relays every 5 years, knowing that: * Different technologies for the relays are used and they require different testing periods; * All relays are essential for safety and therefore engineered, commissioned and maintained to a high standard; * Network operators have sophisticated management regimes for protection systems and the associated relays and management/maintenance regimes are based on years of experience and learning; * Network operators are liable (with criminal sanctions for failure of safety systems) for the safe and reliable operation of protection systems, usually to health and safety regulators; * Black-outs in recent years (e.g. Nov. 2006 in mainland Europe and May 2008 in GB) have shown reliable operation of LFDD-relays at DSO’s premises. Will a fixed arbitrary interval improve or even guarantee relialibility? * Can ENTSO-E provide a proper justification? * Can ENTSO-E present the evidence it has for asserting that 5 years is the optimum in all cases? * Will ENTSO-E provide a CBA? … the supporting document does not give any indication on this. |  |  | Technical
0005-e495-5e7a-d54d-2104 | V1.0 for Public consultation version | 6 | 44 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each Distribution System Operator, which is identified in System Defence Plan, shall perform Low Frequency Demand Disconnection relays testing, at least every five years, following the methodology described in Article 41(1)(e) [NC DC]. | Each TSO and each Distribution System Operator, which is identified in a System Defence Plan, shall perform testing, maintenance and replacement of his Low Frequency Demand Disconnection Relays and systems to maintain the probability of failure on demand below one failure per 1000 demands. It is the own responsibility of the TSO and DSO to comply. However, testing of the complete loops shall be performed at least every three years following the methodology described in Article 41(1)(e) [NC DC]. | Due to historical development, several hundreds of LFDD-relays are installed and in operation at distribution networks all over Europe. These relays use different technologies (mechanical, analogue, digital). They are in operation since different time periods so far and provide different expectancy of life time. The broad variety of relays requires different testing periods and maintenance procedures. Defining a common inspection period for many different types and models of relays will rise costs without providing any proven benefit. The proposed one-size-fits-all approach by ENTSO-E therefore doesn’t reflect the current situation and misses the socio-economic optimum. A graded, matched concept of testing and maintenance, which guarantees a specified minimum availability fits much better and must not be prohibited by the network code. Also TSO relays must be tested. The testing frequency of these important low frequency protection relays, which are the last possibility to prevent a global Black Out, must be sufficient to maintain SIL level 3 (IEC 61508) for the complete underfrequency protection circuit.
0005-bdd6-2f70-e9c5-1040 | V1.0 for Public consultation version | 6 | 44 | - | - | 2014-11-28 15:52:12 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Compliance testing of DSO relays | Compliance testing of TSO and DSO relays | Relays in TSO installations must also be tested! |  |  | legal |  |  |  | Non-confidential
0005-969d-857c-0f0b-c8c2 | V1.0 for Public consultation version | 6 | 44 | - | - | 2014-12-08 17:15:46 | Paul Doyle | ESB Generation & Wholesale Markets | final | Compliance testing of DSO relays | Compliance testing of TSO and DSO relays | Relays in TSO installations must also be tested! |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2105 | V1.0 for Public consultation version | 6 | 44 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Compliance testing of DSO relays | Compliance testing of TSO and DSO relays | Relays in TSO installations must also be tested!
0005-bdad-8710-a3c1-46b9 | V1.0 for Public consultation version | 6 | 45 | 1 | - | 2014-12-04 14:02:19 | Dekinderen Eric | Genrator company | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their communication channels, defined in Article 38, at least every year | "Backup" is not defined and not mentioned in Art. 38 |  |  | technical |  |  |  | Non-confidential
0005-bd85-388a-e2f6-cb38 | V1.0 for Public consultation version | 6 | 45 | 1 | - | 2014-12-08 16:39:21 | Markus Hemmer | EnBW | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year. | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at regular intervals. | A test every year iss not reasonable. The test period should rather be ajar of manufacturer suggestions or the experience of the operator. This is also in line to many other test cycles in european legislation (e.g. in Germany test cycles of risk assesment). |  |  | technical |  |  |  | Non-confidential
0005-9676-7d90-e7d1-3f6b | V1.0 for Public consultation version | 6 | 45 | 1 | - | 2014-11-28 15:52:13 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year. |  | Why is the time period for frequency of testing in the NC; should be decided on National basis. |  |  | technical |  |  |  | Non-confidential
0005-e4a9-d360-0ea7-daf2 | V1.0 for Public consultation version | 6 | 45 | 1 | - | 2014-12-08 17:15:48 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year. |  | Why is the time period for frequency of testing in the NC; should be decided on National basis. |  |  | technical |  |  |  | Non-confidential
0005-4891-0288-10dd-17d9 | V1.0 for Public consultation version | 6 | 45 | 1 | - | 2014-12-03 11:11:00 | AXPO Group |  | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year. | see Comment | The test interval (here 1 year) shall not be defined by the network code but on national level. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2352 | V1.0 for Public consultation version | 6 | 45 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year. | no text proposal (yet). | Why is the time period for frequency of testing in the NC; should be decided on National basis. |  |  | Technical
0005-e495-5e7a-d54d-2229 | V1.0 for Public consultation version | 6 | 45 | 1 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year. | Each TSO and DSO identified in System defence Plan or Restoration Plan (…) | As already noted (see comment on Article 38(1), it is impractical and unreasonable to expect domestic or even small and medium generators to have a redundant voice communication channel and that it has at least 24 hours backup. These users rely solely on public voice communication channels (landlines and mobiles). |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1925 | V1.0 for Public consultation version | 6 | 45 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year. | Each TSO, AND DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year. | As noted under Art 38 (1) above, given the SGU definition it is impractical to expect domestic, or even SMEs to have a redundant voice communication channel and that it have at least 24 hours backup. These users rely on public voice communication channels such as landlines and mobile network. It is wholly unreasonable, and impractical to oblige SGUs in this way.
0005-e495-5e7a-d54d-1927 | V1.0 for Public consultation version | 6 | 45 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR shall test their backup communication channels, | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-1929 | V1.0 for Public consultation version | 6 | 45 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Where these tools and facilities involve DSOs or Significant Grid Users, these parties shall participate in this test. | Where these tools and facilities involve DSOs or Significant Grid Users PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR, these parties shall participate in this test. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-bdc2-7d90-ea29-534d | V1.0 for Public consultation version | 6 | 45 | - | - | 2014-11-28 15:52:14 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year. | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at regular intervals. | A test every year is not reasonable. The test period should rather be ajar of manufacturer suggestions or the experience of the operator. This is also in line with many other test cycles in European legislation (e.g. in Germany test cycles of risk assesment). | [6 empty] | Non-confidential
0005-487d-4eae-0cb3-bf94 | V1.0 for Public consultation version | 6 | 45 | - | - | 2014-12-08 17:15:50 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year. | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at regular intervals. | A test every year is not reasonable. The test period should rather be ajar of manufacturer suggestions or the experience of the operator. This is also in line with many other test cycles in European legislation (e.g. in Germany test cycles of risk assesment). | [6 empty] | Non-confidential
0005-bd99-75ed-4d77-1d3f | V1.0 for Public consultation version | 6 | 45 | - | - | 2014-12-08 20:11:10 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | Households could be forced to undergo annual testing procedures. This procedure will be repeated until they succeed in fulfilling the requirements. Again the cost impact and the inconvenience of this system to consumers is not considered at all. Consumer rights to privacy, safety related issues and social welfare are not mentioned either. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2106 | V1.0 for Public consultation version | 6 | 45 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at least every year. | Each TSO, DSO and Significant Grid User identified in System Defence Plan or Restoration Plan shall test their backup communication channels, defined in Article 38, at regular intervals. | A test every year is not reasonable. The test period should rather be ajar of manufacturer suggestions or the experience of the operator. This is also in line with many other test cycles in European legislation (e.g. in Germany test cycles of risk assesment).
0005-e495-5e7a-d54d-1931 | V1.0 for Public consultation version | 6 | 46 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall test the capability of backup power sources to supply essential services of the substations identified in Restoration Plan, in accordance with Article 39, at least every four years. | Each TSO shall test the capability of backup power sources to supply essential services of the ITS substations identified in Restoration Plan, in accordance with Article 39, at least every four years. | As noted under Art 39 (5) above, this should refer to the TSO substations.
0005-e495-5e7a-d54d-2107 | V1.0 for Public consultation version | 6 | 46 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Add new Article | Each TSO and DSO shall perform functional tests of his grid protection relays at least every three years. After any modernisation of (a part of) the protection equipment and after any malfunction in real operation, the functional tests shall be performed again. | To prevent the system ending in emergency or black out situations, also standard grid protection relays must periodically be tested. The risk is the frequency of occurence multiplied by the probability that the relay fails. As the frequency of occurence is much more than it is in the case of underfrequency relays, they must also be frequently tested.
0005-6f8d-ac6e-0beb-2f19 | V1.0 for Public consultation version | 6 | 46 | - | - | 2014-12-08 17:15:53 | Paul Doyle | ESB Generation & Wholesale Markets | final | Testing of TSO facilities | Compliance testing of TSO facilities | Editorial. |  |  | legal |  |  |  | Non-confidential
0005-216e-db32-e899-735d | V1.0 for Public consultation version | 6 | 46 | - | - | 2014-11-28 15:52:15 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Add new Article | Each TSO and DSO shall perform functional tests of his grid protection relays at least every three years. After any modernisation of (a part of) the protection equipment and after any malfunction in real operation, the functional tests shall be performed again. | To prevent the system ending in emergency or black out situations, also standard grid protection relays must periodically be tested. The risk is the frequency of occurence multiplied by the probability that the relay fails. As the frequency of occurence is much more than it is in the case of underfrequency relays, they must also be frequently tested! |  |  | legal |  |  |  | Non-confidential
0005-e4aa-7d90-ea29-3b03 | V1.0 for Public consultation version | 6 | 46 | - | - | 2014-11-28 15:52:15 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Testing of TSO facilities | Compliance testing of TSO facilities | Editorial. |  |  | legal |  |  |  | Non-confidential
0005-bd85-4e90-0d17-98df | V1.0 for Public consultation version | 6 | 46 | - | - | 2014-12-08 17:15:52 | Paul Doyle | ESB Generation & Wholesale Markets | final | Add new Article | Each TSO and DSO shall perform functional tests of his grid protection relays at least every three years. After any modernisation of (a part of) the protection equipment and after any malfunction in real operation, the functional tests shall be performed again. | To prevent the system ending in emergency or black out situations, also standard grid protection relays must periodically be tested. The risk is the frequency of occurence multiplied by the probability that the relay fails. As the frequency of occurence is much more than it is in the case of underfrequency relays, they must also be frequently tested! |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2108 | V1.0 for Public consultation version | 6 | 46 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Testing of TSO facilities | Compliance testing of TSO facilities | Editorial.
0005-2181-d37e-0c4f-daed | V1.0 for Public consultation version | 6 | 47 | 1 | - | 2014-12-08 17:15:55 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall monitor the proper implementation of the Low Frequency Demand Disconnection on the basis of the yearly written notification on Low Frequency Demand Disconnection provided by the DSO pursuant to Article 20(1) [NC DC] and by the Demand Facility Owner pursuant to Article 22(1)(o) [NC DC]. | Each TSO shall monitor the proper implementation of the complete Low Frequency Demand Disconnection on the basis of the yearly written notification on Low Frequency Demand Disconnection provided by the DSO pursuant to Article 20(1) [NC DC] and by the Demand Facility Owner pursuant to Article 22(1)(o) [NC DC] and the Low Frequency Demand Disconnection in it's own grid. | Also the part in the TSO liability part must be monitored. |  |  | legal |  |  |  | Non-confidential
0005-96b2-3ef2-e8fd-39d6 | V1.0 for Public consultation version | 6 | 47 | 1 | - | 2014-11-28 15:52:16 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall monitor the proper implementation of the Low Frequency Demand Disconnection on the basis of the yearly written notification on Low Frequency Demand Disconnection provided by the DSO pursuant to Article 20(1) [NC DC] and by the Demand Facility Owner pursuant to Article 22(1)(o) [NC DC]. | Each TSO shall monitor the proper implementation of the complete Low Frequency Demand Disconnection on the basis of the yearly written notification on Low Frequency Demand Disconnection provided by the DSO pursuant to Article 20(1) [NC DC] and by the Demand Facility Owner pursuant to Article 22(1)(o) [NC DC] and the Low Frequency Demand Disconnection in it's own grid. | Also the part in the TSO liability part must be monitored. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2109 | V1.0 for Public consultation version | 6 | 47 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall monitor the proper implementation of the Low Frequency Demand Disconnection on the basis of the yearly written notification on Low Frequency Demand Disconnection provided by the DSO pursuant to Article 20(1) [NC DC] and by the Demand Facility Owner pursuant to Article 22(1)(o) [NC DC]. | Each TSO shall monitor the proper implementation of the complete Low Frequency Demand Disconnection on the basis of the yearly written notification on Low Frequency Demand Disconnection provided by the DSO pursuant to Article 20(1) [NC DC] and by the Demand Facility Owner pursuant to Article 22(1)(o) [NC DC] and the Low Frequency Demand Disconnection in it's own grid. | Also the part in the TSO liability part must be monitored.
0005-e495-5e7a-d54d-2230 | V1.0 for Public consultation version | 6 | 47 | 1 |  | 2014-12-08 21:33 | AG | RWE | final | Each TSO shall monitor the proper implementation of the Low Frequency Demand Disconnection on the basis of the yearly written notification on Low Frequency Demand Disconnection provided by the DSO pursuant to Article 20(1) [NC DC] and by the Demand Facility Owner pursuant to Article 22(1)(o) [NC DC]. | See the justification. | This is impractical- TSOs will be receiving millions of written submissions to be taken into account. |  |  | Technical | Fundamental
0005-e495-5e7a-d54d-1933 | V1.0 for Public consultation version | 6 | 47 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | ….on the basis of the yearly written notification on Low Frequency Demand Disconnection provided by ….. the Demand Facility Owner pursuant to Article 22(1)(o) [NC DC]. | Xyz | Has the practicality of the TSO receiving tens of millions of written submissions each year being taken into account(!). Furthermore, once the TSO has this information it has a duty, in common law, to act upon any health and safety information. Failure to do so could open the TSO itself to criminal negligence charges as well as making the TSO itself liable for non criminal compensation if it fails to act on the information it has received. Be careful what you ask for(!).
0005-bd99-75a0-0f6f-3f91 | V1.0 for Public consultation version | 6 | 47 | 2 | - | 2014-12-08 17:15:57 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall review, at least every 5 years, its System Defence Plan to assess its effectiveness. The TSO shall in this review take into account at least: | To assess its effectiveness, each TSO shall review its System Defence Plan at least every year and before implementation of any modernisation of equipment or grid structure having impact on the System Defence. The TSO shall in this review take into account at least: | As the DSO and the owners of significant demand facilities have to write notifications on the implementation every year, the restoration plan shall be reviewed on yearly basis, too. Otherwise, the requirement for yearly notifications is useless and discriminates grid users. It cannot be true that the TSO can change his grid structure or equipment and wait years before reviewing the System Defence Plan! |  |  | legal |  |  |  | Non-confidential
0005-bd9a-7dae-ea29-85f5 | V1.0 for Public consultation version | 6 | 47 | 2 | - | 2014-11-28 15:52:17 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall review, at least every 5 years, its System Defence Plan to assess its effectiveness. The TSO shall in this review take into account at least: | To assess its effectiveness, each TSO shall review its System Defence Plan at least every year and before implementation of any modernisation of equipment or grid structure having impact on the System Defence. The TSO shall in this review take into account at least: | As the DSO and the owners of significant demand facilities have to write notifications on the implementation every year, the restoration plan shall be reviewed on yearly basis, too. Otherwise, the requirement for yearly notifications is useless and discriminates grid users. It cannot be true that the TSO can change his grid structure or equipment and wait years before reviewing the System Defence Plan! |  |  | legal |  |  |  | Non-confidential
0005-e4e5-6066-12d1-9131 | V1.0 for Public consultation version | 6 | 47 | 2 | - | 2014-12-03 11:11:01 | AXPO Group |  | final | Each TSO shall review, at least every 5 years, its System Defence Plan to assess its effectiveness. | see Comment | Next to the 5 year interval, a review of the Defence Plan is also necessary after major grid modifications. Like new or removed grid lines, power stations etc. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2353 | V1.0 for Public consultation version | 6 | 47 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Each TSO shall review, at least every 5 years, its System Defence Plan to assess its effectiveness. The TSO shall in this review take into account at least: a) development and evolutions on its Network since the last review or first design; b) capabilities of new equipment installed on the transmission and distribution systems since the last review or first design; c) Significant Grid Users commissioned since the last review or first design, their capabilities and relevant offered services; d) tests carried out and analysis of system incidents pursuant to Article 33(5) [NC OS]; and e) operational data collected during normal operation and after Disturbance. | no text proposal (yet). | Why is the time period for frequency of testing in the NC; should be decided on National basis. In this case 5 years sounds too long. |  |  | Technical
0005-e495-5e7a-d54d-2110 | V1.0 for Public consultation version | 6 | 47 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall review, at least every 5 years, its System Defence Plan to assess its effectiveness. The TSO shall in this review take into account at least: | To assess its effectiveness, each TSO shall review its System Defence Plan at least every year and before implementation of any modernisation of equipment or grid structure having impact on the System Defence. The TSO shall in this review take into account at least: | As the DSO and the owners of significant demand facilities have to write notifications on the implementation every year, the restoration plan shall be reviewed on yearly basis, too. Otherwise, the requirement for yearly notifications is useless. It does not make sense that the TSO can change his grid structure or equipment and wait years before reviewing the System Defence Plan. In case yearly review of the Defense Plan is not considered appropriate by TSOs, and the review should take place every 2 or 3 years, the notifications should also take place every 2 or 3 years (the same period of time).
0005-e495-5e7a-d54d-2231 | V1.0 for Public consultation version | 6 | 47 | 2 |  | 2014-12-08 21:33 | AG | RWE | final | Each TSO shall review, at least every 5 years, its System Defence Plan to assess its effectiveness. The TSO shall in this review take into account at least: | To assess its effectiveness, each TSO shall review its System Defence Plan at least every year and before implementation of any modernisation of equipment or grid structure having impact on the System Defence. This review shall be subject to NRA approval. The TSO shall in this review take into account at least: | As the DSO and the owners of significant demand facilities have to write notifications on the implementation every year, the restoration plan shall be reviewed on yearly basis, too. Otherwise, the requirement for yearly notifications is useless. It does not make sense that the TSO can change his grid structure or equipment and wait years before reviewing the System Defence Plan. In case yearly review of the Defense Plan is not considered appropriate by TSOs, and the review should take place every 2 or 3 years, the notifications should also take place every 2 or 3 years (the same period of time). The review of the plan must be subject to NRA approval!!! |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-1934 | V1.0 for Public consultation version | 6 | 47 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall review, at least every 5 years, its System Defence Plan to assess its effectiveness. The TSO shall in this review take into account at least: | Each TSO NRA shall review, at least every 5 years, its THE System Defence Plan to assess its effectiveness. THE TSO SHALL ASSIST THE NRA IN THIS REVIEW. The TSO NRA shall in this review take into account at least: | Asking the TSOs to review the System Defence Plan is like asking a student to set (and mark) their own exam questions(!). The incident, in November 2006, which gave rise to the need for NC E&R, arose from the actions / inactions of TSOs. Stakeholders and consumers across the 28 Member States need to have confidence in the System Defence Plan and the Restoration Plan. Relying upon the TSO to review the Plan(s) would be wrong. The TSO has a clear conflict of interest. If the NRA is unable or unwilling themselves to perform this task they can either appoint independent auditors to do it on their behalf or ask ACER to do it on behalf of the NRA.
0005-96b1-5e4e-0beb-9d9d | V1.0 for Public consultation version | 6 | 47 | 3 | - | 2014-12-08 17:15:58 | Paul Doyle | ESB Generation & Wholesale Markets | final | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 Article 21. | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 and Article 21. | Editorial. | [6 empty] | Non-confidential
0005-968a-6602-e76d-4cef | V1.0 for Public consultation version | 6 | 47 | 3 | - | 2014-11-28 15:52:34 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 Article 21. | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 and Article 21. | Editorial. | [6 empty] | Non-confidential
0005-e495-5e7a-d54d-2354 | V1.0 for Public consultation version | 6 | 47 | 3 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 Article 21. | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8(8) and Article 9. | Wrong reference. |  |  | Technical
0005-e495-5e7a-d54d-2111 | V1.0 for Public consultation version | 6 | 47 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 Article 21. | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 and Article 21. | Editorial.
0005-e495-5e7a-d54d-2112 | V1.0 for Public consultation version | 6 | 47 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 Article 21. | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 and Article 21. Any amendment will be subject to consultation. | where on review a need to amend the System Defence or Restoration Plans is determined, then any amendment must be subject to consultation – provision should be included reflecting this.
0005-e495-5e7a-d54d-2232 | V1.0 for Public consultation version | 6 | 47 | 3 |  | 2014-12-08 21:33 | AG | RWE | final | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 Article 21. | When the TSO identifies the need to adapt the System Defence Plan, it shall propose the necessary amendments. Those amendments shall be subject to NRA approval before they can be implemented in accordance with Article 8 and Article 21. Any proposal for amendment shall be subject to public consultation. | Any amendments to the plan must be subject to NRA approval and consulted with the stakeholders! |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-1936 | V1.0 for Public consultation version | 6 | 47 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 Article 21. | When, AS PART OF THE REVIEW UNDERTAKEN ACCORDING TO PARAGRAPH (1), the TSO NRA identifies the need to adapt the System Defence Plan, it shall amend its THE System Defence Plan and implement these amendments in accordance with Article 8 AND Article 21. | As noted above under Art 47 (1) the review must not be undertaken by the TSO but by the NRA (or a person appointed by the NRA or ACER).
0005-2195-008e-0cb3-8980 | V1.0 for Public consultation version | 6 | 48 | 1 | - | 2014-12-08 17:16:00 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall test parts of its Restoration Plan based on computer simulation, in coordination with DSO and Significant Grid Users identified in the Restoration plan, at least every five years. The TSO shall define these simulation tests in a dedicated testing procedure covering at least: | Each TSO shall test the critical parts of its Restoration Plan based on computer simulation, in coordination with DSO and Significant Grid Users identified in the Restoration plan, at least every five years. The TSO shall define these simulation tests in a dedicated testing procedure covering at least: | The TSO shall identify the critical aspects of the Plan and ensure testing of those parts. |  |  | legal |  |  |  | Non-confidential
0005-e4e6-cbb0-e961-6260 | V1.0 for Public consultation version | 6 | 48 | 1 | - | 2014-11-28 15:52:35 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall test parts of its Restoration Plan based on computer simulation, in coordination with DSO and Significant Grid Users identified in the Restoration plan, at least every five years. The TSO shall define these simulation tests in a dedicated testing procedure covering at least: | Each TSO shall test the critical parts of its Restoration Plan based on computer simulation, in coordination with DSO and Significant Grid Users identified in the Restoration plan, at least every five years. The TSO shall define these simulation tests in a dedicated testing procedure covering at least: | The TSO shall identify the critical aspects of the Plan and ensure testing of those parts. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2113 | V1.0 for Public consultation version | 6 | 48 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall test parts of its Restoration Plan based on computer simulation, in coordination with DSO and Significant Grid Users identified in the Restoration plan, at least every five years. The TSO shall define these simulation tests in a dedicated testing procedure covering at least: | Each TSO shall test the critical parts of its Restoration Plan based on computer simulation, in coordination with DSO and Significant Grid Users identified in the Restoration plan, at least every five years. The TSO shall define these simulation tests in a dedicated testing procedure covering at least: | The TSO shall identify the critical aspects of the Plan and ensure testing of those parts.
0005-e495-5e7a-d54d-2233 | V1.0 for Public consultation version | 6 | 48 | 1 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | The TSO shall define these simulation tests in a dedicated testing procedure covering at least (…): | Each TSO shall define these simulation tests in a dedicated testing procedure which shall be subject to NRA approval, covering at least (…): | The Restoration Plan is a key element of the NC ER. Therefor any simulation testing must be subject to NRA approval. |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-1938 | V1.0 for Public consultation version | 6 | 48 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall test parts of its Restoration Plan based on computer simulation, in coordination with DSO and Significant Grid Users identified in the Restoration | Each TSO shall test parts of its Restoration Plan based on computer simulation, in coordination with DSO and Significant Grid Users identified AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR in the Restoration | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-1940 | V1.0 for Public consultation version | 6 | 48 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | ….with DSO and Significant Grid Users identified in the Restoration plan, at least …. | ….with DSO and Significant Grid Users identified in the Restoration pPlan, at least …. | Typo
0005-e495-5e7a-d54d-1942 | V1.0 for Public consultation version | 6 | 48 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | The TSO shall define these simulation tests in a dedicated testing procedure covering at least: | The TSO shall define these simulation tests in a dedicated testing procedure, WHICH SHALL BE SUBJECT TO NRA APPROVAL, covering at least: | The Restoration Plan is a key element of the NC E&R – therefore any simulation testing procedure MUST be subject to explicit NRA approval. If an NRA is unable / unwilling to do this then they should be able to ask ACER to do it on their behalf. It must be remembered that the event, in November 2006, that gave rise to the Network Codes being developed arose from the actions of TSOs and NOT Significant Grid Users. It would therefore be perverse to allow the TSOs alone to write their own homework question, answer it and then mark it. External oversight is vital to give confidence to all stakeholders and consumers across the 28 Member States that the Restoration Plan(s) are robust and fit for purpose.
0005-6f8d-c51c-3cc0-ed7d | V1.0 for Public consultation version | 6 | 48 | 2 | - | 2014-12-05 11:06:23 | Oesterreichs E-Wirtschaft | Oesterreichs E-Wirtschaft | final | In addition, if deemed necessary by the TSO to ensure the effectiveness of the Restoration Plan, each TSO shall perform operational testing of parts of Restoration Plan, in coordination with DSOs and Significant Grid Users identified in the Restoration plan. The TSO shall define these operational tests in a dedicated testing procedure. | In addition, if deemed necessary by the TSO to ensure the effectiveness of the Restoration Plan, each TSO shall perform operational testing of parts of Restoration Plan, in coordination with DSOs and Significant Grid Users identified in the Restoration plan. The TSO shall define in cooperation with the DSOs and Significant Grid Users these operational tests in a dedicated testing procedure. | Test procedures should be prepared together by TSO, DSO and significant grid users as ist is the case with the defence plan (article 21) . | 1 | 4 | technical |  |  |  | Non-confidential
0005-e4a9-ade5-245e-eb58 | V1.0 for Public consultation version | 6 | 48 | 2 | - | 2014-12-08 17:01:19 | Jasmina PIERRE | EdF | final | In addition, if deemed necessary by the TSO to ensure the effectiveness of the Restoration Plan, each TSO shall perform operational testing of parts of Restoration Plan, in coordination with DSOs and Significant Grid Users identified in the Restoration plan. The TSO shall define these operational tests in a dedicated testing procedure. | In addition, if deemed necessary by the TSO to ensure the effectiveness of the Restoration Plan, each TSO shall perform operational testing of parts of Restoration Plan, in coordination with DSOs and Significant Grid Users identified in the Restoration plan. The TSO shall define, in coordination with the DSO and the Significant Grid User, these operational tests in a dedicated testing procedure. | It is essential all the instructions given by the TSO for execution respect the technical constraints and minimize related impacts for grid users. ENTSO-E proposals should be reinforced and foresee a final neutral decision from relevant NRA in case no agreement is reached (reference to coordination process defined in article 5). |  |  | technical |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2234 | V1.0 for Public consultation version | 6 | 48 | 2 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | The TSO shall define these operational tests in a dedicated testing procedure covering at least (…): | Each TSO shall define these operational tests in a dedicated testing procedure which shall be subject to NRA approval, covering at least (…): | The Restoration Plan is a key element of the NC ER. Therefor any simulation testing must be subject to NRA approval. |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-1944 | V1.0 for Public consultation version | 6 | 48 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | ….each TSO shall perform operational testing of parts of Restoration Plan, in coordination with DSOs and Significant Grid Users identified in the Restoration …. | ….each TSO shall perform operational testing of parts of Restoration Plan, in coordination with DSOs and Significant Grid Users identified AS PROVIDING PROCURED SERVICES TO THE RELEVANT NETWORK OPERATOR in the Restoration …. | Given the statement in whereas (6) (b) to “…in the procurement of services necessary to allow the activation of the plan” there needs to be reference here to the measures being procured.
0005-e495-5e7a-d54d-1946 | V1.0 for Public consultation version | 6 | 48 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | …with DSOs and Significant Grid Users identified in the Restoration plan. The …. | …with DSOs and Significant Grid Users identified in the Restoration pPlan. The …. | Typo
0005-e495-5e7a-d54d-1948 | V1.0 for Public consultation version | 6 | 48 | 2 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | The TSO shall define these operational tests in a dedicated testing procedure. | The TSO shall define these operational tests in a dedicated testing procedure WHICH THE TSO WILL SUBMIT TO THE NRA FOR APPROVAL . | The Restoration Plan is a key element of the NC E&R – therefore any operational testing procedure MUST be subject to explicit NRA approval. If an NRA is unable / unwilling to do this then they should be able to ask ACER to do it on their behalf. It must be remembered that the External oversight is vital to give confidence to all stakeholders and consumers across the 28 Member States that the Restoration Plan(s) are robust and fit for purpose.
0005-48a5-d596-12d1-bd0b | V1.0 for Public consultation version | 6 | 48 | 3 | - | 2014-12-03 11:10:59 | AXPO Group |  | final | Each TSO shall review its Restoration Plan to assess its effectiveness, at least every 5 years. | see Comment | Next to the 5 year interval, a review of the Restoration Plan is also necessary after major grid modifications. Like new or removed grid lines, power stations etc. |  |  | legal |  |  |  | Non-confidential
0005-6fb5-857c-0d7b-c3af | V1.0 for Public consultation version | 6 | 48 | 3 | - | 2014-12-08 17:16:48 | Paul Doyle | ESB Generation & Wholesale Markets | final | Each TSO shall review its Restoration Plan to assess its effectiveness, at least every 5 years. | To assess its effectiveness, each TSO shall review its Restoration Plan at least every year and before implementation of any modernisation of equipment or grid structure having impact on the System Restoration. | It cannot be true that the TSO can change his grid structure or equipment and wait 5 years before reviewing the System Restoration Plan! |  |  | legal |  |  |  | Non-confidential
0005-2146-663e-e76c-dd7a | V1.0 for Public consultation version | 6 | 48 | 3 | - | 2014-11-28 15:52:36 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Each TSO shall review its Restoration Plan to assess its effectiveness, at least every 5 years. | To assess its effectiveness, each TSO shall review its Restoration Plan at least every year and before implementation of any modernisation of equipment or grid structure having impact on the System Restoration. | It cannot be true that the TSO can change his grid structure or equipment and wait 5 years before reviewing the System Restoration Plan! |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2114 | V1.0 for Public consultation version | 6 | 48 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Each TSO shall review its Restoration Plan to assess its effectiveness, at least every 5 years. | To assess its effectiveness, each TSO shall review its Restoration Plan at least every year and before implementation of any modernisation of equipment or grid structure having impact on the System Restoration. | It cannot be true that the TSO can change his grid structure or equipment and wait 5 years before reviewing the System Restoration Plan!
0005-e495-5e7a-d54d-2235 | V1.0 for Public consultation version | 6 | 48 | 3 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | When the TSO identifies the need to adapt the System Defence Plan, it shall amend its System Defence Plan and implement these amendments in accordance with Article 8 Article 21. | When the TSO identifies the need to adapt the System Defence Plan, it shall propose the necessary amendments. Those amendments shall be subject to NRA approval before they can be implemented in accordance with Article 8 and Article 21. Any proposal for amendment shall be subject to public consultation. | Any amendments to the plan must be subject to NRA approval and consulted with the stakeholders! |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-2246 | V1.0 for Public consultation version | 6 | 48 | 3 |  | 2014-12-08 12:24 | Wolfram Heckmann | Fraunhofer IWES | final | “Each TSO shall review its restoration Plan to assess its effectiveness…” |  | Who sets the criteria for effectiveness? Will this become a quality element of the regulation? How is the regulator involved in the compliance testing?
0005-e495-5e7a-d54d-1950 | V1.0 for Public consultation version | 6 | 48 | 3 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | Each TSO shall review its Restoration Plan to assess its effectiveness, at least every 5 years. | Each TSO NRA shall review its the Restoration Plan to assess its effectiveness, at least every 5 years. | Asking the TSOs to review the Restoration Plan is like asking a student to set (and mark) their own exam questions(!). The incident, in November 2006, which gave rise to the need for NC E&R, arose from the actions / inactions of TSOs. Stakeholders and consumers across the 28 Member States need to have confidence in the System Defence Plan and the Restoration Plan. Relying upon the TSO to review the Plan(s) would be wrong. The TSO has a clear conflict of interest. If the NRA is unable or unwilling themselves to perform this task they can either appoint independent auditors to do it on their behalf or ask ACER to do it on behalf of the NRA.
0005-e495-5e7a-d54d-2115 | V1.0 for Public consultation version | 6 | 48 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | When the TSO identifies the need to adapt the Restoration Plan, it shall amend its Restoration Plan and implement these amendments in accordance with Article 21. | When the TSO identifies the need to adapt the Restoration Plan, it shall amend its Restoration Plan and implement these amendments in accordance with Article 21. Any amendment will be subject to consultation. | where on review a need to amend the System Defence or Restoration Plans is determined, then any amendment must be subject to consultation – provision should be included reflecting this.
0005-e495-5e7a-d54d-2238 | V1.0 for Public consultation version | 7 | 50 |  |  | 2014-12-08 21:33 | Wilch | RWE | final | See the wording of Article 50- Monitoring- general comment | See the justification. | The wording of this provision should be aligned with the other Network Codes/ Guidelines, in particular the latest version of CACM. |  |  | Legal | Fundamental
0005-bd99-1309-6ff0-14eb | V1.0 for Public consultation version | 7 | 51 | 1 | - | 2014-12-04 09:29:52 | Steve Wilkin | ELEXON Limited | final | ENTSO-E shall establish and regularly convene a stakeholder advisory group which shall represent the views of stakeholders to ENTSO-E. The stakeholder advisory group shall include a broad representation of relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder advisory group as observers. | ENTSO-E shall establish and regularly convene a stakeholder advisory group which shall represent the views of stakeholders to ENTSO-E. The stakeholder advisory group shall include a broad representation of stakeholders. The Agency and the Commission may attend meetings of the stakeholder advisory group as observers. | Who decides who is "relevant"? "Stakeholders" alone should be sufficient, so it is suggested that the word "relevant" is deleted. |  |  | legal |  |  |  | Non-confidential
0005-e4e5-c3fb-2f04-48ec | V1.0 for Public consultation version | 7 | 51 | 1 | - | 2014-12-08 18:18:38 | Thomas Willson |  | final | ENTSO-E shall establish and regularly convene a stakeholder advisory group … | Remove Article 51 but reuse the content on a higher level (not only for NC ER). | After the Network Codes have been brought into force, the Commission itself is responsible for monitoring and amending NCs. An advisory group seems to be very useful, but should also brought in line with the ACER proposal for organising amendments. The Advisory Group should not only monitor the NC ER but other NCs as well. |  |  | legal |  |  |  | Non-confidential
0005-2195-c3ce-d54d-7614 | V1.0 for Public consultation version | 7 | 51 | 1 | - | 2014-12-08 23:56:26 | Gunnar Kaestle | Clausthal University of Technology | final | ENTSO-E shall establish and regularly convene a stakeholder advisory group … | Remove Article 51 but reuse the content on a higher level (not only for NC ER). | After the Network Codes have been brought into force, the Commission itself is responsible for monitoring and amending NCs. An advisory group seems to be very useful, but should also brought in line with the ACER proposal for organising amendments. The Advisory Group should not only monitor the NC ER but other NCs as well. |  |  | legal |  |  |  | Non-confidential
0005-bd99-ac8c-0f0b-1b04 | V1.0 for Public consultation version | 7 | 51 | 1 | - | 2014-12-08 17:16:50 | Paul Doyle | ESB Generation & Wholesale Markets | final | ENTSO-E shall establish and regularly convene a stakeholder advisory group which shall represent the views of stakeholders to ENTSO-E. The stakeholder advisory group shall include a broad representation of relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder advisory group as observers. | ENTSO-E shall establish and regularly convene a stakeholder committee which shall represent the views of stakeholders to ENTSO-E. The stakeholder committee shall include a broad representation of DSOs, Generators and relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder committee as observers. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. DSOs play a special role in this NC, and should therefore be mentioned seperately and not under the umbrella of the 'relevant' stakeholders. |  |  | legal |  |  |  | Non-confidential
0005-e4e5-104b-c92f-7383 | V1.0 for Public consultation version | 7 | 51 | 1 | - | 2014-12-08 19:51:16 | Roland Tual | SEDC | final | 1. ENTSO-E shall establish and regularly convene a stakeholder advisory group which shall represent the views of stakeholders to ENTSO-E. The stakeholder advisory group shall include a broad representation of relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder advisory group as observers. | [8 empty] | confidential
0005-2146-a482-e960-9945 | V1.0 for Public consultation version | 7 | 51 | 1 | - | 2014-11-28 15:52:37 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | ENTSO-E shall establish and regularly convene a stakeholder advisory group which shall represent the views of stakeholders to ENTSO-E. The stakeholder advisory group shall include a broad representation of relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder advisory group as observers. | ENTSO-E shall establish and regularly convene a stakeholder committee which shall represent the views of stakeholders to ENTSO-E. The stakeholder committee shall include a broad representation of DSOs, Generators and relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder committee as observers. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. DSOs play a special role in this NC, and should therefore be mentioned seperately and not under the umbrella of the 'relevant' stakeholders. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2356 | V1.0 for Public consultation version | 7 | 51 | 1 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | ENTSO-E shall establish and regularly convene a stakeholder advisory group which shall represent the views of stakeholders to ENTSO-E. The stakeholder advisory group shall include a broad representation of relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder advisory group as observers. | ENTSO-E shall establish and regularly convene a stakeholder committee advisory group which shall represent the views of stakeholders to ENTSO-E. The stakeholder committee advisory group shall include a broad representation of DSOs and relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder committee advisory group as observers. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. DSOs play a special role in this NC, and should therefore be mentioned seperately and not under the umbrella of the 'relevant' stakeholders. |  |  | Legal
0005-e495-5e7a-d54d-2116 | V1.0 for Public consultation version | 7 | 51 | 1 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | ENTSO-E shall establish and regularly convene a stakeholder advisory group which shall represent the views of stakeholders to ENTSO-E. The stakeholder advisory group shall include a broad representation of relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder advisory group as observers. | ENTSO-E shall establish and regularly convene a stakeholder committee which shall represent the views of stakeholders to ENTSO-E. The stakeholder committee shall include a broad representation of DSOs, Generators and relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder committee as observers. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. DSOs play a special role in this NC, and should therefore be mentioned seperately and not under the umbrella of the 'relevant' stakeholders.
0005-e495-5e7a-d54d-2237 | V1.0 for Public consultation version | 7 | 51 | 1 |  | 2014-12-08 21:33 | Wilch | RWE | final | ENTSO-E shall establish and regularly convene a stakeholder advisory group which shall represent the views of stakeholders to ENTSO-E. The stakeholder advisory group shall include a broad representation of relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder advisory group as observers. | ENTSO-E shall establish and regularly convene a stakeholder committee which shall represent the views of stakeholders to ENTSO-E. The stakeholder committee shall include a broad representation of DSOs, Generators and relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder committee as observers. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. DSOs play a special role in this NC, and should therefore be mentioned seperately and not under the umbrella of the 'relevant' stakeholders. |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-2267 | V1.0 for Public consultation version | 7 | 51 | 1 |  | 2014-12-08 18:16 | Peter Claes | IFIEC | final | 1. ENTSO-E shall establish and regularly convene a stakeholder advisory group which shall represent the views of stakeholders to ENTSO-E. The stakeholder advisory group shall include a broad representation of relevant stakeholders. The Agency and the Commission may attend meetings of the stakeholder advisory group as observers. |  | End consumers should be included in this group.
0005-e495-5e7a-d54d-1952 | V1.0 for Public consultation version | 7 | 51 | 1 |  | 2014-12-08 13:31 | Garth Graham | SSE |  | ENTSO-E shall establish and regularly convene a stakeholder advisory group which shall represent the views of stakeholders to ENTSO-E. | ENTSO-E shall establish and regularly convene a SPECIFIC stakeholder advisory group FOR THIS NETWORK CODE which shall represent the views of stakeholders ; WHO ARE OBLIGED, ACCORDING TO ARTICLE 1, TO COMPLY WITH THIS NETWORK CODE ; to ENTSO-E. | The stakeholder group must be for this specific NC E&R otherwise the views on this critically important NC will not, practically, be able to be both reflect to ENTSOe or views from ENTSOe taken into account by those stakeholders.
0005-969d-d360-0f6f-8da6 | V1.0 for Public consultation version | 7 | 51 | 2 | - | 2014-12-08 17:16:51 | Paul Doyle | ESB Generation & Wholesale Markets | final | The stakeholder advisory group may assist ENTSO-E in: (a) fulfilling its monitoring duties pursuant to Article 8(8) of Regulation (EC) No 714/2009 and in particular in relation with the implementation of this Regulation; and (b) preparing proposals for amendment of this Regulation pursuant to Article 7(1) and (2) of Regulation (EC) No 714/2009. | The stakeholder committee may: (a) assist and check ENTSO-E in fulfilling its monitoring duties pursuant to Article 8(8) of Regulation (EC) No 714/2009 and in particular in relation with the implementation of this Regulation; and (b) prepare proposals for amendment of this Regulation pursuant to Article 7(1) and (2) of Regulation (EC) No 714/2009. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. ENTSO-E introduces here the possibility for the stakeholder committee to be involved in the amendment process. ENTSO-E suggests to take the lead in this amendment process. This is not in line with Regulation 714/2009. ENTSO-E has no defined role in the amendment process (except for the advisory role defined by ACER in its Guidance on this amendment proces). It is up to ACER to play a major role in the amendment process of a network code. Regulation 714/2009 art. 7§1 is also very clear : “Draft amendments to any network code adopted under Article 6 may be proposed to the Agency by persons who are likely to have an interest in that network code, including ...”. In its proposal ENTSO-E denies the right of stakeholders to indepently introduce amendments to the codes/guidelines. The stakeholder committee must be able to act in case of conflict with ENTSO-E. |  |  | legal |  |  |  | Non-confidential
0005-e4aa-b440-e708-5726 | V1.0 for Public consultation version | 7 | 51 | 2 | - | 2014-11-28 15:52:38 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The stakeholder advisory group may assist ENTSO-E in: (a) fulfilling its monitoring duties pursuant to Article 8(8) of Regulation (EC) No 714/2009 and in particular in relation with the implementation of this Regulation; and (b) preparing proposals for amendment of this Regulation pursuant to Article 7(1) and (2) of Regulation (EC) No 714/2009. | The stakeholder committee may: (a) assist and check ENTSO-E in fulfilling its monitoring duties pursuant to Article 8(8) of Regulation (EC) No 714/2009 and in particular in relation with the implementation of this Regulation; and (b) prepare proposals for amendment of this Regulation pursuant to Article 7(1) and (2) of Regulation (EC) No 714/2009. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. ENTSO-E introduces here the possibility for the stakeholder committee to be involved in the amendment process. ENTSO-E suggests to take the lead in this amendment process. This is not in line with Regulation 714/2009. ENTSO-E has no defined role in the amendment process (except for the advisory role defined by ACER in its Guidance on this amendment proces). It is up to ACER to play a major role in the amendment process of a network code. Regulation 714/2009 art. 7§1 is also very clear : “Draft amendments to any network code adopted under Article 6 may be proposed to the Agency by persons who are likely to have an interest in that network code, including ...”. In its proposal ENTSO-E denies the right of stakeholders to indepently introduce amendments to the codes/guidelines. The stakeholder committee must be able to act in case of conflict with ENTSO-E. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2357 | V1.0 for Public consultation version | 7 | 51 | 2 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | The stakeholder advisory group may assist ENTSO-E in: (a) fulfilling its monitoring duties pursuant to Article 8(8) of Regulation (EC) No 714/2009 and in particular in relation with the implementation of this Regulation; and (b) preparing proposals for amendment of this Regulation pursuant to Article 7(1) and (2) of Regulation (EC) No 714/2009. | The stakeholder committee advisory group may assist ENTSO-E in: (a) fulfilling its monitoring duties pursuant to Article 8(8) of Regulation (EC) No 714/2009 and in particular in relation with the implementation of this Regulation; and (b) preparing proposals for amendment of this Regulation pursuant to Article 7(1) and (2) of Regulation (EC) No 714/2009. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. ENTSO-E introduces here the possibility for the stakeholder committee to be involved in the amendment process. ENTSO-E suggests to take the lead in this amendment process. This is not in line with Regulation 714/2009. ENTSO-E has no defined role in the amendment process (except for the advisory role defined by ACER in its Guidance on this amendment proces). It is up to ACER to play a major role in the amendment process of a network code. Regulation 714/2009 art. 7§1 is also very clear : “Draft amendments to any network code adopted under Article 6 may be proposed to the Agency by persons who are likely to have an interest in that network code, including ...”. In its proposal ENTSO-E denies the right of stakeholders to indepently introduce amendments to the codes/guidelines. |  |  | Legal
0005-e495-5e7a-d54d-2117 | V1.0 for Public consultation version | 7 | 51 | 2 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The stakeholder advisory group may assist ENTSO-E in: (a) fulfilling its monitoring duties pursuant to Article 8(8) of Regulation (EC) No 714/2009 and in particular in relation with the implementation of this Regulation; and (b) preparing proposals for amendment of this Regulation pursuant to Article 7(1) and (2) of Regulation (EC) No 714/2009. | The stakeholder committee may: (a) assist and check ENTSO-E in fulfilling its monitoring duties pursuant to Article 8(8) of Regulation (EC) No 714/2009 and in particular in relation with the implementation of this Regulation; and (b) prepare proposals for amendment of this Regulation pursuant to Article 7(1) and (2) of Regulation (EC) No 714/2009. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. ENTSO-E introduces here the possibility for the stakeholder committee to be involved in the amendment process. ENTSO-E suggests to take the lead in this amendment process. This is not in line with Regulation 714/2009. ENTSO-E has no defined role in the amendment process (except for the advisory role defined by ACER in its Guidance on this amendment proces). It is up to ACER to play a major role in the amendment process of a network code. Regulation 714/2009 art. 7§1 is also very clear : “Draft amendments to any network code adopted under Article 6 may be proposed to the Agency by persons who are likely to have an interest in that network code, including ...”. In its proposal ENTSO-E denies the right of stakeholders to indepently introduce amendments to the codes/guidelines. The stakeholder committee must be able to act in case of conflict with ENTSO-E.
0005-2159-c3c0-0ddf-a459 | V1.0 for Public consultation version | 7 | 51 | 3 | - | 2014-12-08 17:16:53 | Paul Doyle | ESB Generation & Wholesale Markets | final | The stakeholder advisory group shall include a broad representation of stakeholders, including DSOs, system users and power equipment manufacturers. Prior to its first meeting and at least yearly thereafter, ENTSO-E shall submit to the Agency the proposed composition of the stakeholder advisory group. The Agency may issue an opinion on the composition of the stakeholder advisory group within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | The stakeholder committee shall include a broad representation of DSOs, Generators and stakeholders, including system users and power equipment manufacturers. Prior to its first meeting and at least yearly thereafter, ENTSO-E shall submit to the Agency the proposed composition of the stakeholder committee. The Agency may issue an opinion on the composition of the stakeholder committee within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. DSOs and generators play a special role in this NC, and should therefore be mentioned seperately and not under the umbrella of the 'relevant' stakeholders. |  |  | legal |  |  |  | Non-confidential
0005-6f8e-5662-e8fc-1736 | V1.0 for Public consultation version | 7 | 51 | 3 | - | 2014-11-28 15:52:39 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The stakeholder advisory group shall include a broad representation of stakeholders, including DSOs, system users and power equipment manufacturers. Prior to its first meeting and at least yearly thereafter, ENTSO-E shall submit to the Agency the proposed composition of the stakeholder advisory group. The Agency may issue an opinion on the composition of the stakeholder advisory group within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | The stakeholder committee shall include a broad representation of DSOs, Generators and stakeholders, including system users and power equipment manufacturers. Prior to its first meeting and at least yearly thereafter, ENTSO-E shall submit to the Agency the proposed composition of the stakeholder committee. The Agency may issue an opinion on the composition of the stakeholder committee within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. DSOs and generators play a special role in this NC, and should therefore be mentioned seperately and not under the umbrella of the 'relevant' stakeholders. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2358 | V1.0 for Public consultation version | 7 | 51 | 3 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | The stakeholder advisory group shall include a broad representation of stakeholders, including DSOs, system users and power equipment manufacturers. Prior to its first meeting and at least yearly thereafter, ENTSO-E shall submit to the Agency the proposed composition of the stakeholder advisory group. The Agency may issue an opinion on the composition of the stakeholder advisory group within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | The stakeholder committee advisory group shall include a broad representation of DSOs and stakeholders, including system users and power equipment manufacturers. Prior to its first meeting and at least yearly thereafter, ENTSO-E shall submit to the Agency the proposed composition of the stakeholder committee advisory group. The Agency may issue an opinion on the composition of the stakeholder committee advisory group within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. DSOs play a special role in this NC, and should therefore be mentioned seperately and not under the umbrella of the 'relevant' stakeholders. |  |  | Legal
0005-e495-5e7a-d54d-2118 | V1.0 for Public consultation version | 7 | 51 | 3 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The stakeholder advisory group shall include a broad representation of stakeholders, including DSOs, system users and power equipment manufacturers. Prior to its first meeting and at least yearly thereafter, ENTSO-E shall submit to the Agency the proposed composition of the stakeholder advisory group. The Agency may issue an opinion on the composition of the stakeholder advisory group within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | The stakeholder committee shall include a broad representation of DSOs, Generators and stakeholders, including system users and power equipment manufacturers. Prior to its first meeting and at least yearly thereafter, ENTSO-E shall submit to the Agency the proposed composition of the stakeholder committee. The Agency may issue an opinion on the composition of the stakeholder committee within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. DSOs and generators play a special role in this NC, and should therefore be mentioned seperately and not under the umbrella of the 'relevant' stakeholders.
0005-487e-b45e-e7d0-31bb | V1.0 for Public consultation version | 7 | 51 | 4 | - | 2014-11-28 15:52:40 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | ENTSO-E shall submit to the Agency proposed rules and procedures of the stakeholder advisory group. The Agency may provide an opinion on the proposed rules and procedures within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | ENTSO-E shall submit to the Agency proposed rules and procedures of the stakeholder committee. The Agency may provide an opinion on the proposed rules and procedures within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. |  |  | legal |  |  |  | Non-confidential
0005-96b1-5e6c-0cb3-8a2a | V1.0 for Public consultation version | 7 | 51 | 4 | - | 2014-12-08 17:16:54 | Paul Doyle | ESB Generation & Wholesale Markets | final | ENTSO-E shall submit to the Agency proposed rules and procedures of the stakeholder advisory group. The Agency may provide an opinion on the proposed rules and procedures within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | ENTSO-E shall submit to the Agency proposed rules and procedures of the stakeholder committee. The Agency may provide an opinion on the proposed rules and procedures within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2359 | V1.0 for Public consultation version | 7 | 51 | 4 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | ENTSO-E shall submit to the Agency proposed rules and procedures of the stakeholder advisory group. The Agency may provide an opinion on the proposed rules and procedures within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | ENTSO-E shall submit to the Agency proposed rules and procedures of the stakeholder committee advisory group. The Agency may provide an opinion on the proposed rules and procedures within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. |  |  | Legal
0005-e495-5e7a-d54d-2119 | V1.0 for Public consultation version | 7 | 51 | 4 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | ENTSO-E shall submit to the Agency proposed rules and procedures of the stakeholder advisory group. The Agency may provide an opinion on the proposed rules and procedures within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | ENTSO-E shall submit to the Agency proposed rules and procedures of the stakeholder committee. The Agency may provide an opinion on the proposed rules and procedures within two (2) months upon submission. ENTSO-E shall take utmost account of such an opinion. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC.
0005-e495-5e7a-d54d-2236 | V1.0 for Public consultation version | 7 | 51 | 4 |  | 2014-12-08 21:33 | Marta Krajewska | Energy UK | final | When the TSO identifies the need to adapt the Restoration Plan, it shall amend its Restoration Plan and implement these amendments in accordance with Article 21. | When the TSO identifies the need to adapt the Restoration Plan, it shall propose the necessary amendments. Those amendements shall be subject to NRA approval before they can be implemented in accordance with Article 21. Any proposal for amendment shall be subject to consultation. | Any amendments to the plan must be subject to NRA approval and consulted with the stakeholders! |  |  | Legal | Fundamental
0005-e4bd-785d-6ec4-7346 | V1.0 for Public consultation version | 7 | 51 | 5 | - | 2014-12-04 09:32:16 | Steve Wilkin | ELEXON Limited | final | The stakeholder advisory group may serve as a specific stakeholder advisory group or may for efficiency reasons be merged with other stakeholder advisory groups established to assist ENTSO-E in accordance with other network codes or guidelines developed pursuant to Article 6 or 18 of Regulation (EC) No 714/2009. | The stakeholder advisory group may serve as a specific stakeholder advisory group or may for efficiency reasons be merged with other stakeholder advisory groups established to assist ENTSO-E in accordance with other network codes or guidelines developed pursuant to Article 6 or 18 of Regulation (EC) No 714/2009. Any such proposed merger shall be subject to public consultation with the stakeholders of the relevant Network Codes and Guidelines and approval by the Agency. | The stakeholders for each Network Code and Guideline are likely to be different, so the concept of mergers between stakeholder groups for efficiency reasons needs very careful consideration before it is undertaken. In fact our strong preference is that for the Network Code on Electricity Balancing and for this Network Code on Emergency and Restoration there should not be mergers with any other stakeholder groups. For the Network Code on Electricity Balancing for example, NEMOs play no role in imbalance settlement whereas third parties, such as ELEXON, may. Similarly NEMOs play a key role in CACM, but third parties, such as ELEXON, do not. And for this Network Code on Emergency and Restoration, it is now a hybrid operational and market code through the inclusion of Chapter 4 so a merger with another operational code or market code stakeholder group would not be appropriate. Ideally Chapter 4 should be moved into the respective parts of the market codes depending on which market is being suspended and restored. For example, the Network Code on Electricity Balancing should cover the suspension and restoration of balancing markets, and the CACM Guideline should cover the suspension and restoration of single day-ahead coupling, etc. But given that the CACM Guidelines are almost complete, we suggest that Chapter 4 alone should fall under the governance of a special stakeholder group with market expertise. |  |  | legal |  |  |  | Non-confidential
0005-bd86-a4be-e76c-36b3 | V1.0 for Public consultation version | 7 | 51 | 5 | - | 2014-11-28 15:52:41 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The stakeholder advisory group may serve as a specific stakeholder advisory group or may for efficiency reasons be merged with other stakeholder advisory groups established to assist ENTSO-E in accordance with other network codes or guidelines developed pursuant to Article 6 or 18 of Regulation (EC) No 714/2009. | The stakeholder committee may serve as a specific stakeholder committee or may for efficiency reasons be merged with other stakeholder committees established in accordance with other network codes or guidelines developed pursuant to Article 6 or 18 of Regulation (EC) No 714/2009. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. The stakeholder committee must be able to act in case of conflict with ENTSO-E. |  |  | legal |  |  |  | Non-confidential
0005-bdad-4ecc-0beb-240d | V1.0 for Public consultation version | 7 | 51 | 5 | - | 2014-12-08 17:16:56 | Paul Doyle | ESB Generation & Wholesale Markets | final | The stakeholder advisory group may serve as a specific stakeholder advisory group or may for efficiency reasons be merged with other stakeholder advisory groups established to assist ENTSO-E in accordance with other network codes or guidelines developed pursuant to Article 6 or 18 of Regulation (EC) No 714/2009. | The stakeholder committee may serve as a specific stakeholder committee or may for efficiency reasons be merged with other stakeholder committees established in accordance with other network codes or guidelines developed pursuant to Article 6 or 18 of Regulation (EC) No 714/2009. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. The stakeholder committee must be able to act in case of conflict with ENTSO-E. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2360 | V1.0 for Public consultation version | 7 | 51 | 5 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | The stakeholder advisory group may serve as a specific stakeholder advisory group or may for efficiency reasons be merged with other stakeholder advisory groups established to assist ENTSO-E in accordance with other network codes or guidelines developed pursuant to Article 6 or 18 of Regulation (EC) No 714/2009. | The stakeholder committee advisory group may serve as a specific stakeholder committee advisory group or may for efficiency reasons be merged with other stakeholder committees advisory groups established to assist ENTSO-E in accordance with other network codes or guidelines developed pursuant to Article 6 or 18 of Regulation (EC) No 714/2009. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. |  |  | Legal
0005-e495-5e7a-d54d-2120 | V1.0 for Public consultation version | 7 | 51 | 5 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The stakeholder advisory group may serve as a specific stakeholder advisory group or may for efficiency reasons be merged with other stakeholder advisory groups established to assist ENTSO-E in accordance with other network codes or guidelines developed pursuant to Article 6 or 18 of Regulation (EC) No 714/2009. | The stakeholder committee may serve as a specific stakeholder committee or may for efficiency reasons be merged with other stakeholder committees established in accordance with other network codes or guidelines developed pursuant to Article 6 or 18 of Regulation (EC) No 714/2009. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. The stakeholder committee must be able to act in case of conflict with ENTSO-E.
0005-bd85-787b-70b8-13c6 | V1.0 for Public consultation version | 7 | 51 | 6 | - | 2014-12-04 09:33:43 | Steve Wilkin | ELEXON Limited | final | The stakeholder advisory group shall ensure a high level of transparency and make publicly available relevant documents such as the rules of procedures, summaries of the stakeholder advisory group meeting minutes or documents related to the meetings. | The stakeholder advisory group shall ensure a high level of transparency and make publicly available relevant documents such as the rules of procedures, summaries of the stakeholder advisory group meeting minutes or documents related to the meetings at the same time as such documents are made available to the stakeholder advisory group itself. | Timing of the provision of information to stakeholders is key to proper transparency and to avoid some stakeholders/competitors who sit on the advisory group having advantage over others who do not, the documents should be published on an appropriate public website at the same time as they are made available to the stakeholder advisory group itself. |  |  | legal |  |  |  | Non-confidential
0005-9676-cbce-ea28-8856 | V1.0 for Public consultation version | 7 | 51 | 6 | - | 2014-11-28 15:52:41 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | The stakeholder advisory group shall ensure a high level of transparency and make publicly available relevant documents such as the rules of procedures, summaries of the stakeholder advisory group meeting minutes or documents related to the meetings. | The stakeholder committee shall ensure a high level of transparency and make publicly available relevant documents such as the rules of procedures, summaries of the stakeholder committee meeting minutes or documents related to the meetings. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. |  |  | legal |  |  |  | Non-confidential
0005-bdd5-5e6c-0beb-40a7 | V1.0 for Public consultation version | 7 | 51 | 6 | - | 2014-12-08 17:16:58 | Paul Doyle | ESB Generation & Wholesale Markets | final | The stakeholder advisory group shall ensure a high level of transparency and make publicly available relevant documents such as the rules of procedures, summaries of the stakeholder advisory group meeting minutes or documents related to the meetings. | The stakeholder committee shall ensure a high level of transparency and make publicly available relevant documents such as the rules of procedures, summaries of the stakeholder committee meeting minutes or documents related to the meetings. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2361 | V1.0 for Public consultation version | 7 | 51 | 6 | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | The stakeholder advisory group shall ensure a high level of transparency and make publicly available relevant documents such as the rules of procedures, summaries of the stakeholder advisory group meeting minutes or documents related to the meetings. | The stakeholder committee advisory group shall ensure a high level of transparency and make publicly available relevant documents such as the rules of procedures, summaries of the stakeholder committee advisory group meeting minutes or documents related to the meetings. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. |  |  | Legal
0005-e495-5e7a-d54d-2121 | V1.0 for Public consultation version | 7 | 51 | 6 |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | The stakeholder advisory group shall ensure a high level of transparency and make publicly available relevant documents such as the rules of procedures, summaries of the stakeholder advisory group meeting minutes or documents related to the meetings. | The stakeholder committee shall ensure a high level of transparency and make publicly available relevant documents such as the rules of procedures, summaries of the stakeholder committee meeting minutes or documents related to the meetings. | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC.
0005-bdad-11e0-a231-d32b | V1.0 for Public consultation version | 7 | 51 | - | - | 2014-12-04 14:03:18 | Dekinderen Eric | Genrator company | final | Stakeholders Advisory Group | This Art has to be coherent with the more general paper of ENTSOE "The role of stakeholders in the implementatiobn and revision of European network codes and related guidelines" dated 3/10/2014 | This Art has to be coherent with the more general paper of ENTSOE "The role of stakeholders in the implementatiobn and revision of European network codes and related guidelines" dated 3/10/2014 |  |  | legal |  |  |  | Non-confidential
0005-96c5-ac50-0beb-e7e4 | V1.0 for Public consultation version | 7 | 51 | - | - | 2014-12-08 17:17:00 | Paul Doyle | ESB Generation & Wholesale Markets | final | Stakeholder Advisory Group | Stakeholder Committee | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. |  |  | legal |  |  |  | Non-confidential
0005-e4bd-105d-4be7-21e6 | V1.0 for Public consultation version | 7 | 51 | - | - | 2014-12-08 20:11:10 | European Committee of Domestic Equipment Manufacturers |  | final |  |  | The decision-making process described in this Network Code appears to be unbalanced in view of the consequences of the requirements involved, notably concerning the preventive system defence plans. These consultation processes are inappropriate for taking decisions towards residential consumers. Although the TSOs - as they are responsible for the security of the electricity system - shall be given exceptional extended authority in emergency, blackout and restoration situations, there should be a supervision by national regulatory authorities to ensure that the principles of proportionality and social welfare are respected, in particular when such plans have consequences on small residential consumers. |  |  | legal |  |  |  | Non-confidential
0005-9675-75a0-0d7b-1b87 | V1.0 for Public consultation version | 7 | 51 | - | - | 2014-12-08 17:17:01 | Paul Doyle | ESB Generation & Wholesale Markets | final | Stakeholders Advisory Group |  | This Article has to be replaced by the more general paper of ENTSOE "The role of stakeholders in the implementatiobn and revision of European network codes and related guidelines" dated 3/10/2014 |  |  | legal |  |  |  | Non-confidential
0005-e4d1-8758-1209-a719 | V1.0 for Public consultation version | 7 | 51 | - | - | 2014-12-03 11:11:00 | AXPO Group |  | final | Original text of issue 13.10.2014 | see Comment | It would be wise to involve the stakeholders already in the drafting phase of a code. Make them part of the drafting teams as they are the keyplayers of the system. |  |  | legal |  |  |  | Non-confidential
0005-bd86-db50-e960-9ec4 | V1.0 for Public consultation version | 7 | 51 | - | - | 2014-11-28 15:52:42 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Stakeholder Advisory Group | Stakeholder Committee | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. |  |  | legal |  |  |  | Non-confidential
0005-96b2-3ef2-e7d0-24ed | V1.0 for Public consultation version | 7 | 51 | - | - | 2014-11-28 15:53:00 | VGB PowerTech e.V. | VGB PowerTech e.V. | final | Stakeholders Advisory Group |  | This Article has to be replaced by the more general paper of ENTSOE "The role of stakeholders in the implementatiobn and revision of European network codes and related guidelines" dated 3/10/2014 |  |  | legal |  |  |  | Non-confidential
0005-e495-5e7a-d54d-2355 | V1.0 for Public consultation version | 7 | 51 | - | - | 2014-12-08 22:31 | Michael Wilch | RWE | final | Stakeholder Advisory Group | Stakeholder Committee Advisory Group | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC. |  |  | Legal
0005-e495-5e7a-d54d-2122 | V1.0 for Public consultation version | 7 | 51 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Stakeholder Advisory Group | Stakeholder Committee | Use of Committee instead of Advisory Group to be in line with Commission drafts of the NC RfG and NC DC.
0005-e495-5e7a-d54d-2123 | V1.0 for Public consultation version | 7 | 51 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | Stakeholders Advisory Group |  | This Article has to be replaced by the more general paper of ENTSOE "The role of stakeholders in the implementatiobn and revision of European network codes and related guidelines" dated 3/10/2014
0005-e495-5e7a-d54d-2239 | V1.0 for Public consultation version | 7 | 51 |  |  | 2014-12-08 21:33 | EDK | GFS | final | ENTSO-E shall establish and regularly convene a stakeholder advisory group which shall represent the views of stakeholders to ENTSO-E. | ENTSO-E shall establish and regularly convene a specific stakeholder advisory group for this Network Code which shall represent the views of the stakeholders who are obliged to comply with its provisions in accordance with Article 1. | The stakeholder group must be for this specific NC ER- given its particular nature and the presence of the market interactions chapter. However, we understand that this issue will be subject to a separate public consultation which shall be open shortly. |  |  | Legal | Fundamental
0005-e495-5e7a-d54d-2124 | V1.0 for Public consultation version | 8 | 52 |  |  | 2014-12-08 16:47 | Charlotte Renaud | EURELECTRIC_VGB Powertech | final | By [date – the same as the date in Article 53], each relevant TSO, DSO and each relevant Significant Grid User shall amend all relevant clauses in contracts and relevant clauses in general terms and conditions, regardless of whether the relevant contracts or general terms and conditions contain an amendment process, in order to achieve compliance with the requirements of this Network Code. | By [date – the same as the date in Article 53], each relevant TSO, DSO and each relevant Significant Grid User shall agree on all necessary amendments in all relevant clauses in contracts and relevant clauses in general terms and conditions, regardless of whether the relevant contracts or general terms and conditions contain an amendment process, in order to achieve compliance with the requirements of this Network Code. | This article is not acceptable as it is. Market participants do not know what the costs of having to comply with this NC’s, as yet unseen, requirements are. The NC RFG for e.g. applies to just new generators who are given up to 3 years post entry into force to make amendments to comply with the NC. This is as far as this NC should also reasonably go to in terms of imposing requirements for changes in contracts on people when often these changes may incur huge costs which under this NC are as yet unquantifiable.
0005-e495-5e7a-d54d-1713 | V1.0 for Public consultation version | 8 | 53 | - | - | 2014-12-08 23:56:26 | Gunnar Kaestle | Clausthal University of Technology | final | It shall apply as from the day of expiration of a XX period following its publication or from DATE | add a figure for XX or a DATE | For the impact assessment of this code, a crucial piece of information is the date when the requirements are becoming binding. |  |  | legal |  |  |  | Non-confidential
confidential

## analysis
Article | Number of comments | total comments | 1236
0 | 52
1 | 41
2 | 59
3 | 11
4 | 24
5 | 16
6 | 3
7 | 4
8 | 94
9 | 66
10 | 26
11 | 24
12 | 43
13 | 63
14 | 20
15 | 26
16 | 18
17 | 38
18 | 30
19 | 22
20 | 88
21 | 47
22 | 8
23 | 2
24 | 28
25 | 1
26 | 9
27 | 13
28 | 5
29 | 10
30 | 2
31 | 6
32 | 15
33 | 9
34 | 8
35 | 10
36 | 6
37 | 38
38 | 21
39 | 34
40 | 35
41 | 16
42 | 20
43 | 7
44 | 9
45 | 14
46 | 7
47 | 19
48 | 21
49 | 0
50 | 1
51 | 45
52 | 1
53 | 1