## Introduction
AS Survey 2018
Survey on Ancillary Services Procurement and Electricity Balancing Market Design
The survey provides support for the implementation of the Electricity Balancing Guideline (EB GL) and highlights the challenges facing the pan-European harmonisation of electricity balancing market design. The survey information is used to monitor the implementation of the EB GL and to report on the development towards a European balancing market.
The members who responded to the 2016 survey are as follows: Austria, Belgium, Bosnia & Herzegovina, Croatia, Czech Republic, Denmark, Estonia, Finland, France, Germany, Greece, Hungary, Ireland & NI, Italy, Latvia, Lithuania, Norway, Poland, Portugal, Romania, Serbia, Slovakia, Slovenia, Spain, Sweden, Switzerland, The Netherlands, United Kingdom.
Caveats
Data collection is a relatively high-level exercise; therefore not all details are captured.
Different countries use different concepts. Hence the development of a single set of definitions encounters difficulty in matching the various concepts. Consequently, in a number of specific cases, the position of a country in a certain group might be debatable.
The survey has been conducted in 2016, thus contains data from 2015/2016, which may be outdated in the meanwhile.
For more information on the Ancillary services survey, please contact ricardo.renedowilliams@entsoe.eu

## Definitions
Terms and Definitions
Link to the ENTSO-E EMR Glossary
Term | Definition
Activation rule | How the frequency restoration reserves are activated i.e. by a Pro-Rata system or on the basis of a Merit Order (cheapest being activated first).
Activation Purpose | Are activations for other purposes than Balancing (e.g. congestion management) possible?
Activation Time | Activation Time means the period of time between receipt of a valid instruction by the Activation Optimisation Function and the end of ramping to meet that instruction.
Additional Components | Other components which determine imbalance charges.
Aggravating Imbalance | BRP imbalance same direction as Imbalance Price Area imbalance.
Average Control Energy Price | Average Control Energy Price is calculated by taking the sum of the control energy prices and dividing it by the number of the prices being examined.
Balance Responsible Party (BRP) | Balancing Responsible Party means a market participant or its chosen representative responsible for its Imbalances.
Balancing Obligation Enforcment | Nature of balance responsibility enforcement.
Central Dispatch | Central dispatch means a scheduling and dispatching model where the generation schedules and consumption schedules as well as dispatching of power generating facilities and demand facilities, in reference to dispatchable facilities, are determined by a TSO within the integrated scheduling process.
Complaint Period | Length of time for which complaints can be made which will be considered in relation to settlement (after the finalized data are produced).
Consumption Responsible Party (CRP) | A party who can be brought to rights, legally and financially, for any imbalance between energy nominated and consumed for all associated Accounting Points.
Cost Recovery Scheme | From who are the costs recovered.
Day Ahead Market Price | Price which evolved on the day ahead market.
Distance to real time of energy products (reserve products activation) | The time ahead from real time when TSO activates a given product (for instance 15 minutes in the case of mFRR/tertiary energy).
Distance to real time of reserve products auctions | The time ahead from real time when auction/agreement for an specific balancing product takes place (for instance = 1 year in the case of a reserve agreement signed 1 year ahead of real time).
Dual Pricing | Imbalance Price does not take system state into account. Different prices for aggravating and non-aggravating imbalance.
Energy Bids | Acceptable Energy Bids.
Ex-post Check | When the monitoring of performance of plant carried out 24 hours after the delivery period.
Exemptions | Market participants which do not have obligations to be responsible for its imbalance.
Exemptions | Those parties that do not have a balancing obligation.
Explicit offer | Specified and limited bids - for Standing unit
Final Imbalance Price | Imbalance price means the price, be it positive, zero or negative, in each imbalance settlement period for an imbalance in each direction. Final imbalance price is calculated price for settlement period that cannot be changed anymore.
Free Offers | Offers without a contract for Balancing Capacity possible.
Frequency Containment Reserve (FCR) | Operating reserves activated for stabilizing System Frequency after an imbalance.
Frequency Restoration Reserve (FRR) | Reserves activated to restore System Frequency to the Nominal Frequency and, where applicable, power balance to the scheduled value. aFRR means automatic FRR, mFRR means manual FRR.
Gate Closure Times (GCT) | Deadline for the participation to a given market or mechanism.
Grid User | The natural or legal person supplying to, or being supplied with active and/or reactive power by a TSO or DSO.
Hybrid | Combination.
Charges and/or fees | Charges and/or fees if the DSO does not respect the tan Phi and/or the diagram rule.
Imbalance Position | The declared energy volume of a balance responsible party used for the calculation of its imbalance.
Imbalance Price | The price, be it positive, zero or negative, in each imbalance settlement period for an imbalance in each direction.
Imbalance Price Area | The area for the calculation of an imbalance price.
Imbalance Settlement Period | The unit of settlement that is applied to the quantities in which the time series is expressed.
Imbalance Settlement Responsible Party (ISR) | A party that is responsible for settlement of the difference between the contracted quantifies and the realized quantifies of energy products for the BRPs in a Market Balance Area.
Implicit offer | If the unit has schedule (it is operate) then automatically must have offer for Voltage Control
Intraday Market Price | The price of the market within regular business hours, short-term prices.
Local constraint | Local constraint means a situation in which there is a need to implement Remedial Action in order to respect Operational Security Limits in the matter of the location.
Main component of Imbalance Prices | The component that determines imbalance charges most of the time.
Mandatory only | Generators connected to the grid are obligated to reserve a certain amount of capacity in order to meet TSO requirements, for a fixed price set by TSO, NRA or for free.
Market only | There is no contract or obligation for a grid user to offer the reserve (before the offer). The grid user can voluntary participate in the market (e.g. tender, auction, market platform (like PX)) and bid a price or customize his offer (e.g. the volume, timeframe). The market result may lead to a bilateral contract.
Mandatory Offers | Generators connected to the grid are obligated to offer the remaining capacity/available capacity.
Mandatory Provision | Generators connected to the grid are obligated to reserve a certain amount of capacity in order to meet TSO requirements, for a fixed price set by TSO, NRA or for free.
Marginal Control Energy Price | The highest price, which can be acceptable.
Marginal Pricing | All capacity or balancing energy settled at the same price – price of the most expansive capacity bid procured or most expansive balancing energy bid activated.
Merit order | A merit order is a way of ranking available sources of energy in ascending order of their short run marginal costs of production, so that those with the lowest marginal costs are the first ones to be brought online to meet demand.
Minimal Incentives | Minimal incentives means that there is some method which leads the BRPs to balance their schedules.
Monitoring | Refers to the type of monitoring in place by the system operator to ensure performance of plant.
Number of Prices | Number of prices for Imbalance Position.
Number of Imbalance Position | Number of Imbalance Positions is a property of local market design. For each Imbalance Position Imbalance Volume is calculated.
Optimization approach | What kind of Voltage Control optimization is available in your control area?
Pay as bid | Contracted parties who provide a service are paid based on their offer price.
Pre contracted | BSP has sold/procured Balancing Capacity.
Pro Rata (Parallel Activation) | All bids always activated in parallel – proportionally.
Procurement Scheme | Background of the offer, which is closest to the real operation time.
Product Resolution (in MW) | The minimum bid size into the balancing market.
Product Resolution (in time) | The maximum resolution for which the product can be bid into the market (for instance =1 hour in the case of a 24 auctions day ahead market for reserve provision).
Production Responsible Party (PRP) | A party who can be brought to rights, legally and financially, for any imbalance between energy nominated and produced for all associated Accounting Points.
Publication | Publication of final Imbalance Price.
Real-Time Monitoring | Monitoring of delivery of ancillary services in real time.
Reducing Imbalance | BRP imbalance opposite direction as Imbalance Area imbalance.
Regulated Price | Price for this service is based on a price that is set by the relevant regulatory authority.
Replacement Reserve (RR) | Replacement Reserves (RR) means the reserves used to restore/support the required level of FRR to be prepared for further system imbalances. This category includes operating reserves with activation time from Time to Restore Frequency up to hours.
Secondary Market for reserve obligation | Trading procedure between the BSPs (where at least one BSP has contract with the TSO) to ensure the prescribed reserve amount of the TSO.
SecVolCon reactive | SecVolCon sending a reactive setpoint to the units (manually or automatically)
SecVolCon voltage | SecVolCon sending a voltage setpoint to the units (manually or automatically)
Self-Dispatch - Portfolio Based | Self Dispatch System – Portfolio based means a scheduling and dispatching model where the aggregated generation schedules and consumption schedules as well as dispatching of power generating facilities and demand facilities are determined by the scheduling agents of those facilities.
Self-Dispatch - Unit Based | Self Dispatch System – Unit based means a scheduling and dispatching model where power generating facilities and demand facilities follow their own generation schedules or consumption schedules.
Settlement Rule | The pricing rules for settlement.
Single Pricing | Imbalance Price takes system state into account, same price for aggravating and non-aggravating imbalance.
Symmetrical Product | Upward regulation volume and for downward regulation volume has to be equal.
Trade Responsible Party (TRP) | A party who can be brought to rights, legally and financially, for any imbalance between energy nominated and consumed for all associated Accounting Points.

## Imbalance Settlement
|  | IS1.0 | IS2.0.1 | IS2.0.2 | IS2.0.3 | IS2.1 | IS3.0 | IS3.1 | IS4.1 | IS4.2 | IS4.3 | IS5.1 | IS5.2 | IS5.3 | IS6.1 | IS6.2 | IS6.3 | IS6.4 | IS6.5 | IS6.6 | IS6.7 | IS7.0 | IS8.1 | IS8.2 | IS8.3 | IS8.4 | IS9.0 | IS10.0 | IS11.0 | IS13.0 | IS14.0 | IS15.0 | IS16.0
AS Survey 2018 | [8 empty] | Settlement Period |  |  | Number of Prices |  |  | Main component of Imbalance Prices | [7 empty] | Control energy prices used
Country | TSO Name | Nature of the balancing obligation | Exemptions - RES | Exemptions - Generators | Exemptions - Other | Is there a limit to exemption? | Number of Imbalance Positions | If there are more than 2 positions, please, clarify! | If 1 position | If 2 positions/Generation | If 2 positions/Consumption | If 1 position | If 2 position/Generation | If 2 position/Consumption | If 1 position/Aggravating imbalances | If 1 position/Reducing imbalances | If 2 positions/For generation "aggravating imbalance" | If 2 positions/For consumption "aggravating imbalance" | If 2 positions/For generation "reducing imbalance" | If 2 positions/For consumption "reducing imbalance" | Additional components | Is there a minimal incentive? | FCR | aFRR | mFRR | RR | Start/ Stop costs in imbalance charges | Publication | Complaint period | Additional - Gate Closure time for notification of Internal Trade Schedules | Additional - Intra Day Market time period | Additional - Can market participants change the approved schedules after Delivery? | Do you consider changes significant/important regarding the imbalance settlement?
Austria | APG | Financial only | No | No | No | N/A | 1 position | - | 15 min | N/A | N/A | Single Pricing | N/A | N/A | Other | Other | N/A | N/A | N/A | N/A | Other | Yes | This product is not used in settlement price calculation | This product is not used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | No | x > 1 week after delivery | x > 12 weeks | Ex-post notification allowed | 15 min | Always (GCT after delivery) | No changes
| VUEN | Financial only | No | No | No | N/A | 1 position | - | 15 min | N/A | N/A | Single Pricing | N/A | N/A | Other | Other | N/A | N/A | N/A | N/A | Other | Yes | This product is not used in settlement price calculation | This product is not used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | No | x > 1 week after delivery | x > 12 weeks | Ex-post notification allowed | 15 min | Always (GCT after delivery) | No changes
Belgium | Elia | Legal+financial | No | Yes | No | % of nominations | 1 position | - | 15 min | N/A | N/A | Single Pricing | N/A | N/A | Marginal Control Energy Price | Marginal Control Energy Price | N/A | N/A | N/A | N/A | Variable component | No | This product is not used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | Yes | x <= 1 hour after delivery | x > 12 weeks | N/A | 15 min | Always (GCT after delivery) | No changes
Bulgaria | ESO | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Cyprus | TSO-Cyprus | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Czech Republic | CEPS | Financial only | No | No | No | N/A | 1 position | - | 1 hour | N/A | N/A | Dual Pricing | N/A | N/A | Marginal Control Energy Price | Average Control Energy Price | N/A | N/A | N/A | N/A | Variable component | Yes | TSO is not using this type of product | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | No | x <= 1 day after delivery | 9 < x <= 12 weeks | 1 hour before delivery | 1 hour | Never (GCT before delivery) | No changes
Denmark | Energinet.dk IPC | Financial only | N/A | N/A | N/A | N/A | 2 positions – separate positions for generation and consumption | - | N/A | 1 hour | 1 hour | N/A | Dual Pricing | Single Pricing | N/A | N/A | Marginal Control Energy Price | Marginal Control Energy Price | Day-Ahead Market Price | Marginal Control Energy Price | N/A | Yes | This product is not used in settlement price calculation | This product is not used in settlement price calculation | This product is used in settlement price calculation | This product is not used in settlement price calculation | No | x <= 1 hour after delivery | x <= 3 weeks | 45 min before delivery | 1 hour | Never (GCT before delivery) | No changes
Estonia | Elering | Legal+financial | No | No | No | N/A | 1 position | - | 1 hour | N/A | N/A | Single Pricing | N/A | N/A | Marginal Control Energy Price | Marginal Control Energy Price | N/A | N/A | N/A | N/A | Variable component | No | TSO is not using this type of product | TSO is not using this type of product | This product is used in settlement price calculation | TSO is not using this type of product | No | x > 1 week after delivery | 9 < x <= 12 weeks | 30 min before delivery | 30 min | Only in case of IT or any other problems (TSO approval) | Only minor changes
Finland | Fingrid | Legal+financial | No | No | No | N/A | 2 positions – separate positions for generation and consumption | - | N/A | 1 hour | 1 hour | N/A | Dual Pricing | Single Pricing | N/A | N/A | Marginal Control Energy Price | Marginal Control Energy Price | Day-Ahead Market Price | Marginal Control Energy Price | Constant component | Yes | This product is not used in settlement price calculation | This product is not used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | Yes | x > 1 week after delivery | 3 < x <= 6 weeks | 1 hour before delivery | 1 hour | Never (GCT before delivery) | No changes
France | RTE | Financial only | Yes | No | No | No limit | 1 position | - | 30 min | N/A | N/A | Single Pricing | N/A | N/A | Average Control Energy Price | Average Control Energy Price | N/A | N/A | N/A | N/A | Constant component | No | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | No | x <= 1 hour after delivery | x > 12 weeks | 15 min before delivery | 1 hour | Only in case of IT or any other problems (TSO approval) | Only minor changes
Germany | 50Hertz | Legal+financial | N/A | N/A | N/A | N/A | 1 position | - | 15 min | N/A | N/A | Single Pricing | N/A | N/A | Average Control Energy Price | Average Control Energy Price | N/A | N/A | N/A | N/A | Variable component | Yes | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | No | x > 1 week after delivery | x > 12 weeks | 15 min before delivery | 15 min | Always (GCT after delivery) | Yes
| Amprion | Legal+financial | N/A | N/A | N/A | N/A | 1 position | - | 15 min | N/A | N/A | Single Pricing | N/A | N/A | Average Control Energy Price | Average Control Energy Price | N/A | N/A | N/A | N/A | Variable component | Yes | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | No | x > 1 week after delivery | x > 12 weeks | 15 min before delivery | 15 min | Always (GCT after delivery) | Yes
| TransnetBW | Legal+financial | N/A | N/A | N/A | N/A | 1 position | - | 15 min | N/A | N/A | Single Pricing | N/A | N/A | Average Control Energy Price | Average Control Energy Price | N/A | N/A | N/A | N/A | Variable component | Yes | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | No | x > 1 week after delivery | x > 12 weeks | 15 min before delivery | 15 min | Always (GCT after delivery) | Yes
| Tennet Germany | Legal+financial | N/A | N/A | N/A | N/A | 1 position | - | 15 min | N/A | N/A | Single Pricing | N/A | N/A | Average Control Energy Price | Average Control Energy Price | N/A | N/A | N/A | N/A | Variable component | Yes | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | No | x > 1 week after delivery | x > 12 weeks | 15 min before delivery | 15 min | Always (GCT after delivery) | Yes
Greece | ADMIE | Legal+financial | Yes | No | No | No limit | > 2 positions | 1 position for consumption Several positions for generation (one per generation unit) 1 position for imports 1 position for exports | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Yes | This product is not used in settlement price calculation | This product is not used in settlement price calculation | This product is not used in settlement price calculation | This product is not used in settlement price calculation | Yes | x > 1 week after delivery | x <= 3 weeks | N/A | N/A | Never (GCT before delivery) | No changes
Hungary | MAVIR | Legal+financial | Yes | No | No | Other | 1 position | - | 15 min | N/A | N/A | Dual Pricing | N/A | N/A | Average Control Energy Price | Day-Ahead Market Price | N/A | N/A | N/A | N/A | Variable component | Yes | This product is used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | This product is used in settlement price calculation | Yes | x > 1 week after delivery | 3 < x <= 6 weeks | 1 hour before delivery | 15 min | Only in case of IT or any other problems (TSO approval) | No changes
Ireland | EirGrid | Financial only | N/A | N/A | N/A | N/A | 1 position | - | 30 min | N/A | N/A | Single Pricing | N/A | N/A | Marginal Control Energy Price | Marginal Control Energy Price | N/A | N/A | N/A | N/A | Variable component | No | This product is not used in settlement price calculation | TSO is not using this type of product | This product is used in settlement price calculation | TSO is not using this type of product | No | x <= 1 hour after delivery | x > 12 weeks | 1 hour before delivery | 30 min | Never (GCT before delivery) | No changes
Italy | Terna | Financial only | N/A | N/A | N/A | N/A | > 2 positions | In Italy we calculate an imbalance volume for each production or consumption unit | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Variable component | No | This product is not used in settlement price calculation | This product is not used in settlement price calculation | This product is not used in settlement price calculation | This product is not used in settlement price calculation | No | x <= 1 day after delivery | x > 12 weeks | N/A | 1 hour | Never (GCT before delivery) | No changes
Latvia | AST | Financial only | No | No | No | N/A | 1 position | - | 1 hour | N/A | N/A | Single Pricing | N/A | N/A | Marginal Control Energy Price | Marginal Control Energy Price | N/A | N/A | N/A | N/A | Variable component | Yes | TSO is not using this type of product | TSO is not using this type of product | This product is used in settlement price calculation | TSO is not using this type of product | No | x > 1 week after delivery | x > 12 weeks | 45 min before delivery | 1 hour | Never (GCT before delivery) | Yes
Lithuania | LITGRID | Legal+financial | Yes | No | No | Other | 1 position | - | 1 hour | N/A | N/A | Single Pricing | N/A | N/A | Marginal Control Energy Price | Marginal Control Energy Price | N/A | N/A | N/A | N/A | Variable component | Yes | TSO is not using this type of product | TSO is not using this type of product | This product is used in settlement price calculation | TSO is not using this type of product | No | x > 1 week after delivery | x <= 3 weeks | 45 min before delivery | 1 hour | Only in case of IT or any other problems (TSO approval) | No changes
Luxembourg | CREOS | Legal+financial | No | No | No | N/A | 1 position | - | 15 min | N/A | N/A | Single Pricing | N/A | N/A | Average Control Energy Price | Average Control Energy Price | N/A | N/A | N/A | N/A | Variable component | No | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | No | x > 1 week after delivery | x > 12 weeks | 45 min before delivery | 15 min | Never (GCT before delivery) | N/A
Malta | Enemalta | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Netherlands | TenneT NL | Legal+financial | No | No | No | N/A | 1 position | - | 15 min | N/A | N/A | Single Pricing | N/A | N/A | Marginal Control Energy Price | Marginal Control Energy Price | N/A | N/A | N/A | N/A | N/A | N/A | This product is not used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | No | x <= 1 hour after delivery | x <= 3 weeks | Ex-post notification allowed | 15 min | Always (GCT after delivery) | No changes
Poland | PSE | Financial only | N/A | N/A | N/A | N/A | 1 position | - | 1 hour | N/A | N/A | Dual Pricing | N/A | N/A | Marginal Control Energy Price | Marginal Control Energy Price | N/A | N/A | N/A | N/A | N/A | No | This product is used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | This product is used in settlement price calculation | No | x <= 1 day after delivery | x > 12 weeks | 1 hour before delivery | 1 hour | Never (GCT before delivery) | No changes
Portugal | REN | Financial only | N/A | N/A | N/A | No limit | > 2 positions | For generation the imbalance is calculated by imbalance area. A market player can have more than one imbalance area | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Other | Yes | This product is not used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | No | x > 1 week after delivery | 9 < x <= 12 weeks | 1 hour before delivery | 1 hour | Never (GCT before delivery) | No changes
Romania | Transelectrica | Legal+financial | N/A | N/A | N/A | N/A | 1 position | - | 1 hour | N/A | N/A | Dual Pricing | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Variable component | N/A | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | Yes | N/A | x > 12 weeks | N/A | N/A | Never (GCT before delivery) | No changes
Slovakia | SEPS | Financial only | Yes | No | No | x <= 1MW | 1 position | - | 15 min | N/A | N/A | Single Pricing | N/A | N/A | Marginal Control Energy Price | Marginal Control Energy Price | N/A | N/A | N/A | N/A | N/A | Yes | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | No | x > 1 week after delivery | 3 < x <= 6 weeks | 1 hour before delivery | 1 hour | Never (GCT before delivery) | No changes
Slovenia | ELES | Financial only | No | No | No | N/A | 1 position | - | 1 hour | N/A | N/A | Dual Pricing | N/A | N/A | Average Control Energy Price | Day-Ahead Market Price | N/A | N/A | N/A | N/A | Variable component | Yes | This product is not used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | No | x > 1 week after delivery | x > 12 weeks | Ex-post notification allowed | 1 hour | N/A | No changes
Spain | REE | Financial only | No | No | No | No limit | 2 positions – separate positions for generation and consumption | - | N/A | 1 hour | 1 hour | N/A | Dual Pricing | Dual Pricing | N/A | N/A | Average Control Energy Price | Average Control Energy Price | Day-Ahead Market Price | Day-Ahead Market Price | Variable component | No | TSO is not using this type of product | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | No | x <= 1 day after delivery | x > 12 weeks | 1 hour before delivery | 1 hour | Never (GCT before delivery) | Yes
Sweden | SVENSKA KRAFTNÄT | Legal+financial | N/A | N/A | N/A | N/A | 2 positions – separate positions for generation and consumption | - | N/A | 1 hour | 1 hour | N/A | Dual Pricing | Single Pricing | N/A | N/A | Marginal Control Energy Price | Marginal Control Energy Price | Day-Ahead Market Price | Marginal Control Energy Price | Constant component | Yes | This product is not used in settlement price calculation | This product is not used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | Yes | x <= 1 week after delivery | x <= 3 weeks | 45 min before delivery | 1 hour | Only in case of IT or any other problems (TSO approval) | No changes
GB/United Kingdom | National Grid | Financial only | N/A | N/A | N/A | N/A | 1 position | - | 30 min | N/A | N/A | Single Pricing | N/A | N/A | Average Control Energy Price | Average Control Energy Price | N/A | N/A | N/A | N/A | Variable component | No | This product is not used in settlement price calculation | TSO is not using this type of product | This product is used in settlement price calculation | This product is used in settlement price calculation | Yes | x <= 1 hour after delivery | x > 12 weeks | 1 hour before delivery | 1 hour | Never (GCT before delivery) | No changes
| SHETL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| SPTransmission | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
> Northern Ireland | SONI | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Croatia | HOPS | Legal+financial | Yes | Yes | No | No limit | 1 position | - | 1 hour | N/A | N/A | Single Pricing | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No | TSO is not using this type of product | This product is used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | No | x > 1 week after delivery | 3 < x <= 6 weeks | 15 min before delivery | 1 hour | Never (GCT before delivery) | No changes
Iceland | Landsnet | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Montenegro | Crnogorski elektroprenosni sistem AD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Serbia | EMS | Legal+financial | No | No | No | N/A | 1 position | - | 1 hour | N/A | N/A | Single Pricing | N/A | N/A | Average Control Energy Price | Average Control Energy Price | N/A | N/A | N/A | N/A | N/A | Yes | TSO is not using this type of product | This product is not used in settlement price calculation | This product is not used in settlement price calculation | This product is not used in settlement price calculation | No | x > 1 week after delivery | x > 12 weeks | 1 hour before delivery | 1 hour | Never (GCT before delivery) | Yes
The former Yugoslav Republic of Macedonia | MEPSO | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Turkey | TEIAS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Albania | OST | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Bosnia and Herzegovina | ISO BIH | Legal+financial | No | No | No | No limit | 1 position | - | 1 hour | N/A | N/A | Dual Pricing | N/A | N/A | Other | N/A | N/A | N/A | N/A | N/A | Other | No | This product is not used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | No | x <= 1 day after delivery | x <= 3 weeks | 45 min before delivery | 1 hour | Never (GCT before delivery) | No changes
Kosovo (UNMIK) | KOSTT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Moldova | Moldelectrica | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Ukraine | Ukrenergo | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Norway | Statnett | Legal+financial | N/A | N/A | N/A | N/A | 2 positions – separate positions for generation and consumption | - | N/A | 1 hour | 1 hour | N/A | Dual Pricing | Single Pricing | N/A | N/A | Marginal Control Energy Price | Marginal Control Energy Price | Day-Ahead Market Price | Marginal Control Energy Price | Constant component | Yes | This product is not used in settlement price calculation | This product is not used in settlement price calculation | This product is used in settlement price calculation | TSO is not using this type of product | No | x <= 1 week after delivery | x <= 3 weeks | 45 min before delivery | 1 hour | Never (GCT before delivery) | No changes
Switzerland | Swissgrid | Legal+financial | N/A | N/A | N/A | N/A | 1 position | - | 15 min | N/A | N/A | Dual Pricing | N/A | N/A | Other | Other | N/A | N/A | N/A | N/A | Variable component | Yes | TSO is not using this type of product | This product is used in settlement price calculation | This product is used in settlement price calculation | This product is used in settlement price calculation | No | x > 1 week after delivery | x > 12 weeks | Ex-post notification allowed | 15 min | Always (GCT after delivery) | No changes
Monaco |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
San Marino |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Andorra | FEDA/RTE/REE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Vatican City |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Liechtenstein | LKW | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Belarus |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## Ancillary Services
|  | AS1.0 | AS1.1 | AS2.1 | AS2.2 | AS1.3 | AS2.3 | AS2.4 | AS1.5 | AS2.5 | AS2.6 | AS1.7 | AS2.7 | AS2.8 | AS3.4 | AS3.6 | AS3.8 | AS4.1 | AS4.2 | AS4.3 | AS4.4 | AS4.5 | AS4.6 | AS4.7 | AS4.8 | AS5.1 | AS5.2 | AS5.3 | AS5.4 | AS5.5 | AS5.6 | AS5.7 | AS5.8 | AS6.1 | AS6.2 | AS6.3 | AS6.4 | AS6.5 | AS6.6 | AS6.7 | AS6.8 | AS7.1 | AS7.2 | AS7.3 | AS7.4 | AS7.5 | AS7.6 | AS7.7 | AS7.8 | AS8.1 | AS8.3 | AS8.5 | AS9.1 | AS9.2 | AS9.3 | AS9.4 | AS9.5 | AS9.6 | AS9.7 | AS9.8 | AS10.1 | AS10.2 | AS10.3 | AS10.4 | AS10.5 | AS10.6 | AS10.7 | AS10.8 | AS11.1 | AS11.2 | AS11.3 | AS11.4 | AS11.5 | AS11.6 | AS11.7 | AS11.8 | AS12.1 | AS12.2 | AS12.3 | AS12.4 | AS12.5 | AS12.6 | AS12.7 | AS12.8 | AS13.1 | AS13.2 | AS13.3 | AS13.4 | AS13.5 | AS13.6 | AS13.7 | AS13.8 | AS14.6 | AS14.8 | AS15.8 | AS15.4 | AS15.6 | AS16.2 | AS16.4 | AS16.6 | AS16.8 | AS17.4 | AS17.6 | AS17.8 | AS18.0
AS Survey 2018 |  |  | Frequency Containment Reserve |  |  | Frequency Restoration Reserve (Automatic) |  |  | Frequency Restoration Reserve (Manual) |  |  | Replacement Reserve |  |  | Frequency Restoration Reserve (Automatic) | Frequency Restoration Reserve (Manual) | Replacement Reserve | Frequency Containment Reserve |  | Frequency Restoration Reserve (Automatic) |  | Frequency Restoration Reserve (Manual) |  | Replacement Reserve |  | Frequency Containment Reserve |  | Frequency Restoration Reserve (Automatic) |  | Frequency Restoration Reserve (Manual) |  | Replacement Reserve |  | Frequency Containment Reserve |  | Frequency Restoration Reserve (Automatic) |  | Frequency Restoration Reserve (Manual) |  | Replacement Reserve |  | Frequency Containment Reserve |  | Frequency Restoration Reserve (Automatic) |  | Frequency Restoration Reserve (Manual) |  | Replacement Reserve |  | Frequency Containment Reserve | Frequency Restoration Reserve (Automatic) | Frequency Restoration Reserve (Manual) | Frequency Containment Reserve |  | Frequency Restoration Reserve (Automatic) |  | Frequency Restoration Reserve (Manual) |  | Replacement Reserve |  | Frequency Containment Reserve |  | Frequency Restoration Reserve (Automatic) |  | Frequency Restoration Reserve (Manual) |  | Replacement Reserve |  | Frequency Containment Reserve |  | Frequency Restoration Reserve (Automatic) |  | Frequency Restoration Reserve (Manual) |  | Replacement Reserve |  | Frequency Containment Reserve |  | Frequency Restoration Reserve (Automatic) |  | Frequency Restoration Reserve (Manual) |  | Replacement Reserve |  | Frequency Containment Reserve |  | Frequency Restoration Reserve (Automatic) |  | Frequency Restoration Reserve (Manual) |  | Replacement Reserve |  | Frequency Restoration Reserve (Manual) | Replacement Reserve | Replacement Reserve | Frequency Restoration Reserve (Automatic) | Frequency Restoration Reserve (Manual) | Frequency Containment Reserve | Frequency Restoration Reserve (Automatic) | Frequency Restoration Reserve (Manual) | Replacement Reserve | Frequency Restoration Reserve (Automatic) | Frequency Restoration Reserve (Manual) | Replacement Reserve | Changes?
|  |  | Procurement scheme | [11 empty] | Activation rule |  |  | Product Resolution (in MW) | [7 empty] | Product Resolution (in time) | [7 empty] | Distance to real time of reserve products auctions/Distance to real time of energy products | [7 empty] | Provider | [7 empty] | Symmetrical product |  |  | Settlement Rule | [7 empty] | Cost recovery scheme | [7 empty] | Monitoring | [7 empty] | Transfer of BSPs obligation allowed? | [7 empty] | In case transfer obligation is allowed, is there an organised secondary market? | [7 empty] | Can offered products be partially activated? |  |  |  |  | Free Bids allowed? |  |  |  | Are activations possible for other purposes than for balancing?
Country | TSO Name | What is the balancing process in place? | Capacity | Capacity | Energy | Capacity | Capacity | Energy | Capacity | Capacity | Energy | Capacity | Capacity | Energy | Energy | Energy | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Capacity | Capacity | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Capacity | Energy | Energy | Energy | What is the activation time of RR from 0 to max? | What is the activation time of FRRa from 0 to max? | What is the activation time of FRRm from 0 to max? | Energy | Energy | Energy | Energy | Energy | Energy | Energy | Do you consider changes significant/important regarding the ancillary sevices?
Austria | APG | Self-Dispatch - Portfolio Based | Yes | Market only | N/A | Yes | Market only | Market only | Yes | Market only | Market only | No | N/A | N/A | Merit order | Merit order | N/A | x <= 1MW | N/A | 1MW < x <= 5 MW | 1MW < x <= 5 MW | x <= 1MW | x <= 1MW | N/A | N/A | Week(s) | N/A | Hour(s) | Hour (or blocks) | Hour(s) | Hour (or blocks) | N/A | N/A | Day(s) | N/A | Day(s) | x <= 1 minute | Day(s) | 5 minutes < x <= 15 minutes | N/A | N/A | Generators Only | N/A | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | N/A | N/A | Has to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | Pay as bid | N/A | Pay as bid | Pay as bid | Pay as bid | Pay as bid | N/A | N/A | N/A | N/A | Hybrid | Hybrid | Hybrid | Hybrid | N/A | N/A | Ex-Post Check | N/A | Ex-Post Check | Ex-Post Check | Ex-Post Check | Ex-Post Check | N/A | N/A | Yes | No | Yes | Yes | Yes | Yes | N/A | N/A | No | No | No | No | No | No | N/A | N/A | No in none direction | N/A | N/A | 90s < x <= 5 min | 5min < x <= 15 min | No | No | No | N/A | No | No | N/A | N/A
| VUEN | Self-Dispatch - Portfolio Based | Yes | Market only | N/A | Yes | Market only | Market only | Yes | Market only | Market only | No | N/A | N/A | Merit order | Merit order | N/A | x <= 1MW | N/A | 1MW < x <= 5 MW | 1MW < x <= 5 MW | x <= 1MW | x <= 1MW | N/A | N/A | Week(s) | N/A | Hour(s) | Hour (or blocks) | Hour(s) | Hour (or blocks) | N/A | N/A | Day(s) | N/A | Day(s) | x <= 1 minute | Day(s) | 5 minutes < x <= 15 minutes | N/A | N/A | Generators Only | N/A | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | N/A | N/A | Has to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | Pay as bid | N/A | Pay as bid | Pay as bid | Pay as bid | Pay as bid | N/A | N/A | N/A | N/A | Hybrid | Hybrid | Hybrid | Hybrid | N/A | N/A | Ex-Post Check | N/A | Ex-Post Check | Ex-Post Check | Ex-Post Check | Ex-Post Check | N/A | N/A | Yes | No | Yes | Yes | Yes | Yes | N/A | N/A | No | No | No | No | No | No | N/A | N/A | No in none direction | N/A | N/A | 90s < x <= 5 min | 5min < x <= 15 min | No | No | No | N/A | No | No | N/A | N/A
Belgium | Elia | Self-Dispatch - Unit Based | Yes | Market only | N/A | Yes | Market only | Market only | Yes | Market only | Market only | No | N/A | N/A | Pro Rata (Parallel Activation) | Merit order | N/A | x <= 1MW | N/A | x <= 1MW | x <= 1MW | x <= 1MW | x <= 1MW | N/A | N/A | Week(s) | N/A | Week(s) | 15 minutes | Month(s) | 15 minutes | N/A | N/A | Week(s) | N/A | Week(s) | x <= 1 minute | Month(s) | x <= 1 minute | N/A | N/A | Generators + Load + Pump Storage + Batteries | N/A | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | N/A | N/A | Don't need to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | Pay as bid | N/A | Pay as bid | Pay as bid | Pay as bid | Pay as bid | N/A | N/A | 100% Grid Users (through tariff) | N/A | 100% Grid Users (through tariff) | 100% Grid Users (through tariff) | 100% Grid Users (through tariff) | 100% Grid Users (through tariff) | N/A | N/A | Ex-Post Check | Ex-Post Check | Ex-Post Check | Ex-Post Check | Ex-Post Check | Ex-Post Check | N/A | N/A | Yes | No | Yes | Yes | Yes | Yes | N/A | N/A | Yes | No | No | Yes | Yes | Yes | N/A | N/A | Yes, in all directions | N/A | N/A | 5min < x <= 15 min | 5min < x <= 15 min | No | Yes | Yes | N/A | No | Yes | N/A | N/A
Bulgaria | ESO | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Cyprus | TSO-Cyprus | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Czech Republic | CEPS | Self-Dispatch - Unit Based | Yes | Market only | N/A | Yes | Market only | Market only | Yes | Market only | Market only | No | N/A | N/A | Pro Rata (Parallel Activation) | Merit order | N/A | 1MW < x <= 5 MW | N/A | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | N/A | N/A | Hour(s) | N/A | Hour(s) | N/A | Hour(s) | Hour (or blocks) | N/A | N/A | Year or more + Month(s) + Day(s) | N/A | Year or more + Month(s) + Day(s) | x <= 1 minute | Year or more + Month(s) + Day(s) | 5 minutes < x <= 15 minutes | N/A | N/A | Generators Only | N/A | Generators + Load | Generators + Load | Generators + Load + Pump Storage | Generators + Load + Pump Storage | N/A | N/A | Has to be symmetrical | Has to be symmetrical | Don't need to be symmetrical | Pay as bid | N/A | Pay as bid | Regulated Price | Pay as bid | Pay as bid | N/A | N/A | 100% Grid Users (through tariff) | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | Hybrid | N/A | Hybrid | Hybrid | Hybrid | Hybrid | N/A | N/A | Yes | No | Yes | N/A | Yes | N/A | N/A | N/A | No | No | No | N/A | No | N/A | N/A | N/A | No in none direction | N/A | N/A | 5min < x <= 15 min | 5min < x <= 15 min | No | No | No | N/A | No | No | N/A | N/A
Denmark | Energinet.dk IPC | Self-Dispatch - Portfolio Based | Yes | Market only | N/A | Yes | Hybrid | Hybrid | Yes | Market only | Market only | No | N/A | N/A | Pro Rata (Parallel Activation) | Merit order | N/A | x <= 1MW | N/A | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 5 MW < x <= 10 MW | 5 MW < x <= 10 MW | N/A | N/A | Hour(s) | N/A | Month(s) | Hour (or blocks) | Hour(s) | Hour (or blocks) | N/A | N/A | Day(s) | N/A | Month(s) + Day(s) | 5 minutes < x <= 15 minutes | Day(s) | 5 minutes < x <= 15 minutes | N/A | N/A | Generators + Load + Batteries | N/A | Generators + Load | Generators + Load | Generators + Load | Generators + Load | N/A | N/A | Don't need to be symmetrical | Has to be symmetrical | Don't need to be symmetrical | Marginal Pricing | N/A | Pay as bid | Regulated Price | Marginal Pricing | Marginal Pricing | N/A | N/A | 100% Grid Users (through tariff) | N/A | 100% Grid Users (through tariff) | 100% Grid Users (through tariff) | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | Ex-Post Check | N/A | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | N/A | N/A | No | No | No | No | No | No | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 5min < x <= 15 min | 5min < x <= 15 min | No | Yes | Yes | N/A | No | Yes | N/A | N/A
Estonia | Elering | Self-Dispatch - Portfolio Based | No | N/A | N/A | No | N/A | N/A | Yes | N/A | Market only | No | N/A | N/A | N/A | Merit order | N/A | N/A | N/A | N/A | N/A | N/A | x <= 1MW | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Hour (or blocks) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 15 minutes < x <= H-1 | N/A | N/A | N/A | N/A | N/A | N/A | Generators Only | Generators + Load | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Marginal Pricing | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 100% BRP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Hybrid | N/A | N/A | N/A | N/A | N/A | N/A | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No | N/A | N/A | Yes, in all directions | N/A | N/A | N/A | 5min < x <= 15 min | N/A | N/A | Yes | N/A | N/A | Yes | N/A | N/A
Finland | Fingrid | Self-Dispatch - Portfolio Based | Yes | Market only | N/A | Yes | Market only | N/A | Yes | Market only | Market only | No | N/A | N/A | Pro Rata (Parallel Activation) | Merit order | N/A | x <= 1MW | N/A | 1MW < x <= 5 MW | N/A | 1MW < x <= 5 MW | 1MW < x <= 5 MW | N/A | N/A | Hour(s) | N/A | Hour(s) | N/A | Week(s) | Hour (or blocks) | N/A | N/A | Day(s) | N/A | Day(s) | N/A | Week(s) | 5 minutes < x <= 15 minutes | N/A | N/A | Generators + Load + Batteries | Generators + Load + Batteries | Generators Only | Generators Only | Generators + Load | Generators + Load | N/A | N/A | Has to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | Marginal Pricing | Marginal Pricing | Pay as bid | Marginal Pricing | Pay as bid | Marginal Pricing | N/A | N/A | Hybrid | 100% BRP | 100% BRP | 100% BRP | Hybrid | 100% BRP | N/A | N/A | Hybrid | N/A | Hybrid | Hybrid | Hybrid | Real-Time Monitoring | N/A | N/A | No | No | No | No | No | No | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 90s < x <= 5 min | 5min < x <= 15 min | No | No | Yes | N/A | Yes | Yes | N/A | N/A
France | RTE | Self-Dispatch - Unit Based | Yes | Mandatory only | N/A | Yes | Hybrid | Mandatory only | Yes | Market only | Market only | Yes | Market only | Market only | Pro Rata (Parallel Activation) | Merit order | Merit order | x <= 1MW | No minimum bid size | x <= 1MW | No minimum bid size | 5 MW < x <= 10 MW | x <= 1MW | 5 MW < x <= 10 MW | x <= 1MW | Week(s) | 30 minutes | Hour(s) | 30 minutes | Week(s) | 30 minutes | Week(s) | 15 minutes | Week(s) | x <= H-1 | Day(s) | 15 minutes < x <= H-1 | Year or more | 15 minutes < x <= H-1 | Year or more | 15 minutes < x <= H-1 | Generators + Load + Pump Storage + Batteries | Generators + Load + Pump Storage + Batteries | Generators + Pump Storage | Generators + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Don't need to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | Pay as bid | Regulated Price | Regulated Price | N/A | Marginal Pricing | Pay as bid | Marginal Pricing | Marginal Pricing | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | Hybrid | Hybrid | Hybrid | Hybrid | Ex-Post Check | Ex-Post Check | Ex-Post Check | Ex-Post Check | Yes | No | Yes | No | Yes | No | Yes | No | No | No | No | No | No | No | No | No | Yes, in all directions | Yes, in all directions | N/A | 5min < x <= 15 min | 5min < x <= 15 min | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes
Germany | 50Hertz | Self-Dispatch - Portfolio Based | Yes | Market only | N/A | Yes | Market only | Market only | Yes | Market only | Market only | No | N/A | N/A | Merit order | Merit order | N/A | x <= 1MW | N/A | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | N/A | N/A | Week(s) | N/A | Hour(s) | Hour (or blocks) | Hour(s) | Hour (or blocks) | N/A | N/A | Day(s) | N/A | Day(s) | x <= 1 minute | Day(s) | 5 minutes < x <= 15 minutes | N/A | N/A | Generators + Load + Pump Storage + Batteries | N/A | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | N/A | N/A | Has to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | Pay as bid | N/A | Pay as bid | Pay as bid | Pay as bid | Pay as bid | N/A | N/A | 100% Grid Users (through tariff) | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | Real-Time Monitoring | N/A | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | N/A | N/A | Yes | Yes | Yes | Yes | Yes | Yes | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 90s < x <= 5 min | 5min < x <= 15 min | No | No | No | N/A | No | No | N/A | N/A
| Amprion | Self-Dispatch - Portfolio Based | Yes | Market only | N/A | Yes | Market only | Market only | Yes | Market only | Market only | No | N/A | N/A | Merit order | Merit order | N/A | x <= 1MW | N/A | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | N/A | N/A | Week(s) | N/A | Hour(s) | Hour (or blocks) | Hour(s) | Hour (or blocks) | N/A | N/A | Day(s) | N/A | Day(s) | x <= 1 minute | Day(s) | 5 minutes < x <= 15 minutes | N/A | N/A | Generators + Load + Pump Storage + Batteries | N/A | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | N/A | N/A | Has to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | Pay as bid | N/A | Pay as bid | Pay as bid | Pay as bid | Pay as bid | N/A | N/A | 100% Grid Users (through tariff) | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | Real-Time Monitoring | N/A | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | N/A | N/A | Yes | Yes | Yes | Yes | Yes | Yes | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 90s < x <= 5 min | 5min < x <= 15 min | No | No | No | N/A | No | No | N/A | N/A
| TransnetBW | Self-Dispatch - Portfolio Based | Yes | Market only | N/A | Yes | Market only | Market only | Yes | Market only | Market only | No | N/A | N/A | Merit order | Merit order | N/A | x <= 1MW | N/A | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | N/A | N/A | Week(s) | N/A | Hour(s) | Hour (or blocks) | Hour(s) | Hour (or blocks) | N/A | N/A | Day(s) | N/A | Day(s) | x <= 1 minute | Day(s) | 5 minutes < x <= 15 minutes | N/A | N/A | Generators + Load + Pump Storage + Batteries | N/A | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | N/A | N/A | Has to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | Pay as bid | N/A | Pay as bid | Pay as bid | Pay as bid | Pay as bid | N/A | N/A | 100% Grid Users (through tariff) | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | Real-Time Monitoring | N/A | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | N/A | N/A | Yes | Yes | Yes | Yes | Yes | Yes | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 90s < x <= 5 min | 5min < x <= 15 min | No | No | No | N/A | No | No | N/A | N/A
| Tennet Germany | Self-Dispatch - Portfolio Based | Yes | Market only | N/A | Yes | Market only | Market only | Yes | Market only | Market only | No | N/A | N/A | Merit order | Merit order | N/A | x <= 1MW | N/A | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | N/A | N/A | Week(s) | N/A | Hour(s) | Hour (or blocks) | Hour(s) | Hour (or blocks) | N/A | N/A | Day(s) | N/A | Day(s) | x <= 1 minute | Day(s) | 5 minutes < x <= 15 minutes | N/A | N/A | Generators + Load + Pump Storage + Batteries | N/A | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | N/A | N/A | Has to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | Pay as bid | N/A | Pay as bid | Pay as bid | Pay as bid | Pay as bid | N/A | N/A | 100% Grid Users (through tariff) | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | Real-Time Monitoring | N/A | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | N/A | N/A | Yes | Yes | Yes | Yes | Yes | Yes | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 90s < x <= 5 min | 5min < x <= 15 min | No | No | No | N/A | No | No | N/A | N/A
Greece | ADMIE | Central Dispatch | Yes | Market only | N/A | Yes | Market only | Hybrid | Yes | Mandatory only | N/A | No | N/A | N/A | Pro Rata (Parallel Activation) | Merit order | N/A | x <= 1MW | N/A | x <= 1MW | N/A | x <= 1MW | N/A | N/A | N/A | Hour(s) | N/A | Hour(s) | N/A | Hour(s) | N/A | N/A | N/A | Day(s) | N/A | Day(s) | N/A | N/A | N/A | N/A | N/A | Generators Only | Generators Only | Generators Only | Generators Only | Generators Only | Generators Only | N/A | N/A | Don't need to be symmetrical | Don't need to be symmetrical | N/A | Marginal Pricing | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 100% BRP | N/A | N/A | N/A | N/A | N/A | Hybrid | Ex-Post Check | Hybrid | Hybrid | Hybrid | Hybrid | N/A | N/A | No | No | No | No | No | No | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | N/A | N/A | Yes | Yes | Yes | N/A | No | Yes | N/A | N/A
Hungary | MAVIR | Self-Dispatch - Portfolio Based | Yes | Mandatory only | N/A | Yes | Mandatory only | Market only | No | N/A | N/A | Yes | Mandatory only | Market only | Merit order | N/A | Merit order | x <= 1MW | N/A | x <= 1MW | x <= 1MW | N/A | N/A | x <= 1MW | x <= 1MW | Hour(s) | N/A | Hour(s) | Hour (or blocks) | N/A | N/A | Hour(s) | Hour (or blocks) | Day(s) | N/A | Day(s) | x <= 1 minute | N/A | N/A | Day(s) | Depends on the unit | Generators + Batteries | N/A | Generators Only | Generators Only | N/A | N/A | Generators + Load | Generators + Load | Has to be symmetrical | Don't need to be symmetrical | N/A | Pay as bid | N/A | Pay as bid | Pay as bid | N/A | N/A | Pay as bid | Pay as bid | 100% Grid Users (through tariff) | N/A | 100% Grid Users (through tariff) | Hybrid | N/A | N/A | 100% Grid Users (through tariff) | Hybrid | Ex-Post Check | N/A | Real-Time Monitoring | Real-Time Monitoring | N/A | N/A | Ex-Post Check | Ex-Post Check | Yes | No | Yes | No | N/A | N/A | Yes | No | Yes | No | Yes | No | N/A | N/A | Yes | No | N/A | Yes, in all directions | Depends on the unit | 5min < x <= 15 min | N/A | No | Yes | N/A | Yes | Yes | N/A | Yes | Only minor changes
Ireland | EirGrid | Central Dispatch | Yes | Hybrid | Hybrid | No | N/A | N/A | Yes | Hybrid | Market only | No | N/A | N/A | N/A | Merit order | N/A | x <= 1MW | x <= 1MW | N/A | N/A | x <= 1MW | x <= 1MW | N/A | N/A | N/A | 30 minutes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Depends on the unit | N/A | N/A | Generators + Load + Pump Storage + Batteries | Generators + Load + Pump Storage + Batteries | N/A | N/A | Generators + Load + Pump Storage + Batteries | Generators + Load + Pump Storage + Batteries | N/A | N/A | N/A | N/A | Don't need to be symmetrical | N/A | Hybrid | N/A | N/A | Regulated Price | Hybrid | N/A | N/A | 100% Grid Users (through tariff) | 100% Grid Users (through tariff) | N/A | N/A | 100% Grid Users (through tariff) | 100% Grid Users (through tariff) | N/A | N/A | Hybrid | Hybrid | N/A | N/A | Hybrid | Hybrid | N/A | N/A | No | No | N/A | N/A | No | No | N/A | N/A | No | No | N/A | N/A | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | N/A | Depends on the unit | No | N/A | Yes | N/A | N/A | Yes | N/A | N/A
Italy | Terna | Central Dispatch | Yes | Mandatory only | Mandatory only | Yes | N/A | Hybrid | Yes | N/A | Hybrid | Yes | N/A | Hybrid | Pro Rata (Parallel Activation) | Merit order | Merit order | No minimum bid size | N/A | N/A | x <= 1MW | N/A | x <= 1MW | N/A | x <= 1MW | N/A | N/A | N/A | Hour (or blocks) | N/A | Hour (or blocks) | N/A | Hour (or blocks) | N/A | N/A | N/A | x <= 1 minute | N/A | 5 minutes < x <= 15 minutes | N/A | x > H-1 | Generators Only | Generators Only | N/A | Generators Only | N/A | Generators + Pump Storage | N/A | Generators + Load + Pump Storage | Has to be symmetrical | N/A | N/A | N/A | Regulated Price | N/A | Pay as bid | N/A | N/A | N/A | Pay as bid | N/A | N/A | N/A | 100% Grid Users (through tariff) | N/A | N/A | N/A | 100% Grid Users (through tariff) | N/A | N/A | N/A | Real-Time Monitoring | N/A | N/A | N/A | Real-Time Monitoring | No | No | No | No | No | No | Yes | No | No | No | No | No | No | No | No | No | Yes, in all directions | Yes, in all directions | x > 1 hour | 5min < x <= 15 min | 5min < x <= 15 min | No | Yes | N/A | Yes | No | Yes | Yes | No changes
Latvia | AST | Self-Dispatch - Portfolio Based | No | N/A | N/A | No | N/A | N/A | Yes | Market only | Market only | No | N/A | N/A | N/A | Merit order | N/A | N/A | N/A | N/A | N/A | No minimum bid size | x <= 1MW | N/A | N/A | N/A | N/A | N/A | N/A | Year or more | Hour (or blocks) | N/A | N/A | N/A | N/A | N/A | N/A | Year or more | 15 minutes < x <= H-1 | N/A | N/A | N/A | N/A | N/A | N/A | Generators Only | Generators Only | N/A | N/A | N/A | N/A | Don't need to be symmetrical | N/A | N/A | N/A | N/A | Pay as bid | Marginal Pricing | N/A | N/A | N/A | N/A | N/A | N/A | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | N/A | N/A | N/A | N/A | Real-Time Monitoring | Real-Time Monitoring | N/A | N/A | N/A | N/A | N/A | N/A | No | No | N/A | N/A | N/A | N/A | N/A | N/A | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | N/A | 5min < x <= 15 min | N/A | N/A | Yes | N/A | N/A | Yes | N/A | N/A
Lithuania | LITGRID | Self-Dispatch - Unit Based | No | N/A | N/A | No | N/A | N/A | Yes | Hybrid | Market only | Yes | Market only | N/A | N/A | Merit order | N/A | N/A | N/A | N/A | N/A | No minimum bid size | x <= 1MW | No minimum bid size | N/A | N/A | N/A | N/A | N/A | Year or more | Hour (or blocks) | Year or more | N/A | N/A | N/A | N/A | N/A | Year or more | 15 minutes < x <= H-1 | Year or more | N/A | N/A | N/A | N/A | N/A | Generators + Pump Storage | Generators + Pump Storage | Generators Only | N/A | N/A | N/A | Don't need to be symmetrical | N/A | N/A | N/A | N/A | Regulated Price | Marginal Pricing | Regulated Price | N/A | N/A | N/A | N/A | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | N/A | N/A | N/A | N/A | N/A | Hybrid | Hybrid | Hybrid | N/A | N/A | N/A | N/A | N/A | Yes | No | Yes | No | N/A | N/A | N/A | N/A | No | No | No | No | Yes, in all directions | N/A | N/A | N/A | 5min < x <= 15 min | N/A | N/A | Yes | No | N/A | Yes | Yes | No changes
Luxembourg | CREOS | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Malta | Enemalta | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
The Netherlands | TenneT NL | Self-Dispatch - Portfolio Based | Yes | Market only | N/A | Yes | Market only | Market only | Yes | Market only | Market only | No | N/A | N/A | Merit order | Merit order | N/A | x <= 1MW | N/A | x <= 1MW | x <= 1MW | 5 MW < x <= 10 MW | 1MW < x <= 5 MW | N/A | N/A | Week(s) | N/A | Month(s) | 15 minutes | Month(s) | 15 minutes | N/A | N/A | Day(s) | N/A | Month(s) | x <= 1 minute | Month(s) | 5 minutes < x <= 15 minutes | N/A | N/A | Generators + Load + Batteries | N/A | Generators + Load + Batteries | Generators + Load + Batteries | Generators + Load | Generators + Load | N/A | N/A | Has to be symmetrical | Has to be symmetrical | Don't need to be symmetrical | Pay as bid | N/A | Pay as bid | Marginal Pricing | Pay as bid | Marginal Pricing | N/A | N/A | 100% Grid Users (through tariff) | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | Ex-Post Check | N/A | Ex-Post Check | Ex-Post Check | Ex-Post Check | Ex-Post Check | N/A | N/A | No | No | No | No | No | No | N/A | N/A | No | No | N/A | N/A | N/A | N/A | N/A | N/A | No in none direction | N/A | N/A | 5min < x <= 15 min | N/A | No | Yes | Yes | N/A | No | No | N/A | N/A
Poland | PSE S.A. | Central Dispatch | Yes | Hybrid | N/A | Yes | Hybrid | Market only | No | N/A | N/A | Yes | Hybrid | Market only | Merit order | N/A | Merit order | x <= 1MW | x <= 1MW | x <= 1MW | x <= 1MW | N/A | N/A | x <= 1MW | x <= 1MW | N/A | Hour (or blocks) | N/A | Hour (or blocks) | N/A | N/A | Hour(s) | Hour (or blocks) | N/A | N/A | N/A | x <= 1 minute | N/A | N/A | N/A | 15 minutes < x <= H-1 | Generators Only | Generators Only | Generators Only | Generators Only | N/A | N/A | Generators Only | Generators + Load | Has to be symmetrical | Has to be symmetrical | N/A | Regulated Price | Marginal Pricing | Regulated Price | Marginal Pricing | N/A | N/A | Regulated Price | Marginal Pricing | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | 100% Grid Users (through tariff) | 100% BRP | Hybrid | Hybrid | Hybrid | Hybrid | N/A | N/A | Hybrid | Hybrid | No | No | No | No | N/A | N/A | No | No | No | No | No | No | N/A | N/A | No | No | N/A | Yes, in all directions | Depends on the unit | 90s < x <= 5 min | N/A | No | No | N/A | Yes | No | N/A | Yes | No changes
Portugal | REN | Self-Dispatch - Unit Based | Yes | Mandatory only | N/A | Yes | Market only | N/A | Yes | Market only | Mandatory only | Yes | N/A | Mandatory only | Pro Rata (Parallel Activation) | Merit order | Merit order | No minimum bid size | N/A | x > 10MW | N/A | N/A | No minimum bid size | N/A | No minimum bid size | N/A | N/A | Hour(s) | N/A | N/A | Hour (or blocks) | N/A | Hour (or blocks) | N/A | N/A | Day(s) | N/A | N/A | Depends on the unit | N/A | 5 minutes < x <= 15 minutes | Generators Only | Generators Only | Generators Only | Generators Only | N/A | Generators + Pump Storage | N/A | Generators + Pump Storage | Has to be symmetrical | Don't need to be symmetrical | N/A | N/A | N/A | Marginal Pricing | Marginal Pricing | N/A | Marginal Pricing | N/A | Marginal Pricing | N/A | N/A | 100% Grid Users (through tariff) | 100% BRP | N/A | 100% BRP | N/A | 100% BRP | Ex-Post Check | Ex-Post Check | Hybrid | Hybrid | N/A | Hybrid | N/A | Ex-Post Check | No | No | Yes | No | Yes | N/A | No | No | No | No | No | No | Yes | No | No | No | Yes, in all directions | Yes, in all directions | Depends on the unit | 90s < x <= 5 min | Depends on the unit | No | No | No | No | No | No | No | No changes
Romania | Transelectrica | Self-Dispatch - Unit Based | Yes | Mandatory only | Mandatory only | Yes | Market only | Hybrid | Yes | Market only | Market only | Yes | Market only | Market only | Merit order | Merit order | Merit order | 1MW < x <= 5 MW | N/A | x > 10MW | x > 10MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | Hour(s) | N/A | Hour(s) | Hour (or blocks) | Hour(s) | Hour (or blocks) | Hour(s) | Hour (or blocks) | N/A | N/A | Day(s) | x > H-1 | Day(s) | 5 minutes < x <= 15 minutes | Day(s) | 15 minutes < x <= H-1 | Generators Only | Generators Only | Generators Only | Generators Only | Generators Only | Generators Only | Generators Only | Generators Only | Has to be symmetrical | Has to be symmetrical | Don't need to be symmetrical | N/A | N/A | Marginal Pricing | Marginal Pricing | Marginal Pricing | Pay as bid | Marginal Pricing | Pay as bid | N/A | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | Real-Time Monitoring | Yes | No | Yes | No | Yes | No | Yes | No | No | No | No | No | No | No | N/A | No | N/A | N/A | Depends on the unit | 90s < x <= 5 min | 5min < x <= 15 min | No | No | No | N/A | No | N/A | N/A | No changes
Slovakia | SEPS | Self-Dispatch - Portfolio Based | Yes | Market only | N/A | Yes | Market only | Market only | Yes | Market only | Market only | No | N/A | N/A | Pro Rata (Parallel Activation) | Merit order | N/A | x <= 1MW | x <= 1MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | N/A | N/A | Hour(s) | Hour (or blocks) | Hour(s) | Hour (or blocks) | Hour(s) | Hour (or blocks) | N/A | N/A | Year or more + Month(s) + Day(s) | N/A | Year or more + Month(s) + Day(s) | x <= 1 minute | Year or more + Month(s) + Day(s) | 5 minutes < x <= 15 minutes | N/A | N/A | Generators Only | Generators Only | Generators Only | Generators Only | Generators + Load + Pump Storage | Generators + Load + Pump Storage | N/A | N/A | Has to be symmetrical | Has to be symmetrical | Don't need to be symmetrical | Pay as bid | Hybrid | Pay as bid | Pay as bid | Pay as bid | Pay as bid | N/A | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | Hybrid | Hybrid | Hybrid | Hybrid | Hybrid | Hybrid | N/A | N/A | Yes | No | Yes | No | Yes | No | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 5min < x <= 15 min | 5min < x <= 15 min | No | No | No | N/A | No | No | N/A | N/A
Slovenia | ELES | Self-Dispatch - Unit Based | Yes | Mandatory only | N/A | Yes | Hybrid | Hybrid | Yes | Hybrid | Hybrid | No | N/A | N/A | Pro Rata (Parallel Activation) | Merit order | N/A | No minimum bid size | No minimum bid size | x <= 1MW | N/A | 1MW < x <= 5 MW | x <= 1MW | N/A | N/A | N/A | N/A | Year or more | N/A | Year or more | Hour (or blocks) | N/A | N/A | N/A | N/A | Year or more | N/A | Year or more + Month(s) | 15 minutes < x <= H-1 | N/A | N/A | Generators Only | Generators Only | Generators + Pump Storage | Generators + Pump Storage | Generators + Load | Generators + Load + Pump Storage | N/A | N/A | Has to be symmetrical | Has to be symmetrical | Don't need to be symmetrical | N/A | N/A | Pay as bid | Pay as bid | Pay as bid | Pay as bid | N/A | N/A | N/A | N/A | 100% Grid Users (through tariff) | 100% BRP | N/A | 100% BRP | N/A | N/A | Ex-Post Check | Ex-Post Check | Real-Time Monitoring | Real-Time Monitoring | Ex-Post Check | Ex-Post Check | N/A | N/A | No | No | No | No | Yes | No | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 5min < x <= 15 min | 5min < x <= 15 min | No | No | No | N/A | No | No | N/A | N/A
Spain | REE | Self-Dispatch - Unit Based | Yes | Mandatory only | Mandatory only | Yes | Market only | Market only | Yes | Mandatory only | Market only | Yes | Market only | Market only | Pro Rata (Parallel Activation) | Merit order | Merit order | No minimum bid size | N/A | 5 MW < x <= 10 MW | x <= 1MW | N/A | x <= 1MW | 5 MW < x <= 10 MW | 5 MW < x <= 10 MW | N/A | N/A | Hour(s) | Hour (or blocks) | N/A | Hour (or blocks) | Hour(s) | Hour (or blocks) | N/A | N/A | Day(s) | x <= 1 minute | N/A | 15 minutes < x <= H-1 | Day(s) | 15 minutes < x <= H-1 | Generators Only | Generators Only | Generators Only | Generators Only | Generators + Pump Storage | Generators + Pump Storage | Generators Only | Generators + Pump Storage | Has to be symmetrical | Don't need to be symmetrical | N/A | N/A | N/A | Marginal Pricing | Marginal Pricing | N/A | Marginal Pricing | Marginal Pricing | Marginal Pricing | N/A | N/A | 100% Grid Users (through tariff) | 100% BRP | N/A | 100% BRP | Hybrid | 100% BRP | Ex-Post Check | Ex-Post Check | Real-Time Monitoring | Real-Time Monitoring | Ex-Post Check | Hybrid | Ex-Post Check | Ex-Post Check | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | No | No | No | No | No | Yes, in all directions | Yes, in all directions | 15 min < x <= 30 min | 90s < x <= 5 min | 5min < x <= 15 min | No | No | Yes | Yes | No | Yes | No | Yes
Sweden | Svenska kraftnät | Self-Dispatch - Portfolio Based | Yes | Market only | N/A | Yes | Market only | N/A | Yes | Market only | Market only | No | N/A | N/A | Pro Rata (Parallel Activation) | Merit order | N/A | x <= 1MW | N/A | 5 MW < x <= 10 MW | N/A | 5 MW < x <= 10 MW | 5 MW < x <= 10 MW | N/A | N/A | Hour(s) | N/A | Hour(s) | N/A | Month(s) | Hour (or blocks) | N/A | N/A | Day(s) | N/A | Day(s) | N/A | N/A | 5 minutes < x <= 15 minutes | N/A | N/A | Generators Only | Generators Only | Generators Only | Generators Only | Generators + Load | Generators + Load | N/A | N/A | Has to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | Pay as bid | Marginal Pricing | Pay as bid | Marginal Pricing | Pay as bid | Marginal Pricing | N/A | N/A | Hybrid | 100% BRP | 100% BRP | 100% BRP | Hybrid | 100% BRP | N/A | N/A | Hybrid | Hybrid | Hybrid | Hybrid | Hybrid | Real-Time Monitoring | N/A | N/A | No | No | No | No | No | No | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 90s < x <= 5 min | 5min < x <= 15 min | No | No | Yes | N/A | Yes | Yes | N/A | N/A
GB/United Kingdom | National Grid | Self-Dispatch - Unit Based | Yes | Hybrid | N/A | No | N/A | N/A | Yes | Market only | Market only | Yes | Market only | Hybrid | N/A | Merit order | Merit order | 1MW < x <= 5 MW | N/A | N/A | N/A | 5 MW < x <= 10 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | N/A | N/A | N/A | N/A | Month(s) | N/A | Year or more | N/A | Week(s) | N/A | N/A | N/A | Month(s) | Depends on the unit | Month(s) | Depends on the unit | Generators + Load + Pump Storage + Batteries | N/A | N/A | N/A | Generators + Load + Pump Storage + Batteries | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Generators + Load + Pump Storage | Has to be symmetrical | N/A | Don't need to be symmetrical | Pay as bid | N/A | N/A | N/A | Pay as bid | Pay as bid | Pay as bid | Pay as bid | 100% Grid Users (through tariff) | N/A | N/A | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | Hybrid | N/A | N/A | N/A | Hybrid | Hybrid | Hybrid | Hybrid | Yes | No | N/A | N/A | Yes | No | No | No | No | No | N/A | N/A | No | No | No | No | Yes, in all directions | Yes, in all directions | Depends on the unit | N/A | Depends on the unit | Yes | N/A | Yes | Yes | N/A | Yes | Yes | No changes
| SHETL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| SPTransmission | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
> Northern Ireland | SONI | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Croatia | HOPS | Self-Dispatch - Portfolio Based | Yes | Mandatory only | Mandatory only | Yes | Mandatory only | Hybrid | Yes | Hybrid | Hybrid | No | N/A | N/A | Pro Rata (Parallel Activation) | Merit order | N/A | No minimum bid size | N/A | x <= 1MW | x <= 1MW | x <= 1MW | x <= 1MW | N/A | N/A | N/A | N/A | Year or more | Hour (or blocks) | Year or more | Hour (or blocks) | N/A | N/A | N/A | N/A | Month(s) | 15 minutes < x <= H-1 | Week(s) + Day(s) | 15 minutes < x <= H-1 | N/A | N/A | Generators Only | Generators Only | Generators Only | Generators Only | Generators + Load + Pump Storage | Generators + Load + Pump Storage | N/A | N/A | Has to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | N/A | N/A | Pay as bid | Pay as bid | Pay as bid | Pay as bid | N/A | N/A | Hybrid | N/A | Hybrid | 100% BRP | Hybrid | 100% BRP | N/A | N/A | Hybrid | Hybrid | Hybrid | Hybrid | Hybrid | Hybrid | N/A | N/A | No | No | No | No | No | No | N/A | N/A | No | No | No | N/A | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 90s < x <= 5 min | 5min < x <= 15 min | No | No | No | N/A | No | Yes | N/A | N/A
Iceland | Landsnet | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Montenegro | Crnogorski elektroprenosni sistem AD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Serbia | EMS | Central Dispatch | Yes | Mandatory only | Mandatory only | Yes | Mandatory only | Mandatory only | Yes | Mandatory only | Mandatory only | No | N/A | N/A | Pro Rata (Parallel Activation) | Merit order | N/A | x <= 1MW | x <= 1MW | x <= 1MW | x <= 1MW | x <= 1MW | x <= 1MW | N/A | N/A | Year or more | N/A | Year or more | Hour (or blocks) | Year or more | Hour (or blocks) | N/A | N/A | N/A | N/A | N/A | x > H-1 | N/A | x > H-1 | N/A | N/A | Generators Only | Generators Only | Generators Only | Generators Only | Generators + Pump Storage | Generators + Pump Storage | N/A | N/A | Has to be symmetrical | Has to be symmetrical | Has to be symmetrical | N/A | N/A | Regulated Price | Hybrid | Regulated Price | Pay as bid | N/A | N/A | N/A | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | Hybrid | Hybrid | Hybrid | Hybrid | Hybrid | Hybrid | N/A | N/A | No | No | No | No | No | N/A | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 5min < x <= 15 min | 5min < x <= 15 min | No | No | Yes | N/A | No | Yes | N/A | N/A
The former Yugoslav Republic of Macedonia | MEPSO | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Turkey | TEIAS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Albania | OST | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Bosnia and Herzegovina | ISO BIH | Central Dispatch | Yes | Mandatory only | Mandatory only | Yes | Market only | Market only | Yes | Market only | Market only | No | N/A | N/A | Pro Rata (Parallel Activation) | Merit order | N/A | No minimum bid size | N/A | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 5 MW < x <= 10 MW | 5 MW < x <= 10 MW | N/A | N/A | N/A | N/A | Month(s) | Hour (or blocks) | Month(s) | Hour (or blocks) | N/A | N/A | N/A | N/A | Day(s) | x > H-1 | Day(s) | 15 minutes < x <= H-1 | N/A | N/A | Generators Only | Generators Only | Generators Only | Generators Only | Generators + Load + Pump Storage | Generators + Load + Pump Storage | N/A | N/A | N/A | Has to be symmetrical | Don't need to be symmetrical | N/A | N/A | Pay as bid | Pay as bid | Pay as bid | Pay as bid | N/A | N/A | N/A | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | N/A | N/A | N/A | N/A | Ex-Post Check | Ex-Post Check | Ex-Post Check | Ex-Post Check | N/A | N/A | No | No | No | No | No | No | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 90s < x <= 5 min | 5min < x <= 15 min | Yes | No | Yes | N/A | Yes | Yes | N/A | N/A
Kosovo (UNMIK) | KOSTT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Moldova | Moldelectrica | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Ukraine | Ukrenergo | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Norway | Statnett SF | Self-Dispatch - Unit Based | Yes | Hybrid | N/A | Yes | Market only | N/A | Yes | Market only | Market only | No | N/A | N/A | Pro Rata (Parallel Activation) | Merit order | N/A | x <= 1MW | N/A | 5 MW < x <= 10 MW | N/A | x <= 1MW | 5 MW < x <= 10 MW | N/A | N/A | Hour(s) | N/A | Hour(s) | N/A | Hour(s) | Hour (or blocks) | N/A | N/A | Day(s) | N/A | Day(s) | N/A | Day(s) | 5 minutes < x <= 15 minutes | N/A | N/A | Generators Only | Generators Only | Generators Only | Generators Only | Generators + Load | Generators + Load | N/A | N/A | Don't need to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | Marginal Pricing | Marginal Pricing | Marginal Pricing | Marginal Pricing | Marginal Pricing | Marginal Pricing | N/A | N/A | 100% BRP | 100% BRP | 100% Grid Users (through tariff) | 100% Grid Users (through tariff) | Hybrid | 100% BRP | N/A | N/A | Hybrid | Ex-Post Check | N/A | N/A | Hybrid | Hybrid | N/A | N/A | No | No | No | No | No | No | N/A | N/A | No | No | No | No | No | No | N/A | N/A | Yes, in all directions | N/A | N/A | 90s < x <= 5 min | 5min < x <= 15 min | No | No | Yes | N/A | No | Yes | N/A | N/A
Switzerland | Swissgrid | Self-Dispatch - Portfolio Based | Yes | Market only | N/A | Yes | Market only | N/A | Yes | Market only | Market only | Yes | Market only | Market only | Pro Rata (Parallel Activation) | Merit order | Merit order | x <= 1MW | N/A | 1MW < x <= 5 MW | N/A | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | 1MW < x <= 5 MW | Week(s) | N/A | Week(s) | N/A | Hour(s) | Hour (or blocks) | Week(s) | Hour (or blocks) | Day(s) | N/A | Day(s) | N/A | Day(s) | 5 minutes < x <= 15 minutes | Day(s) | 15 minutes < x <= H-1 | Generators + Load + Pump Storage + Batteries | N/A | Generators + Load + Pump Storage + Batteries | Generators + Load + Pump Storage + Batteries | Generators + Load + Pump Storage + Batteries | Generators + Load + Pump Storage + Batteries | Generators + Load + Pump Storage + Batteries | Generators + Load + Pump Storage + Batteries | Has to be symmetrical | Don't need to be symmetrical | Don't need to be symmetrical | Pay as bid | N/A | Pay as bid | Hybrid | Pay as bid | Pay as bid | Pay as bid | Pay as bid | 100% Grid Users (through tariff) | N/A | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | 100% Grid Users (through tariff) | 100% BRP | Hybrid | Ex-Post Check | Hybrid | Ex-Post Check | Hybrid | Ex-Post Check | Hybrid | Ex-Post Check | Yes, only in case of forced outage | No | Yes, only in case of forced outage | No | Yes, only in case of forced outage | Yes, only in case of forced outage | Yes, only in case of forced outage | No | No | No | No | No | No | No | No | No | No in none direction | No in none direction | 15 min < x <= 30 min | 90s < x <= 5 min | 5min < x <= 15 min | No | No | Yes | No | Yes | Yes | Yes | Yes
Monaco |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
San Marino |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Andorra | FEDA/RTE/REE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Vatican City |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Liechtenstein | LKW | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Belarus |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## Load Parcitipation
|  | L1.0 | L2.1 | L2.2 | L2.3 | L2.4 | L2.5 | L3.1 | L3.2 | L3.3 | L3.4 | L3.5 | L3.6 | L3.7 | L4.0 | L5.0 | L6.0 | L7.0 | L8.0
AS Survey 2018 |  | Load Participation
If the answer to L1.0 is No:
Country | TSO Name | Do load providers use the same market mechanisms and activation procedure as generation to provide these services (for both capacity and energy)? | What type of specific market solution use for load providers of balancing services for both capacity and energy? | Product Resolution (in MW) | Product Resolution (in time) | What type of specific activation rule do you follow with load type BSP´s? | Settlement Rule | Load participation - Are aggregators participates nowadays in these balancing services? | Load participation - Are large consumers participates nowadays in these balancing services? | Load participation - Are pump storage units consumers participates nowadays in these balancing services? | Load participation - Are aggregated small size consumers participates nowadays in these balancing services? | Load participation - Are small consumers participates nowadays in these balancing services? | Load participation - Are other storage consumers participates nowadays in these balancing services? | Load participation - Are other consumers participates nowadays in these balancing services? | What is the product resolution for load BSP´s to participate at these balancing services? | Monitoring | Besides balancing services, do you use load BSP´s in order to solve local constraints? | What level of control of the load does the TSO have? | Do you consider changes significant/important regarding the load participation?
Austria | APG | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
| VUEN | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Belgium | Elia | No | Specific market solution | x <= 1MW | 15 minutes | Merit Order | Pay as bid | Yes | Yes | Yes | Yes | Yes | No | No | x <= 1MW | Ex-Post Check | No | Direct Control (Manual) | No changes
Bulgaria | ESO | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Cyprus | TSO-Cyprus | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Czech Republic | CEPS | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Denmark | Energinet.dk IPC | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Only minor changes
Estonia | Elering | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Finland | Fingrid | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Yes
France | RTE | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Yes
Germany | 50Hertz | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
| Amprion | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
| TransnetBW | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
| Tennet Germany | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Greece | ADMIE | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Hungary | MAVIR | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Ireland | EirGrid | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Italy | Terna | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Only minor changes
Latvia | AST | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Lithuania | LITGRID | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Luxembourg | CREOS | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Malta | Enemalta | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
The Netherlands | TenneT NL | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Poland | PSE S.A. | No | Specific market solution | x <= 1MW | Hour (or blocks) | Merit Order | Marginal Pricing | Yes | Yes | No | Yes | Yes | No | No | N/A | Hybrid | No | N/A | No changes
Portugal | REN | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Yes
Romania | Transelectrica | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Slovakia | SEPS | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Slovenia | ELES | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Spain | REE | No | Long term auctions | Other | Hour (or blocks) | N/A | Pay as bid | No | Yes | No | No | No | No | No | 1MW < x <= 5 MW | Real-Time Monitoring | Yes | Direct Control (Manual) | Yes
Sweden | Svenska kraftnät | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
GB/United Kingdom | National Grid | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
| SHETL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| SPTransmission | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
> Northern Ireland | SONI | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Croatia | HOPS | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Only minor changes
Iceland | Landsnet | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Montenegro | Crnogorski elektroprenosni sistem AD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Serbia | EMS | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
The former Yugoslav Republic of Macedonia | MEPSO | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Turkey | TEIAS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Albania | OST | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Bosnia and Herzegovina | ISO BIH | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Kosovo (UNMIK) | KOSTT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Moldova | Moldelectrica | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Ukraine | Ukrenergo | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Norway | Statnett SF | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Switzerland | Swissgrid | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Monaco |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
San Marino |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Andorra | FEDA/RTE/REE | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Vatican City |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Liechtenstein | LKW | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Belarus |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## Voltage Control
|  | VC1.0 | VC2.0 | VC2.1 | VC2.2 | VC2.3 | VC6.0 | VCQ2.1 | VCQ2.2 | VCQ2.3 | VCQ2.4 | VCQ2.5 | VCQ2.6 | VCQ2.7 | VCQ2.8 | VCQ2.9 | VCQ3.1 | VCQ3.2 | VCQ3.3 | VCQ3.4 | VCQ3.5 | VCQ3.6 | VCQ3.7 | VCQ4.0 | VCQ5.0 | VCQ6.0 | VCQ7.0 | VCQ8.1 | VCQ8.2 | VCQ8.3 | VCQ8.4 | VCQ8.5 | VCQ9.1 | VCQ9.2 | VCQ9.3 | VCQ9.4 | VCQ9.5 | VCQ9.6 | VCQ9.7 | VCQ10.0 | VCQ11.0 | VCQ12.0 | VCQ13.0
AS Survey 2018 |  | VC1.0: Voltage Control and Additional Questions
Reactive energy is needed in order to control the voltages in the transmission system.
Country | TSO Name | Do you consider the voltage support as part of ancillary services? | Which power plants have to provide voltage control? Is it a mandatory service in your country? | How do you determine the optimal use of reactive energy? | If the needed reactive energy results from an optimisation problem, how does the objective function in general look like? | What kind of optimization approach do you use? | Implicit / explicit offers or bids from BSP? | Who are the providers of the voltage control service? | Who are the providers of the voltage control service? | Who are the providers of the voltage control service? | Who are the providers of the voltage control service? | Who are the providers of the voltage control service? | Who are the providers of the voltage control service? | Who are the providers of the voltage control service? | Who are the providers of the voltage control service? | Who are the providers of the voltage control service? | What type of regulations for the voltage control demanded to the power plants? | What type of regulations for the voltage control demanded to the power plants? | What type of regulations for the voltage control demanded to the power plants? | What type of regulations for the voltage control demanded to the power plants? | What type of regulations for the voltage control demanded to the power plants? | What type of regulations for the voltage control demanded to the power plants? | What type of regulations for the voltage control demanded to the power plants? | If a power plant is able to provide voltage control, which grid it should be connected to? | Is it a service paid by the TSO? | What are the settlement rules for the price of voltage Control? | Does the TSO verify/monitor the voltage control? | Does the TSO own reactive power compensation systems? | Does the TSO own reactive power compensation systems? | Does the TSO own reactive power compensation systems? | Does the TSO own reactive power compensation systems? | Does the TSO own reactive power compensation systems? | What are the settlement rules for the exchange of reactive power between transmission and distribution grids? | What are the settlement rules for the exchange of reactive power between transmission and distribution grids? | What are the settlement rules for the exchange of reactive power between transmission and distribution grids? | What are the settlement rules for the exchange of reactive power between transmission and distribution grids? | What are the settlement rules for the exchange of reactive power between transmission and distribution grids? | What are the settlement rules for the exchange of reactive power between transmission and distribution grids? | What are the settlement rules for the exchange of reactive power between transmission and distribution grids? | What are the settlement rules for the price of reactive power between transmission and distribution grids? | Existing of secondary voltage control (SecVolCon) voltage control for the nominated mains? | Existing of tertiary voltage control | Do you consider changes significant/important regarding the voltage control?
Austria | APG | Yes | - | Both | Operator's experience | Centralised optimisation approach | N/A | Yes | Yes | No | Yes | No | No | Yes | Yes | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Partly | Regulated price | Real time monitoring | Yes | Yes | Yes | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No rules | N/A | N/A | No changes
| VUEN | Yes | - | Both | Operator's experience | Centralised optimisation approach | N/A | Yes | Yes | No | Yes | No | No | Yes | Yes | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Partly | Regulated price | Real time monitoring | Yes | Yes | Yes | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No rules | N/A | N/A | No changes
Belgium | Elia | Yes | - | Both | Both | Both | Implicit | Yes | No | No | Yes | No | No | No | Yes | No | No | Yes | No | Yes | No | No | No | Transmission grid | Yes | Free | Hybrid | Yes | Yes | Yes | No | Yes | No | Yes | No | No | No | No | No | Charges and/or fees | SecVolCon reactive | N/A | Yes
Bulgaria | ESO | bar: VC1.0 to VCQ13.0
Cyprus | TSO-Cyprus | bar: VC1.0 to VCQ13.0
Czech Republic | CEPS | Yes | All units connected to the transmission grid (220kV +) must be capable of voltage control | Optimisation program | Optimisation program | Centralised optimisation approach | Explicit | Yes | No | No | No | No | No | No | Yes | No | No | No | No | No | Yes | No | No | Transmission grid | Yes | N/A | Real time monitoring | Yes | Yes | No | No | No | Yes | No | No | No | No | No | No | No rules | Operating in closed loop | Operating in open loop | No changes
Denmark | Energinet.dk IPC | Yes | - | Both | Both | Both | Implicit | Yes | No | No | No | No | No | No | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Transmission grid | Partly | Hybrid | Hybrid | Yes | No | No | No | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Free | Operating in open loop | N/A | No changes
Estonia | Elering | Yes | It is mandatory. All power plants that are connected to the main grid must have voltage control capability. | Operator's experience, studies | N/A | N/A | Implicit | Yes | No | No | Yes | No | Yes | No | Yes | No | No | Yes | No | No | Yes | No | No | Both | Partly | Regulated price | Ex post check | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | No | Regulated price | N/A | N/A | No changes
Finland | Fingrid | Yes | Mandatory service for all power plants. | Operator's experience, studies | N/A | N/A | N/A | Yes | No | No | Yes | No | No | Yes | Yes | No | No | Yes | Yes | Yes | No | No | No | Both | No | N/A | Hybrid | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | No | No | Charges and/or fees | N/A | N/A | No changes
France | RTE | Yes | no | Both | Optimisation program | Centralised optimisation approach | Implicit | Yes | No | No | No | No | No | No | Yes | No | No | Yes | No | No | No | No | No | Transmission grid | Partly | Regulated price | Ex post check | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Regulated price | N/A | N/A | Yes
Germany | 50Hertz | Yes | The framework of voltage control requirements for plants connected to the high-voltage grid is provided by the German Transmission Code. Concrete requirements within the given framework are agreed between connecting TSO and power plant operator and included in the grid connection contracts. A similar framework does also exist for medium-voltage grids. | Operator's experience, studies | N/A | N/A | N/A | Yes | No | No | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | Both | Partly | Free | Ex post check | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | No | Charges and/or fees | N/A | N/A | No changes
| Amprion | Yes |  | Operator's experience, studies | N/A | N/A | N/A | Yes | No | No | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | Both | Partly | Free | Ex post check | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | No | Charges and/or fees | N/A | N/A | No changes
| TransnetBW | Yes |  | Operator's experience, studies | N/A | N/A | N/A | Yes | No | No | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | Both | Partly | Free | Ex post check | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | No | Charges and/or fees | N/A | N/A | No changes
| Tennet Germany | Yes |  | Operator's experience, studies | N/A | N/A | N/A | Yes | No | No | Yes | No | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | No | Yes | Both | Partly | Free | Ex post check | Yes | Yes | Yes | No | Yes | Yes | No | No | No | No | No | No | Charges and/or fees | N/A | N/A | No changes
Greece | ADMIE | Yes | - | Operator's experience, studies | N/A | Both | N/A | Yes | No | No | No | No | No | No | Yes | No | No | Yes | Yes | No | No | No | No | Transmission grid | No | N/A | Hybrid | Yes | Yes | Yes | No | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No rules | N/A | N/A | No changes
Hungary | MAVIR | Yes | If the gross installed capacity is more than 50 MW and the power plant is connected to the transmission grid, or 132 kV, the service is mandatory. | Both | Both | Centralised optimisation approach | Explicit | Yes | No | No | No | No | No | No | Yes | No | No | No | No | Yes | Yes | Yes | No | Both | Yes | Pay as bid | Real time monitoring | Yes | Yes | No | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No rules | SecVolCon reactive + SecVolCon voltage | N/A | No changes
Ireland | EirGrid | Yes | Mandatory Grid Code requirement for transmission connected units. Commercial opportunities for all other providers (or provisions over and above mandatory requirement). | Both | Both | Both | Both | Yes | No | No | Yes | No | Yes | No | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Transmission grid | Yes | Hybrid | Hybrid | No | No | No | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Italy | Terna | Yes | It’s mandatory for the power units which have nominal power greater or equal than 10 MVA and for all the new HV connected PPM and synchronous generators (formerly PPM had only obligation on power factor cosine phi) | Optimisation program | Operator's experience | Regional-oriented approach | N/A | Yes | No | No | No | No | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | No | No | Transmission grid | No | N/A | Hybrid | Yes | Yes | Yes | No | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No rules | SecVolCon reactive + SecVolCon voltage | N/A | No changes
Latvia | AST | Yes | All power plants connected to the transmission grid are obliged to provide Voltage Control service | Operator's experience, studies | Operator's experience | N/A | N/A | Yes | No | No | Yes | No | No | No | Yes | No | No | Yes | No | No | Yes | No | Yes | Transmission grid | Partly | Pay as bid | Real time monitoring | Yes | Yes | Yes | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No rules | N/A | N/A | No changes
Lithuania | LITGRID | Yes | All power plant conected to transmission gird. All running generator shall provide votage support according technical possibilities from generator. | Both | Both | Centralised optimisation approach | N/A | Yes | No | No | Yes | No | Yes | No | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Transmission grid | Partly | Regulated price | Hybrid | Yes | Yes | Yes | No | Yes | No | No | No | No | No | Yes | No | Regulated price | SecVolCon reactive | N/A | No changes
Luxembourg | CREOS | Yes | - | Operator's experience, studies | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Both | N/A | N/A | N/A | No | No | No | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Charges and/or fees | N/A | N/A | N/A
Malta | Enemalta | - | - | [20 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: Both to N/A
The Netherlands | TenneT NL | Yes | Power plants are not obliged to provide voltage control | Operator's experience, studies | N/A | N/A | Explicit | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | No | No | No | Both | Partly | Pay as bid | Hybrid | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | Charges and/or fees | Operating in open loop | N/A | No changes
Poland | PSE S.A. | Yes | All generating units according to Grid Code are obliged to control the voltage, centrally dispatched units are contracted for such service. | Both | Both | Both | N/A | Yes | No | No | Yes | No | No | Yes | Yes | No | No | No | No | Yes | No | No | No | Both | Yes | Pay as bid | Hybrid | Yes | Yes | Yes | No | No | Yes | No | No | No | No | No | No | Charges and/or fees | Operating in closed loop | Operating in open loop | No changes
Portugal | REN | Yes | All conventional generators have to provide | Both | Both | Both | N/A | Yes | No | No | No | No | No | No | No | No | No | Yes | No | Yes | No | Yes | Yes | Transmission grid | No | N/A | Real time monitoring | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | No | No | No | No rules | Operating in closed loop | Operating in closed loop (automatic) | No changes
Romania | Transelectrica | Yes | - | Operator's experience, studies | N/A | N/A | Implicit | Yes | No | No | No | No | No | No | No | No | No | Yes | No | Yes | No | No | No | Transmission grid | Partly | Regulated price | Real time monitoring | Yes | Yes | No | No | Yes | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Slovakia | SEPS | Yes | Primary voltage control is mandatory and secondary voltage control is paid service. We use secondary voltage control just at transmission level (400 kV and 220 kV). | Both | Both | Centralised optimisation approach | Explicit | Yes | No | No | No | No | No | No | Yes | No | No | No | No | No | Yes | No | No | Transmission grid | Yes | Regulated price | Hybrid | Yes | Yes | No | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No rules | Operating in closed loop | Operating in open loop | No changes
Slovenia | ELES | Yes | - | Operator's experience, studies | N/A | N/A | N/A | Yes | No | Yes | No | No | No | No | Yes | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Transmission grid | Yes | Pay as bid | Real time monitoring | No | No | No | No | No | Yes | No | No | No | No | No | No | No rules | N/A | N/A | No changes
Spain | REE | Yes | Power plants connected to transmission grid with rated power equal or above 30 MW | Both | Both | Centralised optimisation approach | N/A | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | No | No | No | Yes | No | Yes | No | Both | No | N/A | Real time monitoring | Yes | Yes | Yes | No | No | Yes | No | No | No | No | No | No | No rules | N/A | Operating in open loop | Only minor changes
Sweden | Svenska kraftnät | Yes | - | Operator's experience, studies | Both | Regional-oriented approach | N/A | Yes | Yes | No | No | No | No | No | No | No | Yes | No | No | No | No | No | No | Both | No | N/A | Real time monitoring | Yes | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Free | N/A | N/A | No changes
GB/United Kingdom | National Grid | Yes | Mandatory Service (Grid Code Provision) for Conventional Generators and Windfarms connected to the transmission system. Commercial Service for Conventional Generators and Windfarms connected to the transmission system for provision over and above Mandatory levels. | Both | Both | Both | Explicit | Yes | No | No | Yes | No | Yes | No | Yes | No | No | Yes | No | Yes | No | No | No | Both | Yes | Pay as bid | Real time monitoring | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | No | No | Charges and/or fees | N/A | N/A | No changes
| SHETL | - |  | - | - | - | [20 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A N/A to N/A N/A
| SPTransmission | - |  | - | - | - | [20 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A N/A to N/A N/A
> Northern Ireland | SONI | - | - | - | - | - | [20 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A N/A to N/A N/A
Croatia | HOPS | Yes | All power plants need to provide voltage control in mandatory range by grid code. | Operator's experience, studies | N/A | Regional-oriented approach | N/A | Yes | No | No | Yes | No | No | No | Yes | No | No | Yes | No | No | No | No | No | Both | Yes | Hybrid | Ex post check | Yes | Yes | Yes | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No rules | N/A | N/A | Only minor changes
Iceland | Landsnet | - | - | - | - | - | [20 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A N/A to N/A N/A
Montenegro | Crnogorski elektroprenosni sistem AD | - | - | - | - | - | [20 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A N/A to N/A N/A
Serbia | EMS | Yes | - | Operator's experience, studies | Both | Centralised optimisation approach | N/A | Yes | Yes | No | Yes | No | No | No | Yes | No | No | No | No | Yes | Yes | No | No | Transmission grid | Yes | Regulated price | Hybrid | No | No | No | No | No | No | No | No | No | No | Yes | No | Charges and/or fees | SecVolCon voltage | N/A | No changes
The former Yugoslav Republic of Macedonia | MEPSO | - | - | - | - | - | [20 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A N/A to N/A N/A
Turkey | TEIAS | - | - | - | - | - | [20 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A N/A to N/A N/A
Albania | OST | - | - | - | - | - | [20 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A N/A to N/A N/A
Bosnia and Herzegovina | ISO BIH | Yes | Yes | Operator's experience, studies | Operator's experience | N/A | N/A | Yes | No | No | No | No | No | No | No | No | No | Yes | No | No | No | No | No | Transmission grid | No | N/A | N/A | No | No | No | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No rules | N/A | N/A | No changes
Kosovo (UNMIK) | KOSTT | - | - | - | - | - | [20 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A N/A to N/A N/A
Moldova | Moldelectrica | - | - | - | - | - | [20 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A N/A to N/A N/A
Ukraine | Ukrenergo | - | - | - | - | - | [20 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A N/A to N/A N/A
Norway | Statnett SF | Yes | Generators >= 1MVA. Yes, it is a mandatory service. | Operator's experience, studies | N/A | N/A | N/A | Yes | No | No | No | No | Yes | No | No | No | No | No | No | Yes | No | No | No | Both | Yes | Regulated price | Real time monitoring | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | Regulated price | N/A | N/A | No changes
Switzerland | Swissgrid | Yes | All power plants directly connected to the transmission system which are in operation (production, pump mode or synchronous/phase shifting mode), within the scope of their available reactive power that can be exchanged with the transmission system without compromising the active power. | Optimisation program | Optimisation program | Centralised optimisation approach | N/A | Yes | Yes | No | No | No | No | No | Yes | No | No | No | No | No | Yes | No | No | Both | Yes | Regulated price | Real time monitoring | No | No | No | No | No | Yes | Yes | No | No | No | No | No | Charges and/or fees | N/A | N/A | Yes
Monaco |  | - | - | - | - | - | [19 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A to Yes Yes
San Marino |  | - | - | - | - | - | [19 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A to Yes Yes
Andorra | FEDA/RTE/REE | - | - | - | - | - | [19 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A to Yes Yes
Vatican City |  | - | - | - | - | - | [19 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A to Yes Yes
Liechtenstein | LKW | - | - | - | - | - | [19 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A to Yes Yes
Belarus |  | - | - | - | - | - | [19 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: N/A to Yes Yes

## Black Start
|  | BSQ2.1 | BSQ2.0 | BSQ3.0 | BSQ4.0 | BSQ5.0 | BSQ6.0 | BSQ7.0 | BSQ8.1 | BSQ8.2 | BSQ8.3 | BSQ8.4 | BSQ8.5 | BSQ8.6 | BSQ8.7 | BSQ9.0 | BSQ10.0 | BSQ11.0 | BSQ12.0 | BSQ13.0 | BSQ14.0
AS Survey 2018
Country | TSO Name | Which power plants have to provide black start (for example: capacity, technology etc)? Is it a mandatory service in your country? | If a power plant is able to provide black start service, which grid it should be connected to? | Is it a service paid by the TSO? | What are the settlement rules for the price of black start service? | Does the TSO own unit for Black start service? | Does the TSO have some special rules for the distribution/location/number etc of black start service units? For example: is the prescribed amount of BS area-dependent or the TSO only has one prescribed amount per control area? | Does the TSO have a regulated amount of BS control (regarding the whole control area)? | How can the TSO test the BS ability? | How can the TSO test the BS ability? | How can the TSO test the BS ability? | How can the TSO test the BS ability? | How can the TSO test the BS ability? | How can the TSO test the BS ability? | How can the TSO test the BS ability? | How often does the TSO practise the method of the BS process (for example using a training simulator)? | Should be the Black start service provided by a single unit or it is allowed to be a part of a power plant? | How long is the acceptable non-availability period of the BS unit (planned, for example: resurrection & mainteance of the unit)? | Is there a regulated gradient for the BS unit? | Does the TSO verify/Monitoring of the black start service? | Do you consider changes significant/important regarding the black start?
Austria | APG | Hydro storage power plants. Not mandatory for power plants. | Transmission grid | Yes | Pay as bid | No | N/A | No | No | Yes | No | No | No | No | No | Regularly/several times a year | Yes, it can be part of the power plant | Depending on the availability of other BS units | No | Hybrid | No changes
| VUEN |  | Transmission grid | Yes | Pay as bid | No |  | No | No | Yes | No | No | No | No | No | Regularly/several times a year | Yes, it can be part of the power plant | Depending on the availability of other BS units | No | Hybrid | No changes
Belgium | Elia | Gas Power plant & Hydraulic power plants (pumped storage). It is not mandatory. | Transmission grid | Yes | Hybrid | No | 5 black start services procured one for 380kV grid plus 4 zones within control area | No | No | No | No | No | Yes | No | No | Regularly/several times a year | Yes, it can be part of the power plant | Depending on the availability of other BS units | No | Hybrid | Yes
Bulgaria | ESO | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Cyprus | TSO-Cyprus | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Czech Republic | CEPS | No obligations to provide black start for any unit. | Transmission grid | Yes | N/A | No | N/A | No | Yes | No | No | No | No | No | No | Regularly/several times a year | Yes, it can be part of the power plant | N/A | N/A | N/A | No changes
Denmark | Energinet.dk IPC | - | Transmission grid | Yes | Pay as bid | Yes | - | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Regularly/once a year | Yes, it can be part of the power plant | N/A | Yes, 0-100MW/15 min | Real time monitoring/tests | No changes
Estonia | Elering | Black start service is provided by power plants which are included in the restoration plan as black start servide providers. It is not a mandatory service. | Transmission grid | Yes | Hybrid | Yes | No | No | No | No | No | Yes | No | No | No | Occasionally | Yes, it can be part of the power plant | N/A | No | Ex post check | No changes
Finland | Fingrid | Not mandatory. Agreed bilaterally with suitable power plants. | Both | Yes | Free | Yes | No | No | No | No | No | No | No | No | Yes | Regularly | Yes, it can be part of the power plant | N/A | No | Ex post check | No changes
France | RTE | BS not mandatory. Nuclear power plants provide VSC w/o BS. | Both | No | N/A | No | NA | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Regularly/several times a year | N/A | N/A | N/A | N/A | No changes
Germany | 50Hertz | Black start provision according to respective black-start concepts, based on grid connection and specific contracts. | Transmission grid | Yes | Free | No | according to respective black-start concept | No | No | No | No | No | No | No | Yes | Regularly | Yes, it can be part of the power plant | Depending on the availability of other BS units | No | Hybrid | No changes
| Amprion |  | Transmission grid | Yes | Free | No |  | No | No | No | No | No | No | No | Yes | Regularly | Yes, it can be part of the power plant | Depending on the availability of other BS units | No | Hybrid | No changes
| TransnetBW |  | Transmission grid | Yes | Free | No |  | No | No | No | No | No | No | No | Yes | Regularly | Yes, it can be part of the power plant | Depending on the availability of other BS units | No | Hybrid | No changes
| Tennet Germany |  | Transmission grid | Yes | Free | No |  | No | No | No | No | No | No | No | Yes | Regularly | Yes, it can be part of the power plant | Depending on the availability of other BS units | No | Hybrid | No changes
Greece | ADMIE | Predefined power plants have to provide Black Start service | Transmission grid | Yes | Regulated price | No | No | No | No | No | No | No | Yes | No | No | Occasionally | No, it has to be a single unit | Depending on the availability of other BS units | N/A | N/A | No changes
Hungary | MAVIR | If the gross installed capacity is more than 500 MW and the power plant is connected to the transmission grid, the service is mandatory. But there are some power plants who are able to provide BS capability, but their gross installed capacities are less than 500 MW. | Both | Yes | Pay as bid | No | No special rules. | All the units who are able to provide BS must to provide it | No | No | No | No | No | Yes | No | Regularly/once a year | Yes, it can be part of the power plant | Depending on the availability of other BS units | No | Ex post check | No changes
Ireland | EirGrid | It is not mandatory in Ireland but is in Northern Ireland for certain plant types. Technologies currently providing black start across the island: Hydro, Pumped Storage, Interconnectors, Open Cycle Gas Turbines | N/A | N/A | N/A | No | - | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | No changes
Italy | Terna | It is mandatory for the power plants defined in the restoration plan. | Transmission grid | No | N/A | No | We have a fixed number of "restoration path" | All the units who are able to provide BS must to provide it | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Regularly/several times a year | N/A | Depending on the availability of other BS units | N/A | Hybrid | No changes
Latvia | AST | No special rules - agreement with hydro power plant for providing the service. | Transmission grid | Yes | Pay as bid | No | No | No | No | Yes | No | No | No | No | No | Occasionally | Yes, it can be part of the power plant | It is not allowed | No | Hybrid | No changes
Lithuania | LITGRID | Power plants that are included in the black start plan must provide the black start service (due to technology). | Transmission grid | N/A | Regulated price | No | No special rules for distribution, black start service unit shall be located in such a place, where is feasible to restart main generation units. | No | No | No | No | Yes | No | No | No | Occasionally | Yes, it can be part of the power plant | N/A | N/A | Real time monitoring/tests | No changes
Luxembourg | CREOS | - | Transmission grid | N/A | N/A | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Malta | Enemalta | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
The Netherlands | TenneT NL | Black start is contracted and not a mandatory service | Both | Yes | Pay as bid | No | Black Start units are contracted in different parts of the network | Yes, 501-800 MW | No | No | No | Yes | No | No | No | Regularly/once a year | Yes, it can be part of the power plant | It is not allowed | N/A | Hybrid | No changes
Poland | PSE S.A. | It is not a mandatory service in Poland. | Both | Yes | Pay as bid | No | TSO is obliged to fullfill standards from OH Policy 5. | No | No | No | Yes | No | No | No | No | Regularly/several times a year | Yes, it can be part of the power plant | N/A | No | Hybrid | No changes
Portugal | REN | BS is not a mandatory service in Portugal. We have a CCGT and a Hydro that provide that service | Transmission grid | Yes | N/A | No | No special rules | No | No | No | No | No | Yes | No | No | Regularly/once a year | Yes, it can be part of the power plant | Depending on the availability of other BS units | No | Real time monitoring/tests | No changes
Romania | Transelectrica | Power plants that are included in the black start plan must provide the black start service - due to technology; | Transmission grid | No | N/A | N/A | Geographical distance according to respective black-start concept | No | Yes | No | No | No | No | No | No | Regularly | Yes, it can be part of the power plant | Depending on the availability of other BS units | No | Real time monitoring/tests | No changes
Slovakia | SEPS | No, this service is not mandatory. | Both | Yes | Regulated price | No | Yes, we have a set of different rules. Each application for BS providing is assessed separately. | No | No | No | No | No | No | No | Yes | Occasionally | Yes, it can be part of the power plant | Depending on the availability of other BS units | No | Hybrid | No changes
Slovenia | ELES | Yes | Transmission grid | Yes | Pay as bid | No | Prescribed amount of BS is area-dependent. | No | No | No | No | Yes | No | No | No | Occasionally | Yes, it can be part of the power plant | N/A | N/A | Ex post check | No changes
Spain | REE | Mainly hydro untis | Both | N/A | N/A | No | Adequate geographic distribution in order to warrant island operation | No | No | No | No | No | No | Yes | No | Regularly/several times a year | Yes, it can be part of the power plant | N/A | N/A | Real time monitoring/tests | No changes
Sweden | Svenska kraftnät | We have contracts with some suppliers of blackstart capability | Transmission grid | Yes | Free | No | Yes, we have a set of different criterias. | Yes, more than 800 MW | No | No | No | No | No | Yes | No | Regularly/several times a year | N/A | Depending on the availability of other BS units | N/A | Hybrid | No changes
GB/United Kingdom | National Grid | Not a mandatory service for generators. However, mandatory for NG to maintain black start capability - Grid Code and Transmission Licence requirements. Black Start services are procured via bilateral contracts with power stations. | Both | Yes | Pay as bid | No | Restoration strategy is to split GB into 6 geographical zones and contract for at least 3 black start providers from each zone. | No | No | No | No | No | No | Yes | No | Regularly | No, it has to be a single unit | More than one week | No | Real time monitoring/tests | No changes
| SHETL | [14 empty] | - | - | - | - | - | - | bar: Both Both to Yes No; No No to Yes N/A
| SPTransmission | [14 empty] | - | - | - | - | - | - | bar: Both Both to Yes No; No No to Yes N/A
> Northern Ireland | SONI | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Croatia | HOPS | All the units who are able to provide BS must provide it | Both | Yes | Regulated price | No | No. | All the units who are able to provide BS must to provide it | No | No | No | No | No | No | Yes | Regularly/several times a year | Yes, it can be part of the power plant | More than one week | No | Ex post check | No changes
Iceland | Landsnet | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Montenegro | Crnogorski elektroprenosni sistem AD | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Serbia | EMS | HPPs. It is mandatory according to Grid code | Transmission grid | Yes | Regulated price | N/A | N/A | All the units who are able to provide BS must to provide it | No | No | No | Yes | No | No | No | Occasionally | N/A | Depending on the availability of other BS units | No | Ex post check | No changes
The former Yugoslav Republic of Macedonia | MEPSO | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Turkey | TEIAS | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Albania | OST | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Bosnia and Herzegovina | ISO BIH | Yes | Transmission grid | No | N/A | No | No | N/A | No | No | No | Yes | No | No | No | Occasionally | No, it has to be a single unit | Depending on the availability of other BS units | No | N/A | No changes
Kosovo (UNMIK) | KOSTT | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Moldova | Moldelectrica | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Ukraine | Ukrenergo | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Norway | Statnett SF | Power plants that have a significance impact on the reconstruction of the network or other critical functions. | Both | N/A | N/A | No | Power plants that have a significance impact on the reconstruction of the network or other critical functions. | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Regularly | N/A | Depending on the availability of other BS units | No | N/A | No changes
Switzerland | Swissgrid | A buildup-cell is defined as a small subnet, limited in area and electrical network, which consists of one powerstationequipped with black start facilities and one or more powerstationswith islanding functionality being able to keep frequency, voltage and power stable in this buildup-cell, with an adequate load at its disposal. The buildup-cell needs: -to have a direct connection to the 220kV-level -to be connected to the same or neighboring nodes -Its rotating mass (power output) to be between 200 and 250 MW and a switchable load of 10% | Transmission grid | Yes | Pay as bid | No | Distribution of CH in 4 network restoration regions (West, South, Cetraland East): Each region must have 1 buildup-cell | Yes, more than 800 MW | No | No | No | Yes | No | No | No | Regularly/once a year | Yes, it can be part of the power plant | Depending on the availability of other BS units | No | Real time monitoring/tests | No changes
Monaco |  | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
San Marino |  | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Andorra | FEDA/RTE/REE | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Vatican City |  | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Liechtenstein | LKW | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A
Belarus |  | - | [13 empty] | - | - | - | - | - | - | bar: Both Both to Yes N/A