## DISCLAIMER
DISCLAIMER
ENTSO-E assume no liability in the case of any direct, indirect or subsequent damages which occur in any way in connection with the use of the information and the data contained in the TYNDP report or in any official ENTSO-E related document. Use of information and data is to be understood in the broad sense and would include, for example, transmission, display, reuse, reproduction, publication or creation of any derivative work. Irrespective of the above, any use of information and data contained in the TYNDP should enunciate the source of the data an information.

## TABLE OF PROJECTS
REF on map | RGs | Substation 1 | Substation 2 | Project characteristics | Investment need alleviated | Expected benefits | Progress status | Expected time of commissioning | TENE | Comments
1 | CSW | Frades B (PT) | Pedralva 1&2 (PT) | Creation of a new 400kV station in Frades B connected to Pedralva by means of two new 400kV, 40km lines. The realisation of this two connections can take advantage of some already existing 150kV single lines, which will be reconstructed as double circuit lines 400+150kV line and partially sharing towers with those 400kV circuits. | Integration of new hydro power plant in the area. | This project will provide higher RES integration and annual grid losses reduction. | design & permitting | 2015
2 | CSW | Pedralva (PT) | Alfena (PT) | New 50km double circuit Pedralva (PT) - Alfena (PT) 400kV OHL (only one circuit installed in a first step). | Integration of new renewable generation units (wind & hydro) and strengthen the Security of Supply to Porto area. | Expected benefits regard RES integration, increase of NTC and improved security of supply. | planned | 2016
3 | CSW | Pedralva (PT) | Vila Fria (PT) | New 55km double circuit Pedralva - Vila Fria 400kV OHL (one circuit installed), with needed extension of existing Vila Fria substation to include 400kV facilities. | The project is needed to increase the NTC with Spain, improve the capacity of the grid to receive new renewable energy (wind & hydro) in Northern Portugal and secure the supply to Vila Fria. | Expected benefits regard increased NTC, RES integration and improved security of supply. | design & permitting | 2013
4 | CSW | Frades B - Ribeira de Pena - Feira (PT) |  | New 160km double-circuit 400kV OHL Frades B (PT) -Ribeira de Pena (PT) - Feira (PT) (one circuit operated at 220kV between R. Pena and Feira) with a new 400/60kV substation in Rib. Pena. In a first step, only the 130km section Rib. de Pena (PT) - Feira (PT) will be constructed and operated at 220kV as Vila Pouca Aguiar (PT) - Carrapatelo (PT) - Estarreis (PT) (see project 6). In a second step, one circuit of this line will be operated at 400kV. | Integration of new hydro and wind power plant in Northern Portugal. | The project is expected to help RES integration and provide annual grid losses reduction. | planned | 2015
5 | CSW | Macedo de Cavaleiros (PT) | Vila Pouca de Aguiar (PT) | New 75km double circuit 400+220kV OHL (only 220kV circuit installed in the first step) Macedo de Cavaleiros (PT) -Valpaços (PT) - Vila Pouca de Aguiar (PT). | Integration of new renewable generation units and strengthen the Security of Supply to PT. | The project is expected to help RES integration (mainly wind) and improved the security of supply. In addition, an increase of ES-PT NTC is expected, due to reinforced exchange capacity on Douro border. | design & permitting | 2010
6 | CSW | V. P. Aguiar - Carrapatelo - Estarreja (PT) |  | New 400+220kV double circuit OHL (initially only used at 220kV) Vila Pouca Aguiar - (Rib. Pena) - Carrapatelo - Estarreja . Total length of line: 2x(90+49)km. | Integration of new renewable generation units and improving the Security of Supply. | RES integration (mainly wind) and improved security of supply. | design & permitting | 2012/2013
7 | CSW | Armamar - Bodiosa - Paraimo (PT) |  | This 120km double-circuit OHL has been constructed according to 400kV standards but is currently operated at 220kV as Valdigem (PT) - Bodiosa (PT) -Paraimo (PT). The project consists of operating one circuit at 400kV while creating a new 400/220kV substation in Armamar and upgrading the existing Bodiosa substation from 220/60kV to 400/60kV. Total length of line : 120km. | Insufficient capability of existing network to accommodate interior to littoral flows. | The project is expected to help RES integration, increase the NTC and improved the security of supply. | under construction | 2010
8 | CSW | V. Chã B - Arg./Góis - Penela - Paraimo / Batalha (PT) |  | New double circuit 400+220kV OHL (only 400kV circuit installed in a first step) Vila Chã B-Arganil/Gois-Penela (90km) plus new double circuit 400kV OHL (15km) to connect Penela substation to Paraimo - Batalha line. Two new 400/60kV substations at Vila Chã B and Arg./Góis are needed, as well as the expansion of the existing Penela substation to include 400kV facilities. | Insufficient capacity of the existing network to receive new renewable energy (wind and hydro). | The project is expected to help RES integration, improved the security of supply and reduce the annual grid losses. | planned | 2015/2016
9 | CSW | Guarda - Ferro B - (C. Branco) - Falagueira (PT) |  | New double circuit 400+220kV OHL Guarda (PT) -Ferro B (PT) -'Castelo Branco zone' (PT) (between Guarda and Ferro B only the 400kV circuit will be installed) plus new double circuit 400+150kV OHL 'Castelo Branco zone' (PT) -Falagueira (PT). New 400/60kV substations in Guarda and Ferro B. Total length of line: 135km. | Insufficient capacity of existing network to receive new renewable energy (mainly wind). | The project is expected to help RES integration, improved the security of supply and reduce the annual grid losses. | planned | 2013/2014
10 | CSW | Falagueira (PT) | Pego (PT) | New 40km double circuit 400kV OHL (only one circuit installed) substituting for an existing 150kV line. | Insufficient capacity to receive new renewable (wind and hydro) energy and need for alleviating some congestions near Falagueira (PT) substation. | The project is expected to help RES integration, increase the NTC and reduce annual grid losses. | planned | 2014
11 | CSW | Batalha-Lavos-Paraimo (PT) |  | Two new 400kV lines Batalha-Lavos and Lavos-Paraimo, needed to accommodate two new combined cycle power plants (4x435MW) on Littoral Central Region. Total length: 115km. | Needed to receive new CCGT power plants (4x435MW) that are in construction or permitting in Littoral Central Region. | The project is expected to help conventional generation integration, improved the security of supply and reduce annual grid losses. | under construction | 2010/2012
12 | CSW | Rio Maior - Alm. Bispo - Fanhões (PT) |  | New 71km double circuit 400kV OHL feeding Lisbon area from north with creation of a 400/220/60kV substation in Almargem do Bispo. A section of this reinforcement (between Rio Maior and Carvoeira zone) will be finished earlier included on a 400/220kV double circuit line linking Rio Maior and Carregado substations. | The project is needed to improve the security of supply to Lisbon Area. | The project is expected to improve the security & diversity of supply and reduce annual grid losses. | planned | 2016/2019
13 | CSW | Palmela - F. Ferro - Fanhões (PT) |  | Expansion of Fernão Ferro substation to include 400kV facilities and connection to the existent Palmela (PT) - Fanhões (PT) single circuit line by a new 25km double-circuit 400kV OHL. | The project is needed to improve the security of supply on Setúbal Peninsula area. | The project is expected to improve the security & diversity of supply and reduce annual grid losses. | design & permitting | 2012
14 | CSW | Marateca - Pegões - Fanhões (PT) |  | New 90km double-circuit 400kV OHL (one circuit only installed between Pegões and Fanhões). This new line will be connected to already existing line Palmela (PT) - Sines 2 (PT) , so making a direct link Sines-Pegões (PT) -Fanhões (PT) substations. | Congestions on existing network due to north-to-south flows. | Conventional generation integration, improved security of supply and increase of NTC. | design & permitting | 2012
15 | CSW | Falagueira-Estremoz - Divor - Pegões (PT) |  | New 400/60kV substations in Pegoes and Divor connected by a new 116km Pegoes (PT) - Divor (PT) - Estremoz (PT) single circuit 400kV OHL. In addition, the operating voltage of the existing Estermoz substations and the 93km single circuit Falagueira (PT) -Estremoz (PT) 150kV OHL will be changed to 400kV (were prepared for that). | Special needs for TGV projects and reinforcement to Estremoz and Évora supply. | The project is expected to improve the security of supply, increase the NTC and reduce annual grid losses. | design & permitting | 2012
16 | CSW | Aldeadávila (ES) | Lagoaça (PT) - Armamar (PT) - Recarei (PT) | New Duero Interconnection 400kV New 400kV OHL interconnection line Aldeadávila (ES) - Lagoaça (PT) , including new Lagoaça substation (PT). Also associated, the lines Lagoaça-Armamar-Recarei 400kV in PT and the Armamar (PT) 400/220kV substation. On a first phase (2009) a new 400/220kV substation (Lagoaça - PT) will be created with only 220kV level installed, and there will be some rearrangements and reinforcements on the local 220kV network structure. On river crossing a new 220kV double line with separated circuits, firstly Aldeadavila (ES) - Lagoaça (PT) 1 & 2 and changing later to Aldeadavila (ES) - Pocinho (PT) 1 & 2, will substitute the existing two 220kV lines Aldeadavila (ES) – Bemposta (PT) and Aldeadavila (ES)-Pocinho (PT). Total length: 1km (ES)+105km (PT). | Limitations and congestions on the 220kV network in the Douro area where new hydro power stations (~800MW) are in construction or permitting in Portugal, in addition to export/import situations between Portugal and Spain. | Increase of NTC (From today 1100-1500MW up to 1500-2000MW), RES integration and conventional generation integration. Support in Iberian (ES+PT) market integration in MIBEL. | design & permitting for 400kV under construction for Lagoaça substation and 220kV restructuring in Portugal | 2009/2010 | X
17 | CSW | Guillena (ES)-Puebla de Guzman (ES) | Tavira (PT)-Portimao (PT) | New Southern Interconnection New 400kV OHL double-circuit line between Guillena (ES)-Puebla de Guzman (ES) - Tavira (PT) - Portimão (PT), including new Tavira (PT) and P.Guzman (ES) 400kV substations. On the interconnection section P.Guzmán (ES) –Tavira(PT), initially only one circuit will be placed. Total length: 153km (ES)+110km(PT). | Congestion that occurs on the existing 400kV line Alqueva (PT) -Brovales (ES) at high level of exportation from Portugal to Spain, limiting exchange capability from Portugal to Spain. | The project is expected to increase NTC (up to 3000MW from Portugal to Spain), help RES integration and improved the security of supply. Support in Iberian (ES+PT) market integration in MIBEL. | design & permitting | 2011 | X
18 | CSW | O Covelo (ES)-Boboras (ES) | Vila Fría (PT)- Vila Conde (PT) - Recarei (PT) | New double circuit 400kV OHL between O Boboras (ES) -O Covelo (ES) - Vila Fria (PT) - Vila do Conde (PT) - Recarei (PT), including new 400kV substations O Covelo (ES), Boboras (ES), Vila Fria (PT) and Vila do Conde (PT). On the section O Covelo (ES) – Vila do Conde (PT), only one circuit will be placed. Total length: 43km (ES)+112km (PT). | Congestion on the existing 400kV line Cartelle (ES) -Lindoso (PT) at high level of exportation from Spain to Portugal. Special needs for High Speed Train projects. | The project is expected to increase NTC (up to 3000MW from Spain to Portugal), help RES integration and improved the security of supply. General Benefit: Market integration in MIBEL. | design & permitting | 2014 | X
19 | CSW | Vic (ES) | Pierola (ES) | Upgrading (uprating) the existing 75km single circuit Vic-Pierola 400kV line in order to increase its capacity from 1360 MVA to 1710 MVA. | Congestions in the FR-ES border. Necessity of adapting the existing network to the new Eastern interconnection. | Increase of NTC and improved of security of supply. | design & permitting | 2010
20 | CSW | Arkale (ES) | Hernani (ES) | Upgrading the existing 12km single circuit Arkale-Hernani n°2 220kV OHL in order to increase its capacity up to 670 MVA. | Overloads in this line in high export situations to France. | Increase of NTC and RES integration. | design & permitting | 2011
21 | CSW | Aldeadavila (ES) JM Oriol (ES) | Villarino (ES) Arenales (ES) | Upgrading the existing 18km Aldeadávila-Villarino 400kV OHL in order to increase its capacity from 1350MVA to 1690MVA. New 220kV JM Oriol-Arenales, and new Arenales substation. | Limitations in the NTC values from Portugal to Spain. | Increase of NTC on ES-PT border, around 2000MW from PT to ES in some peak situations. RES integration and annual re-dispatching cost reduction. | design & permitting | 2012/2014
22 | CSW | Boimente (ES) | Ichaso (ES) | North axis Project between Galicia and the Basque Country. Part of the project is considered as the Asturias Ring. New 162km double circuit Boimente-Pesoz- Grado 400kV OHL. Change of voltage level of the existing 50km Soto-Tabiella single circuit from 220kV to 400kV, and connection as input/output in Grado. New 178km single circuit Soto-Penagos 400kV OHL. New 96km double circuit Aguayo/Penagos-Abanto 400kV OHL New 34km double circuit Zierbena-Abanto-Gueñes 400kV OHL. New 120km double circuit Gueñes-Ichaso OHL. New 58km double circuit Gozón-Carrio-Lada -Sama 400kV OHL. It is expected to use the corridors of existing lower voltage lines for some sections. New 124km double circuit Sama-Velilla 400kV OHL. Upgrading (uprating) the 73km single circuit Lada-Robla 400kV OHL in order to increase its capacity by around 300 MVA. It includes new 400kV substations Pesoz, El Palo,Salas, Grado, Gozón, Sama, Carrio, Valle del Nalon, Costa Verde, Penagos, Solorzano, Abanto and Ichaso, with transformers to 220kV. | Congestions in the 400kV lines between the north-western area and the East, because of the attraction of this area as a production site. Congestions in the 220kV network due to the increase of demand in Cantabria, that has today only one 400kV injection from the south. Constraints in the north-to-south direction due to the expected increase of generation in the north-West and north-East areas. Limitations of production of Santurce and Zierbena power plants (high concentration of generation), which sole evacuation line (Santurce-Gueñes) has a slight capacity. | The project is expected to help mainly RES and also conventional generation integration. It will allow to connect regional networks and enhance mutual support. In addition, security and quality of supply in some north Spain areas will be improved. | design & permitting | 2010/2015 | X | TEN support for studies concerning: Lada-Velilla, Boimente-Narcea, Soto-Penagos, Penagos-Gueñes and Gueñes-Ichaso, Santurce evacuation
23 | CSW | Vitoria (ES) | Magallon (ES) | Northern part of the new Cantabric-Mediterranean axis. New 144km double circuit Castejón-Muruarte-Dicastillo-Vitoria 400kV OHL, with new 400kV substations in Muruarte and Dicastillo with 400/220kV transformers New 32km double circuit La Serna-Magallón 400kV OHL. | The project is needed to accommodate geographical unbalances between production (in Northern Spain) and consumption (Mediterranean area) that otherwise would produce congestion in the 400kV corridors of Valladolid/Palencia-Madrid and Aragón/Cataluña-Levante. Need to alleviate congestion on the 220kV network supplying Pamplona. Also need to alleviate congestions on the 400kV and 220kV network between La Serna and Magallón in several production profiles (mainly with high wind power energy) and after contingencies. | The project is expected to improve RES integration, security of supply and reduce annual re-dispatching cost. | design & permitting | 2011/2012 | X | TEN: La Serna-Magallon
24 | CSW | Fuendetodos (ES) | Eliana Turis (ES) | Southern part of the new Cantabric-Mediterranean axis. New 110km double circuit Fuendetodos-Muniesa-Mezquita-Morella 400kV OHL. New 77km double circuit Teruel-Mudejar-Morella 400kV-OHL. New 78km double circuit La Plana-Morella 400kV OHL substituting to the existing single circuit line. New 63km single circuit La Eliana-La Plana 400kV OHL and upgrading (uprating) the existing line. New 162km double circuit Mezquita-Platea-Turis 400kV OHL. As a first step, in 2012, the new Turis substation will be equipped with a 400/220kV transformer and connected to the existing 400kV lines Cofrentes-La Eliana, and Catadau-Requena 400kV lines. New 400kV substations Mezquita, Platea, Muniesa, and Mudejar with 400/220kV transformer units Upgrading (uprating) the existing 76km Aragón-Peñaflor 400kV OHL | The project is needed to accommodate geographical unbalances between north of Spain and Mediterranean area, that otherwise would produce congestion in 400kV existing corridors. Necessity of integration of wind power energy in an area without enough transmission network. In addition, congestion is expected in Levante area because the low capacity of the existing La Eliana-La Plana 400kV OHL is not sufficient to cope with the high flows coming from the northwest to supply the high increase of demand in Levante. | RES integration, improved security of supply and conventional generation integration. | design & permitting | 2011/2014
25 | CSW | Aragón (ES) - Isona (ES) & Escatron (ES) - La Secuita (ES) |  | New 167km double circuit Aragón/Peñalba-Monzón II-Isona 400kV OHL with new 400kV substations Monzón II and Isona, and a 400/220kV transformer in Monzon II. New 60km single circuit Escatrón-Els Aubals-La Secuita 400kV OHL with a new 400kV substation in Els Aubals with 400/220kV transformer. | Congestion on existing grid due to unbalanced production and consumption between Aragón and Cataluña. | The project is expected to benefit in Annual re-dispatching cost reduction and higher RES & conventional generation integration. | design & permitting | 2013/2014
26 | CSW | Catadau (ES) | Benajama (ES) | New 123km double-circuit Catadau-Jijona-Benejama 400kV OHL using the right-of-way of the existing 220kV lines that will be dismantled. A new 400kV substation will be created at Jijona and transformers installed in Jijona and Catadau. | Congestions due to the low capacity of the Benejama-Jijona-Catadau axis, that faces overloads due to high north-to-south flows to supply the Levante demand. | The project should improve the security of supply and reduce the annual grid losses. | design & permitting | 2015
27 | CSW | Morvedre (ES) | Santa Ponsa (ES) | Connection of Balearic Islands to Mainland New bipolar 2x200MW HVDC (LCC) 250km connection between Morvedre (mainland) and Santa Ponsa (Mallorca) via 250kV. subsea cable. In addition, Mallorca will be connected to Menorca with a new HVDC 120km link between Santa Ponsa (Mallorca) and Torrente (Menorca). A second connection between Mallorca and Ibiza (60km) will also be constructed. | Need of connecting Balearic Islands (isolated system) to the Continental Europe system through the Spanish mainland. | Expected benefits are an improved security & diversity of supply and connection of isolated areas. | design & permitting | 2011 | X
28 | CSW | Cofrentes (ES) | Pinilla (ES) | New 82km single circuit Cofrentes-Ayora-Campanario-Pinilla 400kV OHL. This project also includes a new 400kV substation in Campanario. | Necessity of mutual support between two axis of 400kV Cofrentes-Benejama-Rocamora and Romica-Rocamora to avoid overloads in contingencies. Look for a possibility to allow more wind power production in the Peñarrubia area. | Expected benefits regard RES integration, annual re-dispatching cost reduction and CO2 emission mitigation. | design & permitting | 2012
29 | CSW | Cartuja (ES) | Guadame (ES) | New 94km double circuit Cartuja-Arcos de la Frontera-La Roda-Cabra-Cordoba-Guadame 400kV OHL . It includes new 400kV substations Cartuja and Cordoba, with 400/220kV transformers. | The concentration of generation (combined cycle and wind power energy) in the Cadiz and Tajo de la Encantada area causes constraints, in contingency situations, in the 400kV and 220kV network in case of high production profiles. | The project will help RES & conventional generation integration and Improved the security of supply. | design & permitting | 2010/2013 | X
30 | CSW | Don Rodrigo (ES) | Almaraz (ES) | Two new double circuit 400kV OHL: Guillena-Guadaira-Don Rodrigo and Guillena-Brovales-Arroyo S.Servan-Alcuescar- Almaraz. This project also includes new 400kV substations in Arroyo S.Servan, Alcuescar and Guadaira with 400/220kV transformers. Total length : 383km. | Expected overloads in the existing link between Extremadura and Sevilla in both directions, depending on the future production profile (new generation in both areas, but mainly in the south). Limits to the PT-ES NTC due to overloads in Alvarado-Balboa 220kV line in profiles from Portugal to Spain. Necessity of increase the flows to supply the high demand in Madrid. | The project is expected to improve the security of supply and help conventional, RES generation integration and avoid limits to NTC from Portugal to Spain. | design & permitting | 2012/2015
31 | CSW | Caparacena (ES) | La Ribina (ES) | New 177km double circuit Caparacena-Baza-La Ribina 400kV OHL, with two new 400kV substations in Baza and La Ribina (these substations will be also connected to existing El Palmar-Litoral 400kV line ). In addition, the existing 173km single circuit Litoral-Tabernas-Hueneja-Caparacena 400kV line will be upgraded (uprated) in order to increase its capacity from 1310 to 1590 MVA. | Necessity of integration of wind and solar power energy in addition to a new pump storage in the area of Baza. It takes the advantage to support the distribution. Need to alleviate the overloads in the 400kV Caparacena-Hueneja in some production profiles. | The project is expected to improve RES (especially wind & solar energy) integration, diversity & security of supply. | design & permitting | 2012/2013
32 | CSW | several 400kV lines concerned (ES) |  | Upgrading several 400kV lines in the area between Aldeadávila, the south of Extremadura, Madrid and the Portuguese border. | Need of alleviating expected overloads in some 400kV lines in contingency situation, due to the new generation projects in Extremadura and south of Madrid. | The project should improve security of supply, conventional generation integration and RES integration. | design & permitting | 2008/2011
33 | CSW | Romica (ES) | Brazatortas (ES) | Transmanchega project (total length 255km) New double circuit line Romica-Manzanares-Brazatortas 400kV OHL. New substation Manzanares with a 400/220kV transformer unit. The new 400kV substation Brazatorta will be commissioned in 2012 and connected to the existing line Guadame-Valdecaballeros. | The project is needed for integration of wind energy (insufficient capacity of existing network to transmit the power). In addition, the 220kV network supplying Ciudad Real is close to congestion and would need some support. | The project is expected to provide higher RES integration and improved security of supply. | design & permitting | 2013/2015
34 | CSW | Trives (ES) | Moraleja (ES) | SUMA Project (using part of an existing 220kV corridor) New 201km single circuit Trives-Aparecida-Valparaiso-Tordesillas 400kV OHL. New 130km double circuit Tordesillas-Segovia/Herreros- Galapagar/(El Cereal-SS Reyes) 400kV OHL New 33km double circuit Galapagar-Moraleja 400kV OHL (substituting for the existing line) and new PST in the 400kV line Galapagar-Moraleja. Upgrade of the 21km existing single circuit Loeches-SS Reyes 220kV OHL to 400kV in order to increase its capacity. New 33km double circuit 400kV Mudarra-Tordesillas OHL and upgrade of the existing 25km single-circuit Mudarra-Tordesillas 400kV line in order to increase its capacity. The project includes new 400kV substations in Aparecida and Herreros . | Congestion from the northwest area to the centre of the country due to the attraction of Galicia as a production site (conventional and wind power plants). The new expected generation in north-Western Spain causes overloads on the lines transmitting the power to Madrid. High flows on Madrid ring cause congestion on the existing Galapagar-Moraleja and SS.Reyes-Loeches 400kV lines. | The project is expected to reduce annual re-dispatching cost, improved the security of supply and help RES integration. It will also help conventional energy integration. | design & permitting | 2011/2015
35 | CSW | to be determined (ES) | to be determined (ES) | Reinforcements in the 220kV network overall the country, in addition to upgrading of 300km of 220kV network , due to wind power evacuation. | Lack of network capacity to evacuate wind power energy, and congestion in some 220kV lines. | These projects will provide higher RES integration. | design & permitting | 2009/2014
36 | CSW CCS North Sea | Sta.Llogaia (ES) | Baixas (FR) | New HVDC (VSC) bipolar interconnection in the Eastern part of the border, via 320kV DC underground cable using existing infrastructures corridors and converters in both ending points. The thermal capacity is expected in the range 2x825-2x1000MW. Total line length: 60km | Limited NTC in both directions and limitations to the integration of wind power energy in the Iberian Peninsula. | The project will provide increased cross-border capacity, up to 2800 MW from FR to ES (today 1400MW), higher RES integration and improved security of supply. The project increases the security of the system in case of major incidents. Close to the diversity of supply benefits, decrease in CO2 emissions is expected. | design & permitting | 2014 | X | European Coordinator Mr. Mario Monti appointed by DGTREN. There is a political agreement on the proposed solution.
37 | CSW | Santa Llogaia (ES) | Bescanó (ES) | New 119km double circuit Sta.Llogaia-Ramis-Bescano-Vic/ Senmenat 400kV OHL (single circuit in some sections) New 400kV substations in Bescano, Ramis and Sta.Llogaia, with 400/220kV transformers in Ramis and Bescano. | Necessity of adapting the existing network to the new Eastern interconnection. Congestions mainly in the 400kV Vic-Baixas line and in Catalonian area in contingencies. Not enough transmission network for the connection of new generation in the Bescano area and support to the security of supply in the Girona area. | The project will provide an increase of NTC, improved the security of supply and support RES integration. | design & permitting | 2010/2012 | X
38 | CSW CCS North Sea | tbd (ES) | tbd (FR) | New cross-border line - not in the French department "Pyrenees Orientales" nor in the Spanish region of Cataluña. | Limited NTC of the ES- FR border in both directions. | Increase of interconnection capacity, up to 4000MW. | under consideration | long term | X
39 | CSW CCS North Sea | Avelin (FR) | Warande (FR) | Reconductoring (with ACSS) of both circuits of existing 400kV OHL between Avelin, Weppes & Warande. Total length : 85km | Need to alleviate congestion due to generation evacuation in Northern France | The project will reduce annual re-dispatching costs and improve the overall capability of the network to accommodate international power exchanges in the area. | under construction | 2010
40 | CSW CCS North Sea | Avelin (FR) Mastaing (FR) |  | Installation of a 3rd busbar in Avelin (existing 400-kV substation) & replacement of components to increase the ability to withstand short-circuit power; Connection of Mastaing (existing 400kV substation) to existing 400kV circuit between Avelin (FR) & Lonny (FR) | Need to alleviate congestion due to generation evacuation in Northern France | These projects will help conventional generation integration and improve the security of supply and the overall capability of the network to accommodate international power exchanges in the area. | under construction | 2012
41 | CSW CCS North Sea | Fruges, Sud-Aveyron, Marne-Sud, Somme (FR) |  | New 400-kV substations connected to existing 400-kV network and equipped with transformers to 220 kV or high voltage networks | Need to connect new wind generation | These projects will result in higher RES integration. | design & permitting / under consideration | mid term
42 | CSW CCS North Sea | Lonny (FR) | Vesle (FR) | Reconstruction of the existing 70km single circuit 400kV OHL as double circuit OHL. | Need to alleviate congestion on the grid in Northern France (future generation evacuation + exchanges with Belgium) | The project will result in higher RES and conventional generation integration. | under consideration | long term (>=2019)
43 | CSW CCS North Sea | Mandarins (FR) |  | Replacement of thyristors in the AC/DC substation (IFA 2000 interconnector, DC voltage 270 kV) | Ageing/obsolescence of Mandarins converters | Reduction of infrastructure vulnerability | design & permitting | 2011
44 | CSW CCS North Sea | Havre (FR) | Rougemontier (FR) | Reconductoring (with ACCS) of existing 54km double circuit 400kV line. | Need to integrate future conventional generation | The project will improve conventional generation integration, resulting in at least 2000MW generation evacuation capacity in Le Havre area. | design & permitting | 2015
45 | CSW CCS North Sea | Taute (FR) | Oudon (FR) | "Cotentin-Maine "Project : new 163km double circuit 400kV OHL connected to existing network via two new substations in Cotentin and Maine regions. | Need to integrate Flamanville 3 nuclear power plant | The project will result in a generation evacuation capacity of 2100 MW in Cotentin area, for conventional units and RES. | design & permitting | 2012
46 | CSW CCS North Sea | Baixas (FR) | Gaudière (FR) | Reconductoring of existing 70km double circuit 400kV OHL to increase its capacity. | Congestion is expected on existing asset due to increased exchanges with the Iberian peninsula | The project will result in increased ability to cope with higher exchanges with the Iberian peninsula. | under consideration | 2014
47 | CSW CCS North Sea | Tamareau (FR) | Tavel (FR) | Reconductoring with ACCS of both circuits of existing 92km double circuit 400kV OHL to increase its capacity. | Congestion on existing asset due to high East to West power flows between Fos and Rhone Valley generation areas and South Western France; risk of energy not supplied to consumers in the Herault department. | The project will improve the security of supply of the Herault department and the ability of the network to accommodate generation in South-Eastern France. | under construction | 2010
48 | CSW CCS North Sea | Gaudière (FR) | Rueyres (FR) | Reconductoring limiting sections (10 km) of existing single circuit 400kV OHL to increase its capacity. | Congestion on existing asset limiting existing generation evacuation, especially in the context of high international power flows. | The project is expected to result in reduced annual re-dispatching costs and improved overall capability of the network to accommodate international power exchanges in the area. | design & permitting | 2012
49 | CSW CCS North Sea | Cantegrit (FR) | Mouguerre (FR) | Reconductoring (with ACSS) of existing 83km single-circuit 220kV OHL to increase its capacity. | Congestion on existing asset, especially in the context of high flows to Spain on the Western axis of the France-Spain interconnection, resulting in potential risk of energy not supplied to consumers or NTC limitation. | The project will improve the security of supply of Bayonne area and also the overall capability of the network to accommodate different patterns of power flows on the Eastern and Western axes of the French-Spanish interconnection | design & permitting | 2011
50 | CSW CCS North Sea | Néoules (FR) | Broc-Carros (FR) | The second circuit (formerly operated at 220kV) of a 197km double-circuit 400kV OHL will be operated at 400kV and 400/225 autotransformers installed in relevant substations. | Congestion due to thermal capacity of existing assets of Provence - Alps-Côte d'Azur (PACA) Region and voltage control problems, resulting in risks of load-shedding in the region. | The project will improve the security of supply of PACA region | under construction | 2010 |  | This project is the consequence of the 2006 cancellation of the permit for a new 400 kV OHL between Boutre and Broc-Carros.
51 | CSW CCS North Sea | Boutre (FR) | La Bocca (FR) | PACA "Filet de sécurité" project: construction of 3 new 220kV underground cables (Boutre - Trans [72 km], Biançon - Fréjus [26 km] & Biançon - La Bocca [16 km]) and installation of reactive power compensation devices in 220 kV Boutre and Trans substations | Congestion due to thermal capacity of existing assets of Provence - Alps-Côte d'Azur (PACA) Region and voltage control problems, resulting in risks of load-shedding in the region | The project will improve the security of supply of PACA region | design & permitting | 2015 |  | This project complements Project 50 just above; needs DSM measures and new generation units in order to be fully efficient.
52 | CSW CCS North Sea | Feuillane (FR) | Realtor (FR) | Operation at 400 kV of existing 63km double circuit OHL previously operated at 220kV | Limitation to future conventional generation in Fos area. | The project will improve the integration of conventional generation: ability to evacuate up to 1400 MW generation in Fos area | under construction | 2011
53 | CSW CCS North Sea | Coulange (FR) | Le Chaffard (FR) | Reconductoring (with ACCS / ACCR) of two existing double circuit 400kV OHL (Coulange - Pivoz-Cordier - Le Chaffard and Coulange - Beaumont-Monteux - Le Chaffard) to increase their capacity. Total length of both lines: 275km | Need to alleviate congestion in the Rhone Valley. | The project is expected to provide annual re-dispatching costs reduction while improving the overall capability of the network to accommodate international power exchanges in the area | design & permitting | 2016
54 | CSW CCS North Sea CSE | Cornier (FR) | Piossasco (IT) | Replacement of conductors (by ACCS) on Albertville (FR) - Montagny (FR) - Cornier (FR) and Albertville (FR) - La Coche (FR) - La Praz (FR) - Villarodin (FR) - Venaus (IT) - Piossasco (IT) single circuit 400kV OHLs. In addition, change of conductors and operation at 400kV of an existing single circuit OHL between Grande Ile and Albertville (FR) currently operated at lower voltage, and associated works in Albertville (FR) 400kV substation. (Total length of lines : 257 km) | Need to increase cross-border capacity between France and Italy and, on the French side, improve the quality of supply of Savoie. | This upgrade of the existing assets is expected to provide an increase by about 600 MW of FR-IT NTC, improving the security of supply of the system. | under construction | 2012 | X
55 | CSW CCS North Sea CSE | Grande Ile (FR) | Piossasco (IT) | "Savoie - Piémont" Project : New 190km HVDC (VSC) interconnection FR-IT via underground cable and converter stations at both ends (two poles, each of them with 500MW capacity). The cables will be laid in the security gallery of the Frejus motorway tunnel and possibly also along the existing motorways' right-of-way. | Need to increase cross-border capacity between France and Italy. | The project will provide an increase of FR-IT NTC by about 1000MW, resulting in higher security of supply for the system. | design & permitting | long term | X
56 | CSW CCS North Sea CSE | Camporosso (IT) |  | New 450 MVA PST in Camporosso (IT) 220kV substation on Camporosso (IT) - Menton (FR) - Trinité-Victor (FR) OHL. | Need to increase the security of supply in both French Cote d'Azur and Italian Liguria areas. | The project allows to operate the 220kV link closed, which provides improved security of supply of the area and a small increase of NTC between France and Italy. | under construction | 2011 | X
57 | CSW CCS North Sea | under consideration (FR) | under consideration (CH) | Reinforcement of the interconnection in the area of Geneva's lake. | Need to increase cross-border capacity of France with Switzerland and Italy. | The aim is to increase cross-border capacity; improved RES integration is also expected. | under consideration | long term
58 | CCS CCE North Sea Baltic Sea | Ensdorf (DE) | St. Avold (FR) | Change of conductors on the German part of this single circuit 220kV line (9 km) and installation of a phase-shifter in Ensdorf (DE) 220kV substation. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Improved security of supply and small increase of NTC | planned | mid term
59 | CSW CCS North Sea | Moulaine (FR) | Aubange (BE) | Installation of a second circuit on the existing 220kV cross-border OHL | Need to increase the cross border capacity on BE-FR border | The NTC will be increased by 300 MW (winter) / 150 MW (summer). | under construction | 2010 | X
60 | CSW CCS North Sea | under consideration (FR) | under consideration (BE) | to be determined. | Need to increase the cross border capacity on BE-FR border | Increase of NTC. | under consideration | long term
60a | North Sea | Lillo (BE) | Mercator (BE) | Doubling of the axis Zandvliet-Mercator via Lillo by erecting a new 35km 380kV double circuit OHL with 1500 MVA capacity. | Needed to avoid overloading of the line during certain contingencies as a result of new generation and increasing demand. | Conventional generation integration; improved security of supply; Increase of NTC. | design & permitting | 2018
61 | CSW CCS North Sea | Moulaine (FR) | Belval (LU) | Connection of SOTEL (industrial grid in LU) to RTE network by mixed (underground cable & OHL) single circuit 220kV line. Parts of the new line use existing ones. | SOTEL request for connection to RTE grid. | Improved the security of supply of SOTEL's customers connected to Belval substation. | design & permitting | 2010 |  | connection of a customer
62 | CSW CCS North Sea | under consideration (FR) | under consideration (UK) | New subsea DC link, between GB and FR, possibly with a capacity of 1000MW (still to be determined). | Need for increasing interconnection capacity GB-continent. | Increase of FR-GB NTC by about 1000MW (still to be determined). | under consideration | ca. 2017
63 | CCS | Lienz (AT) | Veneto region (IT) | The project foresees the reconstruction of the existing 220kV-interconnection line as 380kV-line on an optimized route to minimize the environmental impact. Total length should be in the range of 100-150km. | Increase cross border capacity between Italy and Austria complying IEM. | The project is expected to improve the security of supply and increase the NTC. | planned | long term
64 | CCS | Bressanone (IT) | New substation near Innsbruck (AT) | New double circuit 400kV interconnection through the pilot tunnel of the planned Brenner Base Tunnel. Total line length: 65km. | Need to increase the cross-border capacity between Italy and Austria. | The project is expected to increase the NTC and Improved the security of supply. | under consideration | 2020/2025 | x
65 | CCS | Curon (IT)/ Glorenza (IT) | New substation close to the border in AT | New 380/220kV substation in AT directly located near the border ; erection of a 24km single circuit 220kV-connection via OHL and underground cable till Graun (IT) and upgrade of the existing line Graun (IT) – Glorenza (IT). | Need to increase the cross-border capacity between Italy and Austria. | The project is expected to increase the NTC and Improved the security of supply. | under consideration | long term
66 | CCS CSE | Prati di Vizze (IT) | Steinach (AT) | Upgrade of the existing 44km Prati di Vizze (IT) – Steinach (AT) single circuit 110/132kV OHL, currently operated at medium voltage and installing a 110kV/132kV PST in Steinach (AT). | Need to increase the cross-border capacity between Italy and Austria. | The project is expected to increase the NTC and Improved the security of supply. | design & permitting | short term
67 | CCE CCS CSE | Divaca (SI) |  | Installation of a new 400kV PST to assist control of power flows to Italy on secure level and secure the operation of Slovenian grid enabling full utilisation of regional market. | The project will provide improved security of supply, increased NTC and reduced re-dispatching costs & grid losses. | Improved security of supply, increase of NTC, annual re-dispatching costs reduction and annual losses reduction. | under construction | short term | X
68 | CCE CCS CSE | Okroglo (SI) | Udine (IT) | New 120km double-circuit 400kV OHL with installation of a PST in Okroglo. The thermal rating will be 1500 MVA per circuit. | Need for strengthening the connection between Slovenia and Italy and increasing of power exchange capability. | The project will increase NTC, improved the security of supply and achieve the diversity of supply. The PST in Okroglo substation will secure the operation of Slovenian grid, enabling full utilisation of regional market. | planned | long term | X | Common agreement between IT and SI TSOs
69 | CCE CCS CSE | Candia (IT) | Konjsko (HR) | New 1000MW HVDC interconnection line between Italy and Croatia via 280km 500kVDC subsea cable and converters stations at both ending points. | Need to increase the cross border capacity between Croatia (and South East Europe in general) and Italy. | The project is expected to increase the NTC and Improved the security of supply. | Under consideration | long term
70 | CCS CSE | Villanova (IT) | Tivat (ME) | New 1000MW HVDC interconnection line between Italy and Montenegro via 375km 500kV DC subsea cable and converter stations at both ending points. | Increase cross border capacity between South East Europe area and Italy complying IEM. | increase of NTC , improved Security of Supply. | design & permitting | 2014/2015 | X
71 | CCS CSE | Brindisi (IT) | Babica (AL) | 500MW single pole HVDC Merchant Line between Italy and Albania via 290km 400kV DC subsea cable and converter stations at both ends. On the Italian side, the new line will be connected to the existing substation of Brindisi South. | Need to increase the cross border capacity between South East Europe area and Italy. | The project is expected to increase the NTC and Improved the security of supply. | design & permitting | 2013/2014 |  | Merchant line
72 | CCS CSE | Aetos(GR) | Galatina (IT) | Second 500MW HVDC link between Greece and Italy via 316km 400kVDC subsea cable and converters stations at both ends. | Increase cross border capacity between Balkan area and Italy complying IEM. | Increase of NTC and Improved security of supply. | under consideration | 2020/2025
73 | CCS | El Aouaria (TU) | Partanna (IT) | New 350km 500MW HVDC line between Tunisia and Italy via Sicily with 400kV DC subsea cable and converters stations at both ends. | Need to increase the cross border capacity between Italy and North Africa. | The project is expected to increase the NTC, improved the security of supply and allow for integration of different markets. | design & permitting | 2015
74 | CCS CSE | Chiaramonte Gulfi (IT) | Sorgente (IT) | Realization of 380kV ring grid, trough the construction of 3 new 380kV line: "Chiaramonte Gulfi - Ciminna", "Sorgente - Ciminna" and "Paternò - Priolo". It will be realized a new 380/150kV substation in Caltanissetta area and the voltage upgrade of the existing Ciminna substation up to 380kV. Total line length: 365km. | Congestion on the existing 220kV Sicily network. Future generation evacuation. Energy transfer from Western to Eastern part of Sicily. | RES integration, annual losses reduction and Improved security of supply. | planned | 2015/long term
75 | CCS CSE | Sorgente (IT) | Rizziconi (IT) | New 90km double circuit 400kV line, partly via subsea cable and partly via OHL. This line is part of a larger project that foresees the creation of the future 400kV ring grid of Sicily. | Need of increasing transport capacity between Sicily and Mainland, improving the security of supply (securing the coverage of energy demand and decreasing the probability of loss of load). | The project will support RES integration (by transmitting wind power from Sicily to mainland), reduce grid losses and Improved the security of supply (by avoiding the risk of Sicily tripping to isolated operation). | under construction | 2013
76 | CCS CSE | Partanna (IT) | Ciminna (IT) | New 65km single circuit 400kV OHL in Sicily between existing Partanna and Ciminna substations. | Future generation evacuation. | The project will support RES integration, increase the NTC and reduce the re-dispatching costs. | planned | long term
77 | CCS CSE | Partinico (IT) | Fulgatore (IT) | New 45km single circuit 400kV OHL between Partinico and Fulgatore in Western Sicily. | The project is needed to improve the continuity of service, transmit power from future generation and make possible the interconnection with North Africa. It will also foster the connection of wind power plants foreseen in the area. | The project will support RES integration and reduce grid losses & re-dispatching costs. | planned | 2015
78 | CCS CSE | Piana degli Albanesi (IT) |  | New 220/150kV substation, complying with 400kV standards, connected to the Ciminna substation with a new 400kV line and in & out the existing Bellolampo-Caracoli 400kV line. | Congestion on the 220kV network in the Palermo area. | Improved security of supply and annual losses reduction. | planned | long term
79 | CCS CSE | Agrigento (IT) |  | New 220/150kV substation, complying with 400kV standards. The new substation will be connected in and out to the existing Partanna-Favara 400kV line . | Congestion on the 150kV network in the Agrigento area. | Improved security of supply and annual losses reduction. | planned | long term
80 | CCS CSE | Noto (IT) |  | New 220/150kV substation, complying with 400kV standards, connected in and out to the existing Ragusa-Melilli 400kV line. | The project will improve the security of supply and reduce the grid losses. | Improved security of supply and annual losses reduction. | planned | long term
81 | CCS CSE | Trino (IT) | Lacchiarella (IT) | A new 380kV double circuit OHL between the existing 380kV substations of Trino and Lacchiarella in North West Italy area. Total line length: 95km, Voltage upgrade of the existing Magenta 220/132kV substation up to 380kV. | The project is expected to help conventional generation integration, improve the security of supply and reduce grid losses. | Conventional generation integration, improved security of supply and annual losses reduction. | design & permitting | short term
82 | CCS CSE | Chignolo Po (IT) | Maleo (IT) | A new 380kV double circuit OHL between the new 380kV substations of Chignolo Po and Maleo in Lodi area. Restructuring of HV network. Total line length: 22km. | Congestion of the 380kV in north West /north East area due to further increase of generation in Piemonte-Lombardia and the development of the Italian-French interconnection. | Conventional generation integration, improved security of supply and annual losses reduction. | under construction | 2012
83 | CCS CSE | Volpago (IT) | North Venezia (IT) | Realization of a new 380kV line between the existing substation of North Venezia and the future 380kV substation of Volpago, connected in and out to the 380kV "Sandrigo - Cordignano” . Total line length: 31km. | Unsatisfactory security and quality of supply in the 380kV grid in the Triveneto area. | Improved security of supply and annual losses reduction. | design & permitting | short term
84 | CCS CSE | Casanova (IT) | Vignole (IT) | Voltage upgrade of the existing 100km Casanova-Vignole 220kV OHL to 400kV and new 400/220/150kV substation in Asti area. | Congestion of the 220kV grid due to further increase of generation in Piemonte and development of the Italian French interconnection. | The project is expected to support conventional generation integration, increase the NTC and reduce grid losses. | planned | 2014/long term
85 | CCS CSE | Voghera (IT) | La Casella (IT) | New 45km double circuit 400kV OHL between the existing substations of La Casella and Voghera. | Congestion of the 380kV in north West /north East area due to further increase of generation in Piemonte-Lombardia and the development of the Italian-French interconnection. | The project is expected to improve security of supply, support conventional generation integration and reduce grid losses. | planned | long term
86 | CCS | Foggia (IT) | Villanova (IT) | New 178km double circuit 400kV OHL between existing Foggia and Villanova 400kV substations, also connected in and out to the Larino and Gissi substations. A PST will be installed on the new 400kV line. | Increase of power exchange capability between south and central south of Italy in order to get over the splitting of the regional market caused by limited transfer capability in both directions. | The project is expected to support conventional generation integration, mitigate CO2 emission, reduce grid losses and help RES integration. | design & permitting | 2015
87 | CCS | Feroleto (IT) | Maida (IT) | New 400kV OHL across Calabria between the existing substation of Feroleto and the future substation of Maida, while restructuring the existing grid in North Calabria. | Overcoming the overloads and voltage stability problems limits due to the present production units and the future generation in the area. | Conventional generation integration, CO2 emission mitigation, annual losses reduction and RES Integration. | design & permitting | short term
88 | CCS | Montecorvino (IT) | Benevento (IT) | New 70km double circuit 400kV OHL between the existing 400kV substations of Montecorvino and Benevento II, providing in and out connection to the future substation to be build in Avellino North area, which will be also connected to the existing "Matera-S. Sofia" 400kV line. | Overcoming the overloads and voltage stability problems limits due to the present production units and the future generation in the area. | Conventional generation integration, CO2 emission mitigation, annual losses reduction and RES Integration. | design & permitting | short term
89 | CCS CSE | Fano (IT) | Teramo (IT) | New 200km single circuit 400kV OHL between the existing 400kV substations of Fano and Teramo, providing the connection in and out to the future substation to be built in Macerata area. | Overcoming the congestions between the south and the north market area due to the generation development in the southern Italy. | The project is expected to improve security of supply, support conventional generation integration and reduce grid losses. | planned | 2015
90 | CCS | Calenzano (IT) | Colunga (IT) | Voltage upgrade of the existing 80km Calenzano-Colunga 220kV OHL to 400kV, providing in and out connection to the existing 220/150kV substation of S. Benedetto del Querceto (which already complies with 400kV standards). | Increase of power exchange capability between north and central north of Italy in order to avoid with the regional market splitting. | The project is expected to support conventional generation integration and reduce grid losses. | design & permitting | short term
91 | CCS | Foggia (IT) | Benevento II (IT) | Upgrade of the existing 85km Foggia-Benevento II 400kV OHL and installation of a PST on this line. | Increase of power exchange capability due to the renewable generation development in Southern Italy. | The project is expected to support RES & conventional generation integration and Improved the security of supply. | design & permitting | short term
92 | CCS | West Udine (IT) | Redipuglia (IT) | New 40km double circuit 400kV OHL between the existing substations of West Udine and Redipuglia, providing in and out connection to the future 400kV substation of South Udine. | Over coming the constraints in North Eastern area of Italy, especially near Redipuglia 380kV sub station, in case of high import from Slovenia and high production of conventional power plants. | The project is expected to support conventional generation integration, increase the NTC and Improved the security of supply. | design & permitting | short term
93 | CCS | Dolo (IT) | Camin (IT) | New 15km double circuit 400kV OHL between existing Dolo and Camin 400kV substations, to be built in parallel with the existing line. | Overcoming the constraints in the Venezia and Padova area, due to production development in the North East of Italy. | The project is expected to improve the security of supply, support conventional generation integration and reduce grid losses. | design & permitting | short term
94 | CCS | Sermide (IT) | Carpi (IT) | New 35km 400kV OHL between the existing substations of Sermide and Carpi. | Overcoming the constrains congestion between N and CN market zones, caused by limited transfer. | The project is expected to support conventional generation integration and reduce grid losses. | planned | long term
95 | CCS | Mese (IT) |  | Voltage upgrade of the existing 220/132kV Mese substation up to 400kV. | Overcoming the constrains in operation, due the renewable generation. | The project is expected to support RES integration and reduce grid losses. | planned | short term
96 | CCS | Deliceto (IT) | Bisaccia (IT) | New 30km single circuit 400kV OHL between the future substations of Deliceto and Bisaccia, in the Candela area. | increase of power exchange capability due to the new renewable generation development in the Southern Italy. | The project is expected to support RES & conventional generation integration and reduce grid losses. | design & permitting | short term
96a | CCS CSE | Several new substation in south of Italy (IT) |  | It will be realized a group of new 380/150kV substations. The new substation will be connected to the wind farms in order to avoid the congestions on the 150kV network and dispatch the green energy. | Reduce the congestions on the 150kV network between Puglia, Campania and Calabria. | Improved security of supply and reduction of congestion. | under construction | Mid term
97 | CCS | Polpet (IT) |  | Voltage upgrade of the existing Polpet 150kV/medium voltage substation up to 220kV, complying with 400kV standards. The substation will be connected by two shorts links to the existing Soverzene-Lienz 220kV line. | Overcoming the constrains in operation, due the renewable generation. | The project is expected to support RES integration and reduce grid losses. | planned | long term
98 | CCS | Pordenone (IT) |  | Voltage upgrade of the existing Pordenone 220kV substation up to 400kV. The substation will be connected in and out to the existing Udine O. – Cordignano 400kV line. | Ensuring the supply in N and N-1 condition. | The project is expected to reduce grid losses and Improved the security of supply. | planned | long term
99 | CCS | Avise (IT) | Chatillon (IT) | Voltage upgrade of the existing 40km Avise-Villeneuve-Chatillon single circuit 220kV OHL up to 400kV. | Low transfer capacity on the tie-lines “Riddes – Avise” and “Riddes – Valpelline”, increase import/export power exchanges. | The project is expected to increase the NTC and reduce grid losses. | design & permitting | short term
100 | CCS | Milan (IT) |  | Restructuring of the 220kV network in the urban area of Milan. Some new 220kV cables (33km), a new 220kV substation (Musocco) and some reinforcements of existing assets (35km) are planned. | Overcoming the constrains in operation and ensuring the supply in N and N-1 condition in large urban centres. | The project is expected to improve the security of supply and reduce re-dispatching costs & grid losses. | design & permitting | short term
101 | CCS | Turin (IT) |  | Restructuring of the 220kV network in the urban area of Turin. Some new 220kV cables, some new 220/132kV substations and some reinforcements of existing assets are planned. Total length: 63km. | Need to overcome the congestion in operation and ensure the supply to large urban centres under N and N-1 conditions. | The project is expected to improve the security of supply and reduce grid losses. | design & permitting | 2012/long term
102 | CCS | Naples (IT) |  | Restructuring of the 220kV network in the urban area of Naples. Some new 220kV cables and some reinforcements of existing assets are planned. Total length: 36km. | Need to overcome the congestion in operation and ensure the supply to large urban centres under N and N-1 conditions. | The project is expected to improve the security of supply and reduce re-dispatching costs & grid losses. | design & permitting | long term
103 | CCS | Brescia (IT) |  | New 400/132kV substation in South East area of Brescia, connected in and out to the existing Flero-Nave 400kVOHL, while restructuring the 132kV network. | Need to overcome the congestion in operation and ensure the supply to large urban centres under N and N-1 conditions. | The project is expected to improve the security of supply and support conventional generation integration. | planned | 2015
104 | CCS | Rome (IT) |  | Restructuring of the network in the Rome area. The work consists of : a new 380/150kV substation in south-West area of Rome, connected in and out to the existing 380kV line "Rome West-Rome South", a voltage upgrade of the existing Flaminia substation up to 380kV to be connected in and out to the foreseen 380kV line "Rome West - Rome North" and a restructuring of the 150kV network. | Need to overcome the congestion in operation and ensure the supply to large urban centres under N and N-1 conditions. | The project is expected to improve the security of supply and reduce grid losses. | design & permitting | 2013/long term
105 | CCS | Treviso (IT) |  | New 380/132kV substation in Treviso area, connected in and out to the existing 380kV line “Sandrigo - Cordignano". | Need to improve the security of supply under N and N-1 conditions. | The project is expected to improve the security of supply and reduce grid losses. | design & permitting | long term
106 | CCS | Schio (IT) |  | New 220/132kV substation in Schio area, providing the connection in and out to the existing 220kV line "Ala-Vicenza Monte Viale”. | Need to improve the security of supply under N and N-1 conditions and overcome HV grid congestion. | The project is expected to improve the security of supply and reduce grid losses. | planned | short term
107 | CCS | Vicenza Industrial (IT) |  | New 380/132kV substation in the industrial area of Vicenza, connected in and out to the existing Sandrigo-Dugale 400kV line. | Need to improve the security of supply under N and N-1 conditions. | The project is expected to improve the security of supply and reduce grid losses. | planned | short term
108 | CCS | North West Padova (IT) |  | New 220/132kV substation in North West Padova area, complying with 400kV standards, providing the connection in and out to the existing Dugale-Marghera Substation1 220kV line. | Need to overcome the congestion in operation (also on HV grid) and ensure the supply to large urban centres under N and N-1 conditions. | The project is expected to improve the security of supply and reduce grid losses. | planned | long term
109 | CCS | North Bologna (IT) |  | New 400/132kV substation in North Bologna area connected in and out to the existing Sermide–Martignone 400kV line. | Need to improve the security of supply under N and N-1 conditions and overcome HV grid congestion. | The project is expected to improve the security of supply and reduce grid losses. | planned | short term
110 | CCS CCE | East Vesuvius (IT) |  | New 380/220/150kV substation in East Vesuvius area (near Naples) connected in and out to the existing 380 and 220kV lines “Montecorvino-S. Sofia” and "Nola-S. Valentino". | Need to improve the security of supply under N and N-1 conditions and overcome HV grid congestion. | The project is expected to improve the security of supply and reduce grid losses. | planned | long term
110a | CCS CSE | Rotonda (IT) | Montecorvino (IT) | Upgrade to 380kV of the 220kV Tuscan-Rotonda line. | Increasing transmission capacity between South and Centre of Italy. | RES integration, conventional generation integration and improved security of supply. | planned | Long term
111 | CCS CSE | Lucca (IT) |  | New 380/132kV substation in Lucca area connected in and out to the existing 380kV line “La Spezia-Acciaiolo”. | Need to improve the security of supply under N and N-1 conditions. | The project is expected to reduce re-dispatching costs and grid losses. | planned | long term
112 | CCS | Tirano (IT) | Verderio(IT) | New 140km single circuit 400kV OHL between Tirano and Verderio substations connecting also the new 400kV substation Grosio/Piateda. | Need to reduce the congestion and increase internal transfer capacity. | The project is expected to support RES integration, and reduce grid losses. | planned | long term
113 | CCS | Monte S. Savino (IT) |  | New 400/220/132kV substation in Monte S. Savino area connected to the existing S. Barbara 400kV substation by upgrading an existing 220kV line. | Overcoming the congestions caused by the South-North transits. | The project is expected to improve the security of supply and reduce grid losses. | design & permitting | long term
114 | CCS | Ittiri (IT) | Codrongianos (IT) | New 18km 400kV OHL between the existing substation of Codrongianos and the future 400kV substation of Ittiri that will be also connected in and out to the existing Fiumesanto-Selargius 400kV line. | Overcoming congestion in the Northern Sardinia due to the existing power plants and development of the interconnection with Mainland. | The project is expected to support conventional generation integration. | under construction | 2011
115 | CCS | Fiumesanto (IT) | Latina (IT) | Second pole of HVDC link between Sardinia and mainland Italy via 400kV DC subsea cable (420km). The first pole is in operation since 2009. Total capacity of the bipolar link: 1000MW. | Increase of security of Supply in Sardinia island and overcoming the splitting the regional market caused by limited transfer. | The project is expected to support RES integration, reduce re-dispatching costs and Improved the security of supply. | under construction | 2010
116 | CCS | Casellina (IT) | Tavarnuzze (IT) | New 37km 400kV OHL with rearrangement of EHV grid in the area between Casellina and S. Barbara. Voltage upgrade of the existing substations of Casellina400/132kV and S. Barbara400/132kV. | Overcoming the congestions caused by the upgrading of S. Barbara Power Plant and the South-North transits. | The project is expected to support conventional generation integration. | under construction | 2010
117 | CCS | Castegnero (IT) |  | New 220/132kV substation connected in and out to the existing 220kV line “Cittadella – Este” and “Dugale – Stazione 1”, providing a restructuring of HV grid. | Ensuring the security of supply in N and N-1 condition. | The project is expected to improve the security of supply and reduce grid losses. | under construction | 2011
118 | CCS | Porto Ferraio (Elba Island) | Cornia (Piombino) | New 40km 132kV connection via subsea cable between the existing substation of Porto Ferraio and the future 400/132kV substation of Cornia that will also be connected in and out to the existing Suvereto-Piombino Termica 400kV line. | Need to strengthen the connection of Elba Island to mainland. | The project is expected to improve security of supply, reduce annual re-dispatching costs and annual losses. | design & permitting | short term
119 | CCS | Capri, Ischia, Procida (IT) |  | New 150kV subsea connection between the Capri, Ischia and Procida islands to the existing substations of Cuma and Torre Annunziata (mainland Italy). Total length : 95km. | Need to connect the isolated systems of these islands to mainland. | The project is expected to improve the security of supply, mitigate CO2 emissions and reduce grid losses. | design & permitting | short term
120 | CCS CSE | Lavorgo (CH) | Morbegno (IT) | New 400kV tie line between Italy and Switzerland. | Need to increase cross-border capacity between Italy and Switzerland. | The project is expected to increase NTC. | under consideration | >2020
121 | CCS | Bickigen (CH) | Romanel (CH) | Construction of different new 400kV OHL sections and voltage upgrade of existing 225kV lines into 400kV lines. Total length: 250km. | Need to transmit power from existing and future generation. | The project is expected to support hydro power generation and pump storage integration and Improved the security of supply. | design & permitting | 2014
122 | CCS | Chippis (CH) | Lavorgo (CH) | Construction of different new 400kV line sections and voltage upgrade of existing 225kV lines into 400kV. Total length: 120km. | Need to transmit power from existing and future generation. | The project is expected to support hydro power generation and pump storage integration and Improved the security of supply. | design & permitting | 2014
123 | CCS | Mettlen (CH) | Ulrichen (CH) | Construction of different new 400kV line sections and voltage upgrade of existing 225kV lines into 400kV lines. Total length: 90km. | Need to transmit power from existing and future generation. | The project is expected to support hydro power generation and pump storage integration and Improved the security of supply. | planned | 2015
124 | CCS | Mettlen (CH) | Airolo (CH) | Upgrade of existing 225kV OHL into 400kV. Line length: 90km. | Need to transmit power from existing and future generation. | The project is expected to support hydro power generation and pump storage integration and Improved the security of supply. | under consideration | 2020
125 | CCS | Schwanden (CH) | Limmern (CH) | New 400kV double circuit (OHL and underground cable) between Schwanden and Limmern. | Need to transmit power from future generation and pump storage. | The project is expected to support hydro power generation and pump storage integration and Improved the security of supply. | design & permitting | 2015
126 | CCS | Golbia (CH) | Robbia (CH) | New 2x 400kV cable connection between Golbia and the Bernina line double circuit. | Need to transmit power from future generation and pump storage. | The project is expected to support hydro power generation and pump storage integration and Improved the security of supply. | under consideration | 2020
127 | CCS | Magadino (CH) | Verzasca (CH) | Upgrade of existing 150kV line into 220kV line. | Need to transmit power from future generation and pump storage. | The project is expected to support hydro power generation and pump storage integration and Improved the security of supply. | under consideration | 2020
128 | CCS | Bâtiaz (CH) | Nant de Drance (CH) | New 400kV double circuit OHL between Bâtiaz and Châtelard. New 2x 400kV cable connection between Châtelard and Nant de Drance. Total length: 22km. | Need to transmit power from future generation and pump storage. | The project is expected to support hydro power generation and pump storage integration and Improved the security of supply. | design & permitting | 2014
129 | CCS | Beznau (CH) | Mettlen (CH) | Upgrade of the existing 65km double circuit 220kV OHL to 400kV. | Need to overcome existing bottleneck limiting both import (from France, Germany & Austria) and generation of Beznau power plant. | The project is expected to increase NTC, improved the security of supply and support conventional generation integration. | design & permitting | 2015
130 | CCS | La Punt (CH) | Pradella / Ova Spin (CH) | Installation of the second circuit on existing towers of a double-circuit 400kV OHL (50km). | Need to overcome existing bottleneck limiting import from France, Germany and Austria. | The project is expected to increase NTC. | planned | 2015
131 | CCS | Bickigen (CH) |  | Addition of a second 400/220kV transformer in an existing substation. | Need to overcome existing bottleneck limiting both from France, Germany & Austria. | The project is expected to increase NTC and Improved the security of supply. | design & permitting | 2012
132 | CCS | Mühleberg (CH) |  | Construction of a new 400/220kV substation. | Need to overcome existing bottleneck limiting both from France, Germany & Austria. | The project is expected to increase NTC and Improved the security of supply. | design & permitting | 2012
133 | CCS | Bonaduz (CH) | Mettlen (CH) | Upgrade of the existing 180km double circuit 220kV OHL into 400kV. | Need to improve the connection between the Alps and the urban area. | The project is expected to improve the security of supply. | under consideration | 2020
134 | CCS | Bassecourt (CH) | Romanel (CH) | Construction of different new 400kV line sections and voltage upgrade of existing 225kV lines into 400kV lines. Total length: 140km. | Need to overcome existing bottleneck limiting both from France, Germany & Austria. | The project is expected to increase NTC and Improved the security of supply. | design & permitting | 2012
135 | CCS | 220kV nodes (CH) |  | Many 220kV reinforcement around the urban areas. | Need of better connection of the urban areas. | These projects will improve the security of supply. | planned | 2015
136 | CCS CCE North Sea Baltic Sea | Area of Bodensee (DE, AT, CH) |  | Construction of new lines, extension of existing ones and erection of 400/220/110kV-substation. | This project will increase the current power exchange capacity between the DE, AT and CH. | The project is expected to increase NTC and Improved the security of supply. | planned | long term
137 | CCS CCE North Sea Baltic Sea | Vitkov (CZ) | Mechlenreuth (DE) | New 400kV single circuit tie-line between new (CZ) substation and existing (DE) substation. Length: 70km. | This project will increase the current power exchange capacity between the Czech Republic and Germany. | Increase of NTC. | under consideration | long term
138 | CCS CCE North Sea Baltic Sea | under consideration (CZ) | South-Eastern part of 50Hertz Transmission control area | Possible increase of interconnection capacity between CEPS and 50Hertz Transmission is under consideration: either a new 400kV tie-line (OHL on new route) or a reinforcement of the existing 400kV tie-line Hradec (CEPS) – Röhrsdorf (50Hertz Transmission). | The project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the cross-border transmission capacity of the grid. | It is expected that the project will maintain or even Improved the security of supply, and support RES integration and CCE Market development. | under consideration | long term
139 | CCS CCE North Sea Baltic Sea | Vierraden (DE) | Krajnik (PL) | This project is the conversion of existing 220kV double circuit line Krajnik (PSE Operator) - Vierraden (50Hertz Transmission) into a 400kV line together with installation of phase shifting transformers in Krajnik (PSE Operator) and Mikułowa (PSE Operator). | The project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the cross-border transmission capacity and flexibility of the grid. | It is expected that the project will decrease the loop flow from DE to PL and to CZ/SK. It will improve the security of supply, increase the power exchange capacity between PL and DE on PL/DE/CZ/SK synchronous profile (i.e. support CCE market development) and support the RES integration. | design & permitting | before 2013 | X | conversion of the existing 220 kV double circuit line Krajnik (PSE Operator) - Vierraden (5 Hertz Transmission) into a 400 kV line is a top priority project according to German act for acceleration of transmission grid extension (EnLAG)
140 | CCS CCE North Sea Baltic Sea | Eisenhüttenstadt (DE) | Plewiska (PL) | This project is the 3rd 400kV double circuit OHL interconnection between Poland (Plewiska) and Germany (Eisenhüttenstadt) with reinforcement of the Polish internal grid. Total length is 252km, 242km of which being in Poland. | The project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the cross-border transmission capacity of the grid. | It is expected that the project will support the CCE market development, RES integration and maintain or even Improved security of supply. | planned | long term | X | Top priority project according to German act for acceleration of transmission grid extension (EnLAG); German-Polish project development company is in preparation
141 | CCS CCE North Sea Baltic Sea | Ishøj/Bjæverskov (DK) | Bentwisch (DE) | The Kriegers Flak project is the new subsea cable multiterminal connection between Denmark, Sweden and Germany used for both grid connection of offshore wind farms Kriegers Flak and interconnection. Technical features still have to be determined. | The project will alleviate mainly the need of 1) grid connection for new off-shore wind farms in the Baltic Sea and 2) additional cross-border transmission capacity of the grid. | RES integration and increase of NTC. | under consideration | 2014 |  | http://www.energinet.dk/en/menu/Transmission/New+projects/New+electricity+transmission+installations/Kriegers+Flak/
142 | CCS CCE North Sea Baltic Sea | Tonstad (NO) | tbd (DE) | Nord.Link: A new HVDC connection between Southern Norway and Northern Germany. Estimated subsea cable length: 520 - 600km. Capacity: 700 - 1400MW. | Connecting isolated systems (currently no connection between Germany and Norway). | Increase of NTC (700 - 1400MW), diversity of supply and RES integration. | design & permitting | long term |  | A similar non-TSO project “NorGer” is also under development
143 | CCS CCE North Sea Baltic Sea | Kassö (DK) & Ensted (DE) |  | Installation of two PSTs. This project is in the framework of step 2 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity; This step includes also planed strengthening of existing 380kV lines in the grid of TPS and Energinet.dk . | The project will increase the power exchange capacity between Germany and Denmark Wets. This will improve the market function and contribute to a better utilization of the increasing amount of wind power. | Increase of NTC (Approximately by 500MW when the whole step 2 will be finished), improved security of supply and annual losses reduction. | under construction | mid term
144 | CCS CCE North Sea Baltic Sea | Audorf (DK) | Kassö (DE) | Step 3 in the Danish-German agreement to upgrade the Jutland-DE transfer capacity. It consists of partially an upgrade of existing 400kV line and partially a new 400kV route in Denmark. In Germany new 400kV line mainly in the trace of a existing 220kV line. The total length of this OHL is 114km. | The project will increase the power exchange capacity between Germany and Denmark Wets. This will improve the market function and contribute to a better utilization of the increasing amount of wind power. | This project will enable an Increase of NTC between the two countries, improved security of supply, reduce annual losses. | under consideration | long term |  | In parallel with this project there is a proposal for a new merchant line NorGer.
145 | CCS CCE North Sea Baltic Sea | Niederrhein (DE) | Doetinchem (NL) | New 400kV line double circuit DE-NL interconnection line. Length:60km. | Overloads due to high North-South power flows through the auctioned frontier between the Netherlands and Germany in peak hours of wind in-feed. | Increase of NTC (1000 - 2000MW), improved security of supply and RES integration. | design & permitting | 2013 |  | EnLAG (German Law for new lines)
146 | CCS CCE North Sea Baltic Sea | Aachen/Düren region (DE) | Lixhe (BE) | Connection between Germany and Belgium including new 100km underground cable and extension of existing 380kV-substations. | Low cross border capacity. | NTC increase, conventional generation integration and RES integration. The project will facilitate IEM, since presently there is no direct exchange capability between DE and BE. | under consideration | long term | X
147 | CCS CCE North Sea Baltic Sea | Dollern (DE) | Hamburg/Nord (DE) | New 400kV double circuit OHL Dollern - Hamburg/Nord including one new 400/230kV transformer in substation Hamburg/Nord and new 400kV switchgear Kummerfeld. Length:43km. | Increase of the transmission capacity from north to south-West Germany due to the increase of RES in Northern Germany. | RES integration, improved security of supply and annual re-dispatching costs reduction. | design & permitting | 1. circuit midterm; 2. circuit long-term | X | EnLAG (German Law for new lines)
148 | CCS CCE North Sea Baltic Sea | Audorf (DE) | Hamburg/Nord (DE) | New 400kV double circuit OHL Audorf - Hamburg/Nord including two new 400/230kV transformers in substation Audorf. Length: 65km. | Increase of the transmission capacity from north to south-West Germany, due to the increase of RES in Northern Germany and increase of power exchange capability between Denmark and Germany. | RES integration, improved security of supply and annual re-dispatching costs reduction. | planned | long term | X | Due to the German act "EnLAG"
149 | CCS CCE North Sea Baltic Sea | Dollern (DE) | Stade (DE) | New 400kV double circuit OHL Dollern - Stade including new 400kV switchgear in Stade. Length:14km. | Connection of new power plants. | Conventional generation integration. | design & permitting | mid term
150 | CCS CCE North Sea Baltic Sea | Conneforde (DE) | Maade (DE) | New 400kV double circuit ( underground cable+OHL) Conneforde - Maade including new 400kV switchgear Maade. Length: 37km. | Connection of new power plants. | Conventional generation integration. | design & permitting | long term
151 | CCS CCE North Sea Baltic Sea | Wehrendorf (DE) | Ganderkesee (DE) | New line, extension of existing and erection of substations, erection of 380/110kV-transformers. | Increase of the transmission capacity from north to south-West Germany due to the increase of RES in Northern Germany. | RES integration, improved security of supply and annual re-dispatching costs reduction. | design & permitting | mid term |  | Due to the German act "EnLAG"
152 | CCS CCE North Sea Baltic Sea | Dörpen/West (DE) |  | New substation for connection of offshore wind farms. | Connection of off-shore wind farms. | RES integration and conventional generation integration. | design & permitting | mid term
153 | CCS CCE North Sea Baltic Sea | Redwitz (DE) | Grafenrheinfeld (DE) | Upgrade of 230kV connection Redwitz - Grafenrheinfeld to 400kV, including new 400kV switchgear Eltmann. Line length: 97km. | Support of RES integration in Germany, maintaining of security of supply and support of the market development. | RES integration, improved security of supply and conventional generation integration. | design & permitting | mid term |  | Due to the German act "EnLAG"
154 | CCS CCE North Sea Baltic Sea | Redwitz (DE) |  | New 500 MVAr SVC in substation Redwitz. | Voltage stability. | Improved security of supply. | planned | mid term
155 | CCS CCE North Sea Baltic Sea | Raitersaich (DE) |  | New 500 MVAr SVC in substation Raitersaich. | Voltage stability. | Improved security of supply. | planned | mid term
156 | CCS CCE North Sea Baltic Sea | Niederrhein (DE) | Dörpen/West (DE) | New 400kV double circuit OHL Dörpen - Niederrhein including extension of existing substations. Length: 167km. | Increase of the transmission capacity from north to south-West Germany due to the increase of RES in Northern Germany. | RES integration, improved security of supply and conventional generation integration. | design & permitting | long term |  | Due to the German act "EnLAG"
157 | CCS CCE North Sea Baltic Sea | Wahle (DE) | Mecklar (DE) | New 400kV double circuit OHL Wahle - Mecklar including two new substations. Length: 210km. | Increase of the transmission capacity from north to south-West, due to the increase of RES in Northern Germany. | RES integration, improved security of supply and conventional generation integration. | design & permitting | long term |  | Due to the German act "EnLAG"
158 | CCS CCE North Sea Baltic Sea | Irsching (DE) | Ottenhofen (DE) | Upgrade of 230kV connection Irsching - Ottenhofen to 400kV, including new 400kV switchgear Zolling. Length 76km. | Increase of the transmission capacity from north to south due to increase of transits from North to South Germany. | Improved security of supply, RES integration and conventional generation integration. | planned | long term
159 | CCS CCE North Sea Baltic Sea | Cluster BorWin1 (DE) | Diele (DE) | New line consisting of underground +subsea cable with a total length of 205km. Line capacity: 400MW. | Connection of new offshore wind farm. | RES integration. | under construction | mid term
160 | CCS CCE North Sea Baltic Sea | Offshore- Wind park Nordergründe (DE) | Inhausen (DE) | New line consisting of underground +subsea cable with a total length of 35km. | Connection of new offshore wind farm. | RES integration. | design & permitting | mid term
161 | CCS CCE North Sea Baltic Sea | Offshore- Wind park GEOFreE (DE) | Göhl (DE) | New line consisting of underground +subsea cable with a total length of 32km. | Connection of new offshore wind farm. | RES integration. | design & permitting | mid term
163 | CCS CCE North Sea Baltic Sea | Cluster HelWin1 (DE) | Büttel (DE) | New line consisting of underground +subsea cable with a total length of 145km. Line capacity: aprox. 860MW. This Project includes also a new substation Büttel and connection of this new substation with the existing OHL Brünsbüttel - Wilster. | Connection of new offshore wind farm. | RES integration. | design & permitting | mid term
164 | CCS CCE North Sea Baltic Sea | Cluster SylWin1 (DE) | Büttel (DE) | New line consisting of underground +subsea cable with a total length of 210km. Line capacity: aprox. 690MW. | Connection of new offshore wind farm. | RES integration. | design & permitting | mid term
165 | CCS CCE North Sea Baltic Sea | Cluster DolWin1 (DE) | Dörpen/West (DE) | New line consisting of underground +subsea cable with a total length of 155km. Line capacity: 400MW. | Connection of new offshore wind farm. | RES integration. | design & permitting | mid term
166 | CCS CCE North Sea Baltic Sea | Offshore Wind park Riffgat (DE) | Emden (DE) | New line consisting of underground +subsea cable with a total length of 80km. | Connection of new offshore wind farm. | RES integration. | design & permitting | mid term
167 | CCS CCE North Sea Baltic Sea | Cluster BorWin2 (DE) | Diele (DE) | New line consisting of underground +subsea cable with a total length of 205km. Line capacity: 400-800MW. | Connection of new offshore wind farm. | RES integration. | design & permitting | mid term
168 | CCS CCE North Sea Baltic Sea | Goldshöfe (DE) | Dellmensigen (DE) | Upgrade the line Goldshöfe - Dellmensigen from 220kV to 380kV . Line length:114km. Included with the project : 3x 380kV substations, 2 transformers. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | RES Integration, improved security of supply and annual losses reduction. | under construction | 2012
168a | CCS, Baltic Sea, North Sea | Region South-West Bavaria (DE) |  | Upgrading the existing 220kV OHL to 380kV,length 100km and the extension of existing substations, erection of 380/110kV-transformers. | Upgrading the existing 220 kV OHL to 380 kV, length 100 km and the extension of existing substations, erection of 380/110kV-transformers. | Improved security of supply. | planned | long term
169 | CCS CCE North Sea Baltic Sea | Großgartach (DE) |  | Upgrade the substation for a higher short circuit capacity. New installation includes 10 gas insulated bays, 63 kA, 3 bus-bar and 2 transformers. | Increase of short-circuit current needs due to the change of the topology for the grid. | Improved security of supply and RES Integration. | under construction | 2010
170 | CCS CCE North Sea Baltic Sea | Großgartach (DE) | Hüffenhardt (DE) | New 380kV OHL. Length: 23km. Included with the project : 1 new 380kV substation, 2 transformers. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | RES Integration, improved security of supply and annual losses reduction. | under construction | 2012
171 | CCS CCE North Sea Baltic Sea | Hüffenhardt (DE) | Neurott (DE) | Upgrade of the line from 220kV to 380kV. Length: 11km. Included with the project : 1 new 380kV substation. | Adjustment of the transmission capacity of the grid. | Improved security of supply and annual losses reduction. | planned | 2020
172 | CCS CCE North Sea Baltic Sea | Mühlhausen (DE) | Großgartach (DE) | Upgrading line from 220kV to 380kV. Length:-45km. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | RES Integration, improved security of supply and annual losses reduction. | design & permitting | 2014 |  | EnLAG (German Law for new lines)
173 | CCS CCE North Sea Baltic Sea | Hoheneck (DE) | Endersbach (DE) | Upgrading line from 220kV to 380kV. Length:20km. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | RES Integration and Improved security of supply. | design & permitting | 2014
174 | CCS CCE North Sea Baltic Sea | Bruchsal Kändelweg (DE) | Ubstadt (DE) | A new 380kV OHL. Length:6km. | Adjustment of the transmission capacity of the grid. | Improved security of supply and annual losses reduction. | design & permitting | 2014
175 | CCS CCE North Sea Baltic Sea | Birkenfeld (DE) | Ötisheim (DE) | A new 380kV OHL. Length:11km. | Adjustment of the transmission capacity of the grid. | Improved security of supply and annual losses reduction. | planned | 2020
176 | CCS CCE North Sea Baltic Sea | Villingen (DE) | Weier (DE) | A new 380kV OHL. Length:75km. | Increase of the transmission capacity from north to south-West of Germany, due to the increase of wind energy in Northern part. | RES Integration and annual re-dispatching costs reduction. | under consideration | 2020 |  | EnLAG (German Law for new lines)
177 | CCS CCE North Sea Baltic Sea | Goldshöfe (DE) | Bünzwangen (DE) | A new 380kV OHL. Length: 45km. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | RES Integration and annual re-dispatching costs reduction. | under consideration | 2020 |  | EnLAG (German Law for new lines)
178 | CCS CCE North Sea Baltic Sea | Baden-Württemberg, Süden & Nordosten (DE) |  | Installation of 3x250 MVAr 380kV capacitance banks. | Injection of reactive power. | Voltage stability. | under construction | 2014
179 | CCS CCE North Sea Baltic Sea | Rommerskirchen (DE) | Weißenthurm (DE) | New line, extension of existing and erection of substations, erection of 380/110kV-transformers. Total line length: 100km. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | RES integration, improved security of supply and conventional generation integration. | under construction | mid term |  | EnLAG (German Law for new lines)
180 | CCS CCE North Sea Baltic Sea | Mengede (DE) | Kruckel (DE) | Installation of a second circuit 380kV OHL and extension of existing substations. Line length:16km. | Connection of new power plants. | Conventional generation integration. | planned | mid term
181 | CCS CCE North Sea Baltic Sea | Dauerberg (DE) | Limburg (DE) | New 380kV double circuit OHL, extension of existing and erection of substations, erection of 380/110kV-transformers. Total line length: 46km. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | RES integration and Improved security of supply. | under construction | mid term |  | EnLAG (German Law for new lines)
182 | CCS CCE North Sea Baltic Sea | Kriftel (DE) | Eschborn (DE) | On the main distance upgrading line, extension of existing substations. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | RES Integration and Improved security of supply. | under construction | mid term |  | EnLAG (German Law for new lines)
183 | CCS CCE North Sea Baltic Sea | Wehrendorf (DE) |  | Installation of 300 MVAr 380kV capacitance banks, extension of existing substations. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | Voltage stability and Improved security of supply. | planned | mid term
184 | CCS CCE North Sea Baltic Sea | Bürstadt (DE) |  | Installation of 2 x 300 MVAr 380kV capacitance banks, extension of existing substations. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | Voltage stability and Improved security of supply. | planned | mid term
185 | CCS CCE North Sea Baltic Sea | Area of Muensterland and Westfalia (DE) |  | New lines and installation of additional circuits, extension of existing and erection of several 380/110kV-substations. Total line length: 240km. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | RES integration, improved security of supply and conventional generation integration. | planned | long term |  | EnLAG (German Law for new lines)
186 | CCS CCE North Sea Baltic Sea | Gütersloh (DE) | Bechterdissen (DE) | New lines and installation of additional circuits, extension of existing and erection of 380/110kV-substation. Total line length:27km. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | RES integration and Improved security of supply. | under construction | mid term |  | EnLAG (German Law for new lines)
187 | CCS CCE North Sea Baltic Sea | Area of West-Rhineland (DE) |  | New lines and installation of additional circuits, extension of existing and erection of several 380/110kV-substations. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | RES integration, improved security of supply and conventional generation integration. | under construction | mid term |  | EnLAG (German Law for new lines)
188 | CCS CCE North Sea Baltic Sea | Kruckel (DE) | Dauersberg (DE) | New lines, extension of existing and erection of several 380/110kV-substations. Total line length: 130km. | Increase of the transmission capacity from North to South-West of Germany, due to the increase of wind energy in Northern part. | RES integration, improved security of supply and conventional generation integration. | planned | long term |  | EnLAG (German Law for new lines)
189 | CCS CCE North Sea Baltic Sea | Niederrhein (DE) | Utfort (DE) | New lines and extension of existing 380kV-substations. Total length:31km. |  | RES integration, improved security of supply and conventional generation integration. | planned | long term |  | EnLAG (German Law for new lines)
190 | CCS CCE North Sea Baltic Sea | Saar-Pfalz-Region (DE) |  | New lines, extension of existing and erection of several 380/110kV-substations. |  | Improved security of supply and conventional generation integration. | planned | mid term
191 | CCS CCE North Sea Baltic Sea | Neuenhagen (DE) | Vierraden (DE) | Project of new 380kV double-circuit OHL with 125km length as prerequisite for the planned upgrading of the existing 220kV double-circuit interconnection Krajnik (PL) – Vierraden (DE, 50Hertz Transmission). | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | In particular the project will support RES integration in North Germany/Poland, maintaining the security of supply and support of market development in CCE. | design & permitting | 2011 | X | Top priority project according to German act for acceleration of transmission grid extension (EnLAG)
192 | CCS CCE North Sea Baltic Sea | Hamburg/Krümmel (DE) | Schwerin (DE) | This 380kV double-circuit OHL project will close the missing gap in North-East German grid infrastructure. Only 65km of new line must be constructed, 22km already exist. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Support of RES integration in North Germany, maintaining of security of supply and support of market development. | under construction | 2010 | X | Top priority project according to German act for acceleration of transmission grid extension (EnLAG)
193 | CCS CCE North Sea Baltic Sea | Halle/Saale (DE) | Schweinfurt (DE) | New 380kV double-circuit OHL between the substations Lauchstädt-Vieselbach-Altenfeld-Redwitz with 215km length combined with upgrade between Redwitz and Grafenrheinfeld (see project 153). | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Support of RES integration in Germany, annual redispatching cost reduction, maintaining of security of supply and support of the market development. | partly completed; design & permitting | mid term | X | Top priority project according to German act for acceleration of transmission grid extension (EnLAG); project is also part of the European Energy Programme for Recovery
194 | CCS CCE North Sea Baltic Sea | wind farm cluster Baltic Sea East (DE) | Lüdershagen/ Lubmin (DE) | Offshore wind farm connection project (by AC-cables on transmission voltage level) has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. | Project will satisfy the need of grid connection for new off-shore wind farms in the Baltic Sea. | Support of RES integration in German part of the Baltic sea. | Under consideration, design & permitting | 2011/2015 | X
195 | CCS CCE North Sea Baltic Sea | wind farm cluster Baltic Sea West (DE) | Bentwisch (DE) | Offshore wind farm connection project (by AC-cables on transmission voltage level) has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. This includes an option for an interconnection project between Germany, Denmark and Sweden via offshore wind farms Kriegers Flak (see project 141). | Project will satisfy the need of grid connection for new off-shore wind farms in the Baltic Sea. | Support of RES integration in German part of the Baltic sea. For optional interconnection part, increase of NTC. | Under consideration, design & permitting | 2011/2015 | X | option for an interconnection project between Germany, Denmark and Sweden via offshore wind farms Kriegers Flak is part of the European Energy Programme for Recovery
196 | CCS CCE North Sea Baltic Sea | wind farm Baltic 1 (DE) | Bentwisch (DE) | Offshore wind farm connection of 79km single AC-cable on transmission voltage level has to be constructed and afterwards also to be operated by the TSO (in this project: 50Hertz Transmission) according to German law. There is an extension option for the later grid connection of the offshore wind farm Kriegers Flak 1. | Project will satisfy the need of grid connection for new off-shore wind farms in the Baltic Sea. | Support of RES integration in German part of the Baltic Sea. | under construction | 2010 | X
197 | CCS CCE North Sea Baltic Sea | Neuenhagen (DE) | Wustermark (DE) | Berlin North Ring: replacement of an existing old 220kV double-circuit OHL by a 380kV double-circuit OHL. Length: 75km. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Support of RES and conventional generation integration in Germany, maintaining of security of supply and support of market development in CCE. | design & permitting | 2020 |  | Top priority project according to German act for acceleration of transmission grid extension (EnLAG)
198 | CCS CCE North Sea Baltic Sea | Wuhlheide (DE) | Thyrow (DE) | Berlin South Ring: replacement of an existing old 220kV double-circuit OHL by a 380kV double-circuit OHL. Length: 50km. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Support of RES integration in Germany, maintaining of security of supply and support of market development. | under consideration | long term
199 | CCS CCE North Sea Baltic Sea | Western Pomerania (DE) | Uckermark North (DE) | Construction of new 380kV double-circuit OHLs in North-Eastern part of VE-T control area and decommissioning of existing old 220kV double-circuit OHLs. Length: 135km. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | planned | 2015
200 | CCS CCE North Sea Baltic Sea | Lubmin (DE) | Erfurt area (DE) | New 380kV double-circuit OHL from the Northern part of the 50Hertz Transmission control area to the South-Western part of the 50Hertz Transmission control area with considered further extension to South-Western part of Germany. Length ca. 800km. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | planned | long term |  | Suitable project extension under consideration of ongoing long term system studies.
201 | CCS CCE North Sea Baltic Sea | Bärwalde (DE) | Schmölln (DE) | Upgrade of the existing double-circuit 380kV OHL. Project will be realized earlier than originally planned as part of project 203. Line length: 50km. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | design & permitting | 2013
202 | CCS CCE North Sea Baltic Sea | Reinforcement of the 380kV grid in South-Eastern part of 50Hertz Transmission control area |  | Upgrading of several existing double-circuit 380kV OHL in the South-Eastern part of the control area of 50Hertz Transmission. Total length: 190km. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | planned | long term
203 | CCS CCE North Sea Baltic Sea | 380kV grid extension in South-Eastern part of 50Hertz Transmission control area (DE) |  | New 380kV double-circuit OHL in South-Eastern part of 50Hertz Transmission control area. Total length: 105km. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | under consideration | long term
204 | CCS CCE North Sea Baltic Sea | Pulgar (DE) | Vieselbach (DE) | Upgrading of the existing double-circuit 380kV OHL . Length:105km. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | planned | 2012
205 | CCS CCE North Sea Baltic Sea | Reinforcement of the 380kV grid in Lausitz area (DE) |  | Upgrading of several existing double-circuit 380kV OHL in the Eastern part of the control area of 50Hertz Transmission. Total length: 150km. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | under consideration | long term
206 | CCS CCE North Sea Baltic Sea | 380kV grid reinforcement and extension in Saxony (DE) |  | Upgrade of the existing double-circuit 380kV OHL and also construction of 230km of new 380kV double-circuit OHLs in Saxony (control area of 50Hertz Transmission). Length: 80km. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | under consideration | long term
207 | CCS CCE North Sea Baltic Sea | Substations in South-Western part of 50Hertz Transmission control area (DE) |  | Construction of new reactive power compensation devices. | Project will alleviate the need of additional reactive power. | Support of RES and conventional generation integration in North Germany, maintaining of security of supply and support of market development. | planned | 2012
208 | CCS CCE North Sea Baltic Sea | Substations in South-Western part of 50Hertz Transmission control area (DE) |  | Construction of new reactive power compensation devices. | Project will alleviate the need of additional reactive power. | Support of RES and conventional generation integration in North Germany, maintain security of supply and support of market development. | under consideration | long term
209 | CCS CCE North Sea Baltic Sea | Substations in 50Hertz Transmission control area |  | Construction of new 380kV/110kV substation. | Project will alleviate mainly the need to increase the capability of the grid to accommodate additional generation capacity. | Support of RES integration in Germany and maintain of security of supply. | planned | 2012
210 | CCS CCE North Sea Baltic Sea | Substations in 50Hertz Transmission control area |  | Construction of new 380kV/110kV substation. | Project will alleviate mainly the need to increase the capability of the grid to accommodate additional generation capacity. | Support of RES integration in Germany and maintain of security of supply. | under consideration | long term
211 | CCS CCE North Sea Baltic Sea | Further connections of more offshore wind farms (DE) |  | Further connections in the clusters BorWin, DolWin, SylWin and HelWin. | Connection of new offshore wind farms. | Increase RES integration. | under consideration | long term
212 | CCS CCE North Sea Baltic Sea | Isar (DE) | St. Peter (AT) | New 400kV double circuit OHL Isar - St. Peter including new 400kV switchgears Altheim, Simbach and St. Peter and one new 400/230kV transformer in substation Altheim. Line length: 90km. | This project will increase the current power exchange capacity between Austria and Germany. | Increase of NTC and RES integration. | under consideration | 2017
213 | CCE CCS CSE | Wien SO (AT) | Szombathely (HU) | Installation of the 2nd circuit on the existing interconnection from Wien SO (AT, APG) to the border (both circuits have already been installed on the Hungarian side, one is connected to Györ and the 2nd circuit to Szombathely). Line length: 63km. | Necessity for further wind integration and connection to the 380kV-grid, increasement of transport capacities in the Eastern grid area. | Increase of NTC, RES integration and Improved security of supply. | under construction | 2010/2011
214 | CCE CCS CSE | Gabcikovo (SK) | Györ/Szombathely (HU) Sarasdorf/Wien (AT) | SEPS and MAVIR are considering a new interconnection between SK and HU (starting from Gabčíkovo substation (SK)) and a connection to the existing 400-kV tie-line Györ/Szombathely (HU) - Vienna/Sarasdorf (AT) at the Hungarian side. | Increasement of (n-1)-security and border capacities in this area. | Improved security of supply, increase of NTC and diversity of supply. | under consideration | 2020
215 | CCE CCS | St. Peter (AT) | Salzach neu (AT) | New internal double circuit 380kV-line connecting the substations St. Peter and Salzach neu (replacement of the existing 220kV-line). Length: 46km. | Alleviation of North-to-South congestions, creation of strongly needed enhanced North-to-South transmission capacities. | Improved security of supply, annual re-dispatching costs reduction and annual losses reduction. | under construction | 2011 | X
216 | CCE CCS | Salzach neu (AT) | Tauern (AT) | New internal double circuit 380kV-line connecting the substations Salzach neu and Tauern and erection of the new 380/220/110kV-substation Pongau (replacement of the existing 220kV-line) . Line length: 115km. | Alleviation of North-to-South congestions, creation of strongly needed enhanced North-to-South transmission capacities. | Improved security of supply, RES integration and annual re-dispatching costs reduction. | planned | 2017 | X
217 | CCE CCS | Dürnrohr (AT) | Sarasdorf (AT) | Installation of the 3rd and 4th circuit on the existing line Dürnrohr - Sarasdorf and restructuring in the area of the substation Bisamberg and the 220kV-Weinviertel-line . Total length: 100km. | Increase of (n-1)-security. | Improved security of supply, RES integration and annual losses reduction. | planned | 2012/2015
218 | CCE CCS | Obersielach (AT) | Lienz (AT) | The project is concerning new 380kV-lines connecting the substations Lienz (AT) and Obersielach (AT) to close the Austrian 380kV-Ring in the southern grid area. Line length: 190km. | Increase of (n-1)-security and transport capacities in the southern grid area. | Improved security of supply, conventional generation integration and RES integration. | under consideration | 2020/2025
219 | CCE CCS | Westtirol (AT) | Zell-Ziller (AT) | Upgrade of the existing 220kV-line Westtirol - Zell-Ziller and erection of additional 220/380kV-Transformers. Line length: 105km. | Increase of (n-1)-security and transport capacities in the Western grid area. | Improved security of supply, conventional generation integration and reduction of infrastructure vulnerability. | under consideration | 2012/2020
220 | CCE CCS | Lienz (AT) |  | Erection of a new 220/220kV- PST in the substation Lienz (AT). | Eliminate congestion management measures and allows the meshed operation of the tie-line Lienz - Soverzene. | Improved security of supply, annual re-dispatching costs reduction and increase of NTC. | design & permitting | 2012
221 | CCE CCS | St. Peter (AT) | Ernsthofen (AT) | Upgrade from 220kV-operation to 380kV and erection of a 380kV-Substation in Ernsthofen and St. Peter. | Increase of transport capacities in the East-West direction and necessity for the 380kV-Ring concept. | Improved security of supply, RES integration and conventional generation integration. | planned | 2013
222 | CCE CCS | Silz (AT) | Zell-Ziller (AT) | Upgrade of the existing 220kV-double circuit- OHL Zell-Ziller - Silz. Line length: 42km. | Increase of (n-1)-security and transport capacities in the Western grid area. | Improved security of supply, conventional generation integration and reduction of infrastructure vulnerability. | under consideration | 2013
223 | CCE CCS CSE | Cirkovce (SI) | Heviz (HU) Zerjavenec (HR) | The existing substation of Cirkovce (SI) will be connected to one circuit of the existing Heviz (HU) -Zerjavinec (HR) double circuit 400kV OHL by erecting a new 80km double circuit 400kV OHL in Slovenia. The project will result in two new cross-border circuits: Heviz (HU) - Cirkovce (SI) and Cirkovce (SI) - Žerjavenec (HR). | Increasing power exchange and need to improve market integration. | The project will increase NTC, allowing higher power exchange between Slovenia and Hungary, improved security and diversity of supply and secure the operation of the Slovenian system. | design & permitting | short term | X
224 | CCE CCS CSE | Krsko (SI) | Bericevo (SI) | New 400kV double circuit OHL. This project will strengthen connection between East and Central part of Slovenia and connect an internal loop. Line length: 80km. | Need to improve the security & quality of supply. | The project should benefit in improved security of supply, grid annual losses & annual re-dispatching costs reduction. | design & permitting | short term | X
225 | CCE CCS CSE | Divaca (SI) | Cirkovce (SI) | Upgrading 220kV lines to 400kV in corridor Divaca-Klece-Bericevo-Podlog-Cirkovce. Line length: 193km. | Need to secure the operation of the Slovenian system. | The project is expected to improve the security of supply and reduce annual losses & re-dispatching costs. | planned | long term
226 | CCE CCS CSE | Ernestinovo (HR) | Pecs (HU) | New 400kV double circuit interconnection line between existing stations. Line length: 86km. | Need to increase the cross-border capacity and support market integration. | The project is expected to increase transfer capacity, improved the security of supply and reduce grid losses. | under construction | 2010 | X
227 | CCE CCS CSE | tbd (BA) | tbd (HR) | New 400kV interconnection line between existing stations. | Need to increase the cross-border capacity and support market integration. | The project is expected to improve the security of supply, support conventional generation integration and increase cross-border capacity. | under consideration | tbd
228 | CCE CCS CSE | Trebinje (BA) | Plat (HR) | Re-establishment of previously existing 220kV double circuit interconnection Trebinje(BA)-Plat(HR); Total length 10km. | Need to increase the cross-border capacity and support market integration. | The project is expected to increase the operational security and favour conventional generation integration. | planned | 2014
229 | CCE CCS CSE | TPP Plomin (HR) | Melina (HR) | New 90km double circuit OHL, with two connecting substations and a transformer 400/220kV, 400 MVA. | Need to connect a new generator. | The project is expected to favour conventional generation integration and increase the operational security. | under consideration | 2016
230 | CCE CCS CSE | TPP Sisak (HR) | Mraclin(HR)/Prijedor(BA) | Connection of new generator on existing line 220kV Mraclin (HR) - Prijedor (BA) via a new double circuit OHL. Line length: 12km. | Need to connect a new generator. | The project is expected to favour conventional generation integration and increase the operational security. | design & permitting | 2012
231 | CCE CCS CSE | Konjsko (HR) |  | Installation of a 150 MVAr reactive power device. | Need to control the voltage on the 400kV grid. | The project will improve the security of supply. | planned | 2013
232 | CSE | Visegrad (BA) | Pljevlja (ME) | New 400kV transmission line between existing stations. Line length: 70km. | Market integration, need for new DC cable between ME-IT. | Increase of (n-1) security ; New regional corridor ; Increase NTC. | under consideration | >2015 |  | Support of BA State Regulatory commission, preliminary agreement of TSOs BA, ME and IT
233 | CSE | Tirana (AL) | Podgorica (ME) | New 400kV line Tirana (AL)-Podgorica (ME) with length 157km (128.5km on Albanian side, 76km of which with double circuit and 28.5km on the Montenegrin side). | Need to strengthen the sparse structure of the South East Europe network and to increase the grid capability to transmit power from countries with surplus generation (BG, RO) towards Italy. | The project is expected to increase NTC and Improved the security of supply. | under construction | 2010
233a | Cont.SE | Tivat (ME) |  | A new substation will be connected to the existing line 400kV Podgorica(ME)-Trebinje(BA), with two transformers 2X300MVA 400/110kV, and convertor station for the DC cable Tivat-Villanova (see 70). | market integration. Operation of Montenegrin grid to be improved | RES integration, market integration, increase of NTC. | design & permitting | 2014/2015 |  | signed contract between governments of Italy and Montenegro regarding construction of the AC interconnector IT/ME
233b | Cont.SE | Tivat (ME) | Pljevlja (ME) | New transmission line connecting existing substation Pljevlja and new substation Tivat. It is part of the new interconnection project ME/IT | market integration, need for new DC cable between ME-IT. N-1 security | Improved security of supply, market integration (creation of new interface between countries). | design & permitting | 2016 |  | signed contract between governments of Italy and Montenegro regarding construction of the AC interconnector IT/ME
234 | CSE | Elbasan (AL) | Tirana(AL) | New 400kV AC OHL. Length: 48km. | Need to strengthen the sparse structure of the South East Europe network and to increase the grid capability to transmit power from countries with surplus generation (BG, RO) towards Italy. | The project is expected to increase NTC and Improved the security of supply. | under construction | 2010
235 | CSE | Tirana(AL) | Pristina(RS) | New 238km 400kV OHL; on 78km the circuit will be installed on the same towers as the Tirana-Podgorica OHL currently in construction (see project 233); the rest will be built as single circuit line. | Need to strengthen the sparse structure of the South East Europe network and to increase the grid capability to transmit power from countries with surplus generation (BG, RO) towards Italy. | The project is expected to increase NTC and Improved the security of supply. | under consideration | tbd
236 | CSE | Nis (RS) | Stip (MK) | New 220km 400kV single circuit overhead interconnection between Serbia and FYROM. A new 400/110 substation will be built in Serbia between connection nodes. | Low NTC value between Romania,Serbia and Bulgaria from one side and Greece, Albania and FYROM from other side. Improvement of voltage profile in South Serbia. | The project will increase of NTC and Improved the operational safety & the quality of supply in both countries. | Under construction in RS and design & permitting in MK | 2011/2013 | X
237 | CSE | TPP Kosovo (RS) | Skopje (MK) | A new 400kV OHL relevant to planning investment of 2000MW of TPP in the area of Kosovo and Metohija. Line length: 85km. | Project will alleviate mainly the need to increase 1) the capability of the grid to accommodate additional generation capacity and 2) the transmission capacity of the grid. | The project is expected to favour conventional generation integration and increase the NTC. | under consideration | long term
238 | CSE CCE | Pancevo (RS) | Resita (RO) | New 150km double circuit (single wired at the beginning) 400kV OHL between existing substations. | Need to alleviate the congestion limiting export from Eastern to Western part of South Eastern Europe. Foreseen wind farms in Serbia and Romania need also to be accommodated. | The project will provide an increase of NTC and favour RES integration. | design & permitting | 2015
239 | CSE | Bitola (MK) | Elbasan (AL) | New 200km cross-border single circuit 400kV OHL between existing substations. | Need to strengthen the sparse structure of the South East Europe network and to increase the grid capability to transmit power from countries with surplus generation (BG, RO) towards Italy. | In combination with the recently commissioned 400kV link MK-BG, this project is part of the East-West corridor in South-Eastern Europe. The project will increase the NTC and favour conventional generation integration. | under consideration | long term
240 | CSE | Patras (GR) | 400kV Continental System (GR) | New 400kV substation in Patras (GIS Technology) and in&out connection to the existing Axeloos - Distomo 400kV OHL via a new 15km double circuit line, part of which will consist of subsea cable. The project shall constitute the first 400kV corridor to Peloponnese. | Future generation evacuation and demand growth. | The project will improve the security of supply, favour conventional generation &RES integration. | design & permitting | 2013 | X
241 | CSE | Patras (GR) | Megalopolis (GR) | New 400kV substation in Megalopolis and connection to Patras 400kV substation via a 110km double circuit OHL. 2nd corridor to Peloponnese. | Future generation evacuation and demand growth. | The project will improve the security of supply, favour conventional generation &RES integration. | design & permitting | 2013 | X
242 | CSE | Megalopolis (GR) | Korinthos (GR) | Construction of a new 400kV substation in Korinthos (GIS Technology) and connection to the Megalopolis substation via a 110km double circuit 400kV OHL. | Future generation evacuation and demand growth. | The project will improve the security of supply, favour conventional generation &RES integration. | design & permitting | 2014 | X
243 | CSE | Korinthos (GR) | Koymoyndoyros (GR) | Replacement of the existing 150kV double circuit line by a 87km double circuit 400kV OHL. | Future generation evacuation and demand growth. | The project will improve the security of supply, favour conventional generation &RES integration. | design & permitting | 2014 | X
244 | CSE | Filippi(GR) | Lagadas (GR) | New 400kV substation in Lagadas in Thessaloniki area and connection to the existing substation of Filippi via a new 110km double circuit 400kV OHL. | Market integration, future RES and conventional generation evacuation and improvement of security of supply. | The project will improve the security of supply, favour conventional generation & RES integration. | design & permitting | 2012
245 | CSE | N.Santa (GR) |  | Construction of the new 400kV S/S N.Santa in North Greece. This S/S will serve as the interface for the new line GR-TR, as well as for the interconnection of new wind farms and conventional generation. | Market integration, future RES and conventional generation evacuation and improvement of security of supply. Future interconnection with Turkey. | Increase of NTC, conventional generation integration and RES integration. | under construction | 2012
246 | CSE | Aliveri(GR) | System (GR) | Construction of the new 400kV S/S Aliveri in Eviai area and a new 400kV double circuit line Aliveri-System. Line length: 72km. | Future RES and conventional generation evacuation. | Improved security of supply, conventional generation integration and RES integration. | design & permitting | 2011
247 | CSE | Aliveri(GR) | Larimna (GR) | Construction of the new 400kV S/S Aliveri in Eviai area and a new 400kV double circuit line Aliveri-System. Line length: 128km. | Future RES and conventional generation evacuation. | Improved security of supply, conventional generation integration and RES integration. | design & permitting | 2014
248 | CSE | Polypotamo (GR) | N. Makri (GR) | New 150kV double circuit subsea cable. Line length:33km. | Radial connection of wind farms. | RES integration. | under construction | 2011
249 | CSE | Polypotamo (GR) | N. Evia (GR) | New 150kV double circuit OHL. Line length: 40km. Along the new transmission line, 4 new 150/20kV substation shall be build for the interconnection of new wind farms in Evia island. | Radial connection of wind farms. | RES integration. | design & permitting | 2010
250 | CSE | Lavrion (GR) | Syros (GR) | New 150kV subsea cable DC connection. There is also the possibility to use AC if proved technically and economically feasible. | Connection of isolated systems and future RES integration. | Improved security of supply and reduce energy costs. | design & permitting | long term | X
251 | CSE | Syros (GR) | Cyclades (GR) | New 150kV subsea cables and 4x150kV Substations to islands of Paros, Naxos, Mykonos, Evia. | Connection of isolated systems and future RES integration. | Improved security of supply. | design & permitting | long term | X
252 | CSE | Melliti (GR) | Kardia (GR) | New 400kV double circuit OHL. Length:40km. | Improve security of supply, strengthen of North to South corridor. | Increase of security of supply and market integration. | design & permitting | 2013
253 | CSE | Kardia (GR) | Trikala (GR) | New 400kV double circuit OHL. Length:80km. | Improve security of supply, strengthen of North to South corridor. | Increase of security of supply and market integration. | design & permitting | long term
254 | CSE | Larissa(GR) | Trikala (GR) | New 400kV double circuit OHL. Length:57km. | Market integration. | Increase of export capabilities to Italy. | under consideration | long term
255 | CSE | Lamia (GR) |  | Construction of a new 400kV EHV SS in Lamia and connection to the two circuits of the existing 400kV lines Trikala-Distomo and Larisa-Larymna. | Demand growth and equipment enhancement. | Improved security of supply. | planned | long term
256 | CSE | Maritas East 1 (BG) | N.Santa (GR) | New interconnection line BG-GR by a 130km single circuit 400kV OHL. | Increase of NTC, future generation evacuation and stability enhancement of the future interconnection with Turkey. | Increase the security of the interconnection of BG, GR,TR, help reduce annual losses reduction and increase the transfer limit between GR and BG and BG and Turkey. | under consideration | 2012/2015
257 | CSE | Maritas East 1 (BG) | Plovdiv (BG) | New 93km single circuit 400kV OHL in parallel to the existing one. | Need to connect new 2x300MW generators in M.East1. | This project aims to provide a secure connection of the new generators in M.East, increase the transfer limit between GR and BG and BG and Turkey and increase the security of the interconnection of BG, GR,TR. | planned | 2013
258 | CSE | Maritas East 1 (BG) | Maritas East 3 (BG) | New 13km single circuit 400kV OHL in parallel to the existing one. | Need to connect new 2x300MW generators in M.East1. | This project aims to provide a secure connection of the new generators in M.East, increase the transfer limit between GR and BG and BG and Turkey and increase the security of the interconnection of BG, GR,TR. | planned | 2012
259 | CSE | Plovdiv (BG) | Zlatica (BG) | New 75km single circuit 400kV OHL. | Need to supply the growing demand of the area. | This project aims to increase the security of the Plovdiv region and the Bulgarian system in general. | under construction | 2010
260 | CSE | Plovdiv (BG) | Aleko(BG) | Reconstruction of the existing 220kV OHL and the building of a new second one. Line length: 40km. | For some regimes this line gets overloaded. Main bottleneck of Turkey TTC. | Eliminate the bottleneck, increase the thermal limit from 228 MVA to 720 MVA, increase the security of the Plovdiv region and TTC of Turkey . | planned | 2012
261 | CSE | Karnobat (BG) | Dobrudja (BG) | This project concerns the reconstruction of the existing 220kV OHL. Line length: 95km. | Demand growth. A very important connection between South East generation region and Middle East region - with a big consumption. | Increase the security of the system. | planned | 2013
262 | CSE | Maritas East 1 (BG) | Burgas (BG) | New 400kV OHL. Line length: 135km. | Increase the security of supply of the Burgas region in the maintenance period. | Increase the security of supply of the Burgas region in the maintenance period, increase the transfer limit between GR and BG and BG and Turkey and increase the security of the interconnection of BG, GR,TR. | planned | mid term
263 | CSE | Krushari (BG) |  | New 400/110kV substation to accommodate RES generation. | RES penetration. | Wind generation integration. | planned | 2020
264 | CSE | Vidno (BG) |  | New 400/110kV substation to accommodate RES generation. | RES penetration. | Wind generation integration. | planned | 2020
265 | CSE | Vidno (BG) | Krushari (BG) | New 400kV double circuit OHL to accommodate RES generation. Line length: 2x115km. | RES penetration. | Wind generation integration. | planned | 2020
266 | CSE | Existing interconnection 400kV line Varna (BG) - Issacea (RO) | Krushari (BG) | New 400kV double circuit OHL to accommodate RES generation. Line length: 2x10km. | RES penetration. | Wind generation integration. | planned | 2020
267 | CCE CSE | Suceava (RO) | Baltic (MO) | New 400kV transmission line between existing station in Romania and new substation in Moldavia. Line length: 145km. | Market integration. Creating export opportunities from Ukraine to ENTSO-E countries. | Increase of NTC. | planned | >2020
268 | CCE CSE | Constanta (RO) | Pasakoy (TR) | New DC link (subsea cable) between existing stations in RO and TR. Line length: 400km. | Market integration. | Market. | design & permitting | 2020
269 | CCE CSE | Portile de Fier (RO) | Resita (RO) | New 400kV OHL between existing stations. Line length: 121km. | Need to strengthen the grid between West and Central of Romania. | Increase of NTC and RES integration. | design & permitting | 2015
270 | CCE CSE | Resita( RO) | Timisoara-Sacalaz-Arad (RO) | Upgrade of an existing 220kV single circuit line to 400kV. Line length: 128km. | Need to strengthen the grid between West and Central of Romania. | Increase of NTC and RES integration. | design & permitting | 2019
271 | CCE CSE | IN-OUT in Medgidia on actual 400kV OHL Isaccea-Varna (RO) |  | New400kV double circuit OHL between existing stations. Line length: 13km. | Need to expand the network for access by new generator. | Conventional generation and RES integration. | design & permitting | 2015
272 | CCE CSE | IN-OUT in Medgidia on actual 400kV OHL Isaccea-Dobrudja (RO) |  | New 400kV double circuit OHL between existing stations. Line length: 10km. | Need to expand the network for access by new generator. | Conventional generation and RES integration. | design & permitting | 2014
273 | CCE CSE | Cernavoda (RO) | Stalpu (one line in-out G.Ialomitei - RO) | New 400kV double circuit OHL between existing stations. Line length:171km. | Need to expand the network for access by new generator. | Conventional generation and RES integration. | design & permitting | 2017
274 | CCE CSE | Constanta (RO) | Medgidia(RO) | New 400kV double circuit (one circuit wired) OHL between existing stations. Line length:171km. | Market integration. | Increase of NTC, RES integration and increase security of supply. | design & permitting | 2016
275 | CCE CSE | Smardan(RO) | Gutinas(RO) | New 400kV double circuit OHL between existing stations. Line length:140km. | Need to expand the network for access by new generator. | Conventional generation and RES integration. | design & permitting | 2016
276 | CCE CSE | Suceava(RO) | Gadalin(RO) | New 400kV OHL between existing stations. Line length: 260km. | Need to strengthen the grid between East and West of Romania. | Increase of NTC and RES integration. | planned | 2019
277 | CCE CSE | Heviz (HU) | Szombathely (HU) | New 400kV transmission line between existing stations. Line length: 78km. | In transmission outage situation the underlying distribution network is at risk of overload. | Increased operational security. | under construction | 2009
278 | CCE CSE | Gyor / Liter (HU) | Gonyu (HU) | New substation Gonyu (generator connection point) is connected by splitting and extending existing line Gyor-Liter. | Need to expand the network for access by new generator. | Conventional generation integration. | under construction | 2010
279 | CCE CSE | Gyor (HU) | Martonvasar (HU) | Upgrade of an existing 220kV single circuit line to 400kV double circuit. Line length:84km. | Need to strengthen the grid between Northwest and Central Hungary. | Increased operational security. | design & permitting | 2012
280 | CCE CSE | Gyor / Martonvasar (HU) | Bicske (HU) | New substation Bicske with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Gyor-Martonvasar line. | Need to increase transformation capacity towards distribution. | Increased security of supply. | design & permitting | 2012
281 | CCE CSE | Albertirsa (HU) | Martonvasar (HU) | Adding second circuit to existing 400kV single circuit OHL. Line length: 45km. | Need to improve coupling between North -East and North - West Hungary 400kV grid areas. | Increased operational security. | design & permitting | 2012
282 | CCE CSE | Sajoszoged / God (HU) | Detk (HU) | New substation Detk with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Sajoszoged-God. | High 220/120kV transformer's lose. Improve N-1 security. Connection point is needed for new generator. | Increased operational security and conventional generation integration. | design & permitting | 2012
283 | CCE CSE | Albertirsa / Bekescsaba (HU) | Szolnok (HU) | New substation Szolnok with 2*250 MVA 400/120kV transformers is connected by splitting and extending existing line Albertirsa-Bekescsaba. | High 220/120kV transformers lose, improve N-1 security of supply. | Increased operational security. | design & permitting | 2012
284 | CCE CSE | Martonvasar / Paks (HU) | Dunaujvaros (HU) | New substation Dunaujvaros with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Martonvasar-Paks. | High 220/120kV transformers lose, improve N-1 security of supply. | Increased operational security. | design & permitting | 2012
285 | CCE CSE | Debrecen (HU) |  | New substation Debrecen with 2*250 MVA 400/120kV transformation is connected by changing the operating voltage of line Sajoszoged-Debrecen from 220kV to 400kV, this line being already designed for 400kV. | High 220/120kV transformers lose, improve N-1 security of supply. | Increased operational security. | planned | 2013
286 | CCE CSE | Martonvasar / Liter (HU) | Szekesfehervar (HU) | New substation Szekesfehervar with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Martonvasar-Liter. | Need to increase transformation capacity towards distribution. | Increased operational security. | planned | 2014
287 | CCE CSE | Albertirsa / God (HU) | Godollo (HU) | New substation Godollo with 2*250 MVA 400/120kV transformation is connected by splitting and extending existing line Albertirsa-God. | Need to increase transformation capacity towards distribution. | Increased operational security. | planned | 2015
288 | CCE CSE | Albertirsa / Martonvasar (HU) | Szazhalombatta (HU) | New substation Szazhalombatta is connected by splitting and extending existing line Albertirsa-Martonvasar. | Need to expand the network for access by new generator. | Conventional generation integration. | planned | 2015
289 | CCE CSE | Felsozsolca (HU) | Sajoivanka (HU) | Reconstruction of line to double circuit, installation of the 2nd transformer in substation Sajoivanka. Line length: 29km. | Need to increase transformation capacity towards distribution. | Increased operational security. | under consideration | 2015
290 | CCE CSE | Oroszlany (HU) |  | New substation Oroszlany with 2*250 MVA 400/120kV transformation is connected by splitting and extending the second circuit of line Martonvasar-Gyor. | Need to build new transformer station as old 220/120kV station will be dismantled. | Increased operational security. | under consideration | 2017
291 | CCE CSE | Sajoszoged (HU) |  | New 400/120kV 250MVA transformer with PST. | High 220/120kV transformers lose, improve N-1 security of supply. | Increased operational security. | under consideration | 2017
292 | CCE CSE | Debrecen (HU) |  | Reconstruction of 750kV substation. | 750kV equipment in station Albertirsa reach end of life in 2012, alternative location is considered for improved cost-benefit. | Reduced operating cost. | under consideration | 2013
293 | CCE | Voľa (SK) | point of splitting (SK) | Splitting of the existing single 400kV line between Lemešany and Veľké Kapušany substations to connect the new 400kV substation Voľa with transformation 400/110kV (replacing existing 220kV substation). New 400kV double circuit OHL. Length: 23km. | Request of relevant DSO on future demand growth in next 4 years. New generation units are expected in the future in this area as well. | Improved security of supply and secure and reliable power output evacuation . | design & permitting | 2013
294 | CCE | Lemešany (SK) | Veľké Kapušany (SK) | Restoration of the old 400kV line between Lemešany and Veľké Kapušany substations by installing a second circuit. Line length:74km. | Ensuring of electricity evacuation from new perspective power plant, reinforcement of eastern part of Slovak power system. | Improved security of supply and secure and reliable power output evacuation. | planned | 2018 | X | TEN-E funding is designated for environmental impact assessment study.
295 | CCE | Lemešany (SK) | Moldava (SK) | New 31km double circuit 400kV line, replacing a 220 kV one. The part of the line from Moldava substation up to switching substation Košice was put into operation in 10/2009. | Ensure electricity supply to an important transmission system consumer, now via Košice (400kV) and no more via Lemešany (220kV). Reinforce the Eastern part of the Slovak power system in north-south direction. | Improved security of supply. | under construction | 2011
296 | CCE | Medzibrod (SK) | point of splitting (SK) | Connection of existing 220/110kV Medzibrod substation to the 400kV system by splitting the single 400kV line Sučany - Liptovská Mara. Project includes also the reconstruction of Medzibrod substation from 220kV level to 400kV including transformation 400/110kV. Line length:36km. | Need to enhance electricity supply to Medzibrod nodal area and for an important consumer which is at the same time a significant employer in the concerned region. | Improved security of supply. | design & permitting | 2013
297 | CCE | Križovany (SK) | Horná Ždaňa (SK) | The new substation Bystričany with transformation 400/110kV will be connected to the 400kV system by two new 2x400kV lines from Horná Ždaňa and Križovany substations by splitting only one circuit in Bystričany substation. In the future the substation will be also equipped with a 220kV switchgear. Line length:112km. | The project is linked to the decommissioning of NPP Jaslovské Bohunice V1. Beyond that, there is a need to enhance power withdrawal from new potential generation units, and ensure electricity supply to the industrial area. | Secure and reliable power output evacuation, improved security of supply and internal power system reinforcement. | Planned | 2020 |  | Decision regarding funding from BIDSF is expected in following months.
298 | CCE | Veľký Ďur (SK) | Gabčíkovo (SK) | Erection of new 2x400kV line between two important substations and erection of new switching station Gabčíkovo next to the existing one. Line length:93km. | Need to enhance power withdrawal from new potential generation units in Western Slovakia. | Secure and reliable power output evacuation and Improved security of supply. There are new generation units expected in concerned area, therefore the effect of this line is expected in this way. The project might improve exchange capacity on the Slovak - Hungarian profile. | Planned | 2020 |  | The project is associated to the new Slovak - Hungarian interconnection from Gabčíkovo substation (see project 214).
299 | CCE | Krasikov (CZ) | Horni Zivotice (CZ) | New single circuit 400kV OHL, 1385 MVA. | Need to strengthen the grid in the direction North-south of the system. | Improved operational security ; reduction of infrastructure vulnerability. | design & permitting | 2014
300 | CCE | Chotejovice (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA . | Connection point of a new power unit 660MW. | Conventional generation integration ; reduction of infrastructure vulnerability. | design & permitting | 2011
301 | CCE | Vyskov (CZ) | Chotejovice (CZ) | New single circuit 400kV OHL; 1385 MVA. | Connection of new 400kV substation (Chotejovice) into the rest of the network system. | Conventional generation integration. | design & permitting | 2011
302 | CCE | Vyskov (CZ) | Cechy stred (CZ) | New second circuit 400kV OHL; 1385 MVA. | Need to strengthen the grid in the central part of CZ through doubling the OHL line. Facilitate flow from West to East. | Enhancing security of supply of CZ grid. | planned | 2015
303 | CCE | Babylon (CZ) | Bezdecin (CZ) | New second circuit 400kV OHL; 1385 MVA. | Need to facilitate flow form West to East and enhance security of supply; Facilitate flow from West to East. | Improved security of supply. | planned | 2016
304 | CCE | Babylon (CZ) | Vyskov (CZ) | New second circuit 400kV OHL; 1385 MVA. | Need to facilitate flow form West to East and enhance security of supply. Facilitate flow from West to East. | Improved security of supply. | planned | 2018
305 | CCE | Kletne (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA . | Need to increase transformation capacity to distribution. | Reduction of infrastructure vulnerability. | design & permitting | 2011
306 | CCE | Vitkov (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA. | Need to facilitate connection of RES power generation from 110kV to 400kV, new 400kV interconnection node to DE. | RES integration. | planned | 2015
307 | CCE | Vernerov (CZ) |  | New 400/110kV substation equipped with transformers 2x350MVA. | Need to facilitate connection of RES power generation from 110kV to 400kV, new 400kV connection node to rest of the network. | RES integration ; reduction of infrastructure vulnerability. | planned | >2015
308 | CCE | Vernerov (CZ) | Vitkov (CZ) | New 400kV double circuit OHL, 1385 MVA. | Need to facilitate connection of RES in CZ and enhance security of supply; facilitate flow between CZ and DE. | RES integration ; improved security of supply. | under consideration | >2015 |  | Connection of 2 new 400 kV substations and facilitate power flow between CEPS and tsp
309 | CCE | Vitkov (CZ) | Prestice (CZ) | New 400kV double circuit OHL, 1385 MVA. | Need to facilitate connection of RES in CZ and enhance security of supply. Facilitate flow between CZ and DE. | RES integration ; improved security of supply. | planned | 2020 |  | Connection of 2 new 400 kV substations and facilitate power flow between CEPS and tsp
310 | CCE | Vyskov (CZ) | Reporyje (CZ) | New connection between 2 existing substations line single circuit OHL 1385 MVA. | Need to strengthen the grid in the central part of CZ and enhance security of supply. | Improved security of supply. | under consideration | >2015
311 | CCE | Kocin (CZ) |  | Upgrade of the existing substation 400/110kV; upgrade transformers 2x350MVA. | Future generation evacuation, prevention of high short - circuit current. | Conventional generation integration ; reduction of infrastructure vulnerability. | planned | 2015/2020
312 | CCE | Mirovka (CZ) |  | Upgrade of the existing substation 400/110kV with two transformers 2x250MVA. | Future generation evacuation. | Conventional generation integration ; reduction of infrastructure vulnerability. | planned | 2017/2018
313 | CCE | Kocin (CZ) | Mirovka (CZ) | Connection of 2 existing 400kV substations with double circuit OHL having 120.5km length: and a capacity of 2X1385 MVA. | Future generation evacuation. | Conventional generation integration ; reduction of infrastructure vulnerability. | planned | 2017/2018
314 | CCE | Mirovka (CZ) | V413 (CZ) | New double circuit OHL with a capacity of 2x1385 MVA and 26.5km length. | Need to strengthen the grid. Facilitate flow from West to East. | Enhancing security of supply of CZ grid. | planned | 2018/2019
315 | CCE | Kocin (CZ) | Prestice (CZ) | Adding second circuit to existing single circuit line OHL upgrade in length of 115.8km. Target capacity 2x1385 MVA. | Need to strengthen the grid. | Enhancing security of supply of CZ grid. | planned | 2019/2021
316 | CCE | Mirovka (CZ) | Cebin (CZ) | Adding second circuit to existing single circuit line (88.5km, 2x1385 MVA). | Need to strengthen the grid. | Enhancing security of supply of CZ grid. | planned | 2019/2021
317 | CCE | Hradec (CZ) | Reporyje (CZ) | Upgrade of existing 400kV single circuit OHL with length of 116.9km. Target capacity 1385 MVA. | Need to facilitate flow form West to East and enhance security of supply. | Enhancing security of supply of CZ grid; RES integration. | design & permitting | 2014
319 | CCE Baltic Sea | Skawina (PL) |  | A new AC 400/110kV substation next to existing 220/110kV substation in Cracow Agglomeration Area with transformation 400/110kV 2x400 MVA. New substation Skawina is connected by splitting and extending of existing 400kV lines Tarnów - Tucznawa and Rzeszów - Tucznawa. Dismantling of existing 220/110kV transformers. | Connection to the network of power plants. | Conventional generation integration ; improved security of supply. | design & permitting | 2015
320 | CCE Baltic Sea | Dargoleza (PL) |  | A new AC 400/110kV (400 MVA) substation between existing substations Słupsk and Żarnowiec in Northern Poland. New substation Dargoleza is connected by splitting and extending of existing 400kV line Słupsk - Dargoleza. | Connection to the network of RES. | RES integration ; improved security of supply. | planned | 2015
321 | CCE Baltic Sea | Kromolice (PL) | Pątnów (PL) | New 79km 400kV 1870 MVA OHL interconnection line Kromolice - Pątnów - with one circuit from Plewiska to Koninn temporarily on 220kV after dismantling of 220kV line Plewiska - Konin. | Power output from generating units connected to the transmission network. | Conventional generation integration ; improved security of supply. | under construction | 2015 | X
322 | CCE Baltic Sea | Kromolice (PL) |  | A new AC substation between existing substations Plewiska and Ostrów and Pątnów in Poznań Agglomeration Area with transformation 400/110kV 400 MVA. New substation Kromolice is connected by splitting and extending existing line Ostrów-Plewiska and Pątnów - Plewiska. | Safe operation of the system - increase of the power demand. | Improved security of supply ; increased of NTC. | under construction | 2015
323 | CCE Baltic Sea | Warszawa Siekierki (PL) | Piaseczno (PL) | A new AC 220/110kV substation (with transformation 220/110kV 2x275MVA) in Warsaw Agglomeration Area connected by a new 20km 220kV 333 MVA cable/OHL line Warszawa Siekierki - Piaseczno. | Power output from generating units connected to the transmission network. | Conventional generation integration ; improved security of supply. | design & permitting | 2015
324 | CCE Baltic Sea | Dobrzeń (PL) | Wrocław/ Pasikurowice (PL) | New 50km 400kV 2x1870 MVA OHL double circuit line from Dobrzeń to splitted Pasikurowice - Wrocław line. | Power output from generating units connected to the transmission network. | Conventional generation integration ; improved security of supply ; Increased of NTC. | design & permitting | 2015
325 | CCE Baltic Sea | Krajnik (PL) | Pomorzany (PL) | A new AC substation in Szczecin Agglomeration Area. New substation Pomorzany is connected by new 24km 220kV 522 MVA line Krajnik - Pomorzany and 220/110kV (275 MVA) transformer to existing 110kV switchgear. | Power output from generating units connected to the transmission network. | Conventional generation integration ; improved security of supply. | planned | 2015
326 | CCE Baltic Sea | Grudziądz (PL) | Gdańsk Przyjaźń (PL) | A new AC 400/110kV substation between existing substation Grudziądz and planned substation Gdańsk Przyjaźń with transformation 400 MVA . New substation Pelplin is connected by new 110km 400kV 2x1870 MVA OHL double circuit lines Grudziądz - Pelplin and Pelplin - Gdańsk Przyjaźń after dismantling of 220kV line Jasiniec - Gdańsk. | Power output from generating units connected to the transmission network. | Conventional generation integration ; improved security of supply. | planned | 2015
327 | CCE Baltic Sea | Kozienice (PL) | Ołtarzew (PL) | New 130km 400kV 2x1870 MVA OHL double circuit line Kozienice - Ołtarzew. | Power output from generating units connected to the transmission network. | Conventional generation integration ; improved security of supply. | design & permitting | 2015
328 | CCE Baltic Sea | Piła Krzewina (PL) | Bydgoszcz Zachód (PL) | New 84km 400kV 1870 MVA OHL interconnection line Piła Krzewina - Bydgoszcz Zachód temporarily on 220kV. | Power output from RES. | RES integration ; improved security of supply. | design & permitting | 2015
329 | CCE Baltic Sea | Żydowo (PL) | Słupsk (PL) | A new AC 400/110kV substation next to existing 220/110kV substation in Northern Poland with transformation 400/110kV 400 MVA. New substation Żydowo is connected by new 70km 400kV 2x1870 MVA OHL double circuit lines Żydowo - Słupsk and Żydowo - Gdańsk Przyjaźń. Dismantling of existing 220/110kV. transformers. | Power output from RES. | RES integration ; improved security of supply. | planned | 2015
330 | CCE Baltic Sea | Żydowo (PL) | Gdańsk Przyjaźń (PL) | A new AC substation in Gdańsk Agglomeration Area. New substation Gdańsk Przyjaźń is connected by splitting and extending of one circuit of existing line Żarnowiec - Gdańsk Błonia and new 150km 400kV 2x1870 MVA double circuit OHL line Żydowo - Gdańsk Przyjaźń with one circuit from Żydowo to Gdańsk temporarily on 220kV after dismantling of 220kV line Żydowo - Gdańsk. | Power output from RES. | RES integration ; improved security of supply. | planned | 2015
331 | CCE Baltic Sea | Gorzów (PL) | Leśniow (PL) | Upgrading of sag limitations (new capacity 461 MVA). | Power output from RES, upgrading of sag limitations. | RES integration ; improved security of supply; Increase of NTC. | planned | 2015
332 | CCE Baltic Sea | Recław (PL) | Glinki (PL) | A new AC substation in Szczecin Agglomeration Area. New substation Recław is connected by new 52km 220kV 522 MVA line Recław - Glinki, existing 110kV single circuit line Morzyczyn - Recław upgraded to 220kV and two 220/110kV (275 MVA) transformer to existing 110kV switchgear. Splitting of existing 220kV line Morzyczyn - Police and expanding to Glinki substation. | Power output from RES. | RES integration ; improved security of supply. | design & permitting | 2015
333 | CCE Baltic Sea | Pasikurowice (PL) | Świebodzice (PL) | A new AC substation in Wrocław Agglomeration Area. New substation Wrocław is connected to new 135km (sum) 400kV 1870 MVA lines: Pasikurowice-Wrocław and Świebodzice - Wrocław. New 400kV Wrocław substation with 2x400 MVA, 400/110kV transformation. New 400kV Świebodzice substation with 1x500MVA, 400/220kV transformation and 1x400 MVA, 400/110kV transformation. New 400kV OHL interconnection line Wrocław - Świebodzice after dismantling of 220kV line Świebodzice - Biskupice and new 400kV OHL interconnection line Pasikurowice - Wrocław, including new Wrocław substation. | Safe operation of the system - change of the voltage in the network (elimination of the network congestions) and safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply. | under construction | 2015
334 | CCE Baltic Sea | Pątnów (PL) | Grudziądz (PL) | New 174km 400kV 2x1870 MVA double circuit OHL line Pątnów - Grudziądz after dismantling of 220kV line Pątnów - Jasiniec (two parallel lines) and Jasiniec - Grudziądz. One circuit from Pątnów to Grudziądz via Jasiniec temporarily on 220kV. | Safe operation of the system - change of the voltage in the network (elimination of the network congestions). | Improved security of supply; Increase of NTC. | design & permitting | 2015 | X
335 | CCE Baltic Sea | Ostrołęka (PL) | Olsztyn Mątki (PL) | New 138km 400kV 2x1870 MVA double circuit OHL line Ostrołęka - Olsztyn Mątki after dismantling of 220kV line Ostrołęka - Olsztyn with one circuit from Ostrołęka to Olsztyn temporarily on 220kV. | Safe operation of the system - change of the voltage in the network (elimination of the network congestions). | Improved security of supply. | design & permitting | 2015
336 | CCE Baltic Sea | Warszawa Praga (PL) |  | A new AC substation with 2x275 MVA 220/110kV transformation between existing substations Miłosna and Mory in Warszawa Agglomeration Area, New substation Warszawa Praga is connected by splitting and extending existing line Miłosna-Mory. | Safe operation of the system - increase of the power demand. | Improved security of supply. | planned | 2015
337 | CCE Baltic Sea | Radkowice (PL) | Kielce Piaski (PL) | New 26km 220kV 522 MVA OHL line Radkowice -Kielce Piaski, in Kielce agglomeration area. | Safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply. | design & permitting | 2015
338 | CCE Baltic Sea | Kozienice (PL) | Mory/ Piaseczno (PL) | Replacement of conductors (high temperature conductors). | Safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply. | under construction | 2015
339 | CCE Baltic Sea | Morzyczyn (PL) |  | A new AC substation in Szczecin Agglomeration Area with transformation 400/220kV 330 MVA and 400/110kV 330 MVA. New substation Morzyczyn is connected by splitting and extending existing 400kV line Krajnik - Dunowo. | Safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply. | under construction | 2015
340 | CCE Baltic Sea | Lubocza (PL) |  | An existing substation in Kraków Agglomeration Area. Existing substation will be upgraded by splitting and extending existing 220kV line Siersza- Klikowa and installing second ATR 220/110kV (160 MVA). | Safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply. | planned | 2015
341 | CCE Baltic Sea | Pątnów (PL) | Włocławek (PL) | Upgrading of sag limitations OHL 220kV (389 MVA). | Safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply; Increase of NTC. | planned | 2015
342 | CCE Baltic Sea | Czarna (PL) | Polkowice (PL) | New 400kV OHL interconnection line Czarna -Polkowice (1870 MVA, 22km), including new Polkowice 400kV substation with 500 MVA, 400/220kV transformation. | Safe operation of the system - couplings 220kV with 400kV transmission network (elimination of the network congestions). | Improved security of supply; Increase of NTC. | design & permitting | 2015
343 | CCE Baltic Sea | Byczyna (PL) |  | Upgrading of existing AC 220kV substation Byczyna. A new 400kV AC substation in Silesia Agglomeration Area with transformation 400/220kV 2x 500 MVA. New substation Byczyna is connected by splitting and extending existing line Tarnów - Tucznawa. | Safe operation of the system - couplings 220kV with 400kV transmission network (elimination of the network congestions) and Power output from generating units connected to the transmission network. | Conventional generation integration ; improved security of supply. | under construction | 2015
344 | CCE Baltic Sea | Lublin Systemowa (PL) | Abramowice (PL) | New 220kV cable/OHL interconnection line Lublin Systemowa - Abramowice, in Lublin agglomeration area (522 MVA, 18km). | Safe operation of the system - couplings 220kV with 400kV transmission network (elimination of the network congestions). | Improved security of supply. | design & permitting | 2015
345 | CCE Baltic Sea | Łagisza (PL) |  | A new AC 400kV switchgear in existing substation Łagisza (with transformation 400/220kV 500 MVA and 400/110kV 330 MVA) is connected by splitting and extending of existing 400kV lines Rokitnica - Tucznawa. | Connection to the network of power plants. | Conventional generation integration ; improved security of supply. | under construction | 2015
346 | CCE Baltic Sea | Halemba (PL) |  | Halemba substation is connected by splitting and extending of existing 220kV lines Kopanina - Katowice. | Power output from generating units connected to the transmission network. | Conventional generation integration ; improved security of supply. | planned | 2015
347 | CCE Baltic Sea | Gdańsk I (PL) |  | A new AC 400kV switchgear in existing substation Gdańsk I is connected by splitting and extending of existing 400kV lines Żarnowiec - Gdańsk Błonia. | Safe operation of the system - couplings 220kV with 400kV transmission network (elimination of the network congestions). | Improved security of supply. | under construction | 2015
348 | CCE Baltic Sea | several substations in PSE O control area |  | Installation additional and exchange existing transformers (400/110kV and 220/110kV), capacitors and SVC in substations, upgrading of substations. | Safe operation of the system - increase of the power demand and voltage and reactive power control. | Improved security of supply. | planned | 2015
349 | CCE Baltic Sea | Puławy (PL) |  | A new AC 400kV switchgear in existing substation Pulawy (with transformation 400/220kV 500 MVA) will be connected by splitting and extending existing 400kV lines: Kozienice- Lublin Systemowa and Kozienice - Ostrowiec. | Connection to the network of power plants. | Conventional generation integration ; improved security of supply. | planned | 2020
350 | CCE Baltic Sea | "East" Power Plant (PL) |  | A new AC substation "East" Power Plant + Construction of a new 400kV OHL East Power Plant -Siedlce Ujrzanów (2x1870 MVA)+ Construction of a new 400kV OHL East Power Plant -Chełm with single circuit (1870 MVA) + Construction of a new 400kV OHL East Power Plant - Lublin Systemowa (2x1870 MVA). A new AC 400kV switchgear in existing substation Chelm with transformation 400/220kV 500 MVA. | Connection to the network of power plants and Power output from generating units connected to the transmission network. | Conventional generation integration ; improved security of supply. | planned | 2020
351 | CCE Baltic Sea | Blachownia (PL) |  | A new AC 400kV switchgear in existing substation Blachownia (with transformation 400/220kV 500 MVA and 400/110kV 400 MVA) will be connected by splitting and extending existing 400kV line Joachimów - Wielopole and 220kV line Kedzierzyn - Groszowice. | Connection to the network of power plants. | Conventional generation integration ; improved security of supply. | planned | 2020
352 | CCE Baltic Sea | Dunowo (PL) | Plewiska (PL) | Construction of a new double circuit 400kV OHL Dunowo - Żydowo (2x1870 MVA) partly using existing 220kV line + Construction of a new 400kV OHL Plewiska - Piła Krzewina - Żydowo (2x1870 MVA); single circuit temporarily working as a 220kV + A new AC 400kV switchgear in existing substation Pila Krzewina with transformation 400/220kV 500 MVA. | Power output from RES and connection to the network of RES. | RES integration ; improved security of supply. | design & permitting | 2020 | X
353 | CCE Baltic Sea | Krajnik (PL) | Baczyna (PL) | Construction of a new double circuit 400kV OHL Krajnik - Baczyna (2x1870 MVA, 91km); single circuit temporarily working at 220kV on Krajnik - Gorzów part + New substation 400kV Baczyna will be connected by splitting and extending existing line Krajnik-Plewiska + Upgrading of limitations line Krajnik - Plewiska. | Power output from RES + Reinforcement of Polish internal grid. | RES integration ; improved security of supply; Increase of NTC. | planned | 2020
354 | CCE Baltic Sea | Byczyna (PL) | Podborze (PL) | Double line 400kV Byczyna-Czeczott-Podborze (2x1870 MVA, 155km) will be built in parallel with 220kV line Byczyna-Bieruń-Poręba-Podborze in the same road + New substation 400 and 220kV Podborze (with transformation 400/220kV 500 MVA) will be connected by splitting and extending existing lines Wielopole-Nosovice, Kopanina-Liskovec, Bujaków-Liskovec, Komorowice-Bieruń, Moszczenica-Poręba and new double circuit line 400kV Podborze-Czeczott. | Safe operation of the system - change of the voltage in the network (elimination of the network congestions) and safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply. | design & permitting | 2020
355 | CCE Baltic Sea | Mikułowa (PL) | Świebodzice (PL) | Double circuit line 220kV Mikułowa-Świebodzice will be upgraded to 400kV - single circuit temporarily working at 220kV (2x1870 MVA). | Safe operation of the system - change of the voltage in the network (elimination of the network congestions). | Improved security of supply; Increase of NTC. | planned | 2020 | X
356 | CCE Baltic Sea | Janów (PL) |  | New substation 400kV Janów (with transformation 400/110kV 400 MVA) will be connected by splitting and extending existing line Rogowiec-Płock. | Safe operation of the system - increase of the power demand. | Improved security of supply. | planned | 2020
357 | CCE Baltic Sea | Joachimów (PL) |  | Replacement of a transformer 400/220kV (500 MVA). | Safe operation of the system - increase of the power demand. | Improved security of supply. | planned | 2020
358 | CCE Baltic Sea | Ostrów (PL) | Kromolice (PL) | Installation of a 2nd 400kV circuit along an already existing line on the same voltage. (1870 MVA, 212km). | Safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply; Increase of NTC. | planned | 2020
359 | CCE Baltic Sea | Morzyczyn (PL) | Pomorzany/ Glinki (PL) | New line 220kV (522 MVA). | Safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply. | planned | 2020
360 | CCE Baltic Sea | Miłosna (PL) | Siekierki (PL) | New cable connection 220kV Miłosna - Warszawa Siekierki (333 MVA, 10km). | Safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply. | planned | 2020
361 | CCE Baltic Sea | Ołtarzew (PL) | Mory (PL) | Replacement of conductors (high temperature conductors). (new capacity 461 MVA). | Safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply. | planned | 2020
362 | CCE Baltic Sea | Wielopole (PL) | Moszczenica (PL) | Replacement of conductors (high temperature conductors). (new capacity 461 MVA). | Safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply. | planned | 2020
363 | CCE Baltic Sea | Byczyna (PL) | Siersza (PL) | Replacement of conductors (high temperature conductors). (new capacity 461 MVA). | Safe operation of the system - increase of the reliability (elimination of the network congestions). | Improved security of supply. | planned | 2020
364 | CCE Baltic Sea | Czarna (PL) | Polkowice (PL) | New line will be second 400kV circuit to existing line in the same direction. (1870 MVA, 22km). | Safe operation of the system - couplings 220kV with 400kV transmission network (elimination of the network congestions). | Improved security of supply and increase of NTC. | planned | 2020
365 | CCE Baltic Sea | Wyszków (PL) |  | New substation 400kV Wyszków (with transformation 400/110kV 400 MVA) will be connected by splitting and extending line Ostrołęka-Stanisławów. | Safe operation of the system - increase of the power demand. | Improved security of supply. | design & permitting | 2020
366 | CCE Baltic Sea | Rzeszów (PL) | Chmielnicka (UA) | Establish existing 750kV interconnection between Poland and Ukraine. Mode of operation on border lines (synchronous/asynchronous) depends on results of future study concerning possibility of synchronous connection of Ukraine and Moldova to continental part of ENTSO-E and bilateral Polish - Ukrainian agreement. | The project is the modernisation and resumption of existing 750kV interconnection between Poland and Ukraine. | Increase of NTC and Improved security of supply. | planned | 2020
367 | CCE Baltic Sea | several substations in PSE O control area |  | Installation of an additional transformer + replacement of an existing one (400/110kV and 220/110kV) and shunt reactors in substations, upgrading and decommissioning of substations. | Safe operation of the system - increase of the power demand and voltage and reactive power control. | Improved security of supply. | planned | 2020
368 | CCE Baltic Sea | Ełk (PL) | PL-LT border (LT) | Construction of a new 400kV OHL Ełk to PL-LT border. (2x1870 MVA, 108km). | Reinforcement in Polish internal grid in connection with project: Elk (PL) - Alytus (LT). | Increase of NTC and Improved security of supply with expected additional 600MW capacity between PL and LT. Interconnection LT-PL allow import/export between Poland and Baltic. Also this interconnection is crucial to make possible a synchronous interconnection of Baltic with other ENTSO-E countries. | design & permitting | 2015
369 | CCE Baltic Sea | Siedlce Ujrzanów (PL) | Miłosna (PL) | Construction of a new 400kV OHL Siedlce Ujrzanów - Miłosna (1870 MVA, 84km) + A new AC 400kV switchgear in existing substation Siedlce Ujrzanow with transformation 400/110kV 400 MVA. | Reinforcement in Polish internal grid in connection with project: Elk (PL) - Alytus (LT). | Improved security of supply and increase of NTC. | design & permitting | 2015
370 | CCE Baltic Sea | Ełk (PL) | New substation (Rutki) | Construction of a new 400kV double circuit OHL Ełk - Rutki (2x1870 MVA, 95km) + A new AC 400kV switchgear in existing substation Elk (in two stages) + A new AC substation Rutki. | Reinforcement in Polish internal grid in connection with project: Elk (PL) - Alytus (LT). | Improved security of supply and increase of NTC. | design & permitting | 2015 | X
371 | CCE Baltic Sea | Ostrołęka (PL) | Narew (PL) | Construction of a new 400kV OHL Ostrołęka-New substation (Rutki)-Narew (1870 MVA, 120km) + A new AC 400kV switchgear in existing substation Ostroleka (in two stages) with transformation 400/220kV 500 MVA and with transformation 400/110kV 400 MVA. | Reinforcement in Polish internal grid in connection with project: Elk (PL) - Alytus (LT). | Improved security of supply and increase of NTC. | design & permitting | 2015
372 | CCE Baltic Sea | Oltarzew (PL) |  | A new AC substation with two transformers 400/220kV 2x500 MVA and one 400/110kV 400 MVA will be connected by splitting 400kV line Rogowiec-Miłosna and Miłosna-Płock and 220kV line Mory-Sochaczew and Mory-Janów. | Reinforcement in Polish internal grid in connection with project: Elk (PL) - Alytus (LT). | Improved security of supply and increase of NTC. | under construction | 2015
373 | CCE Baltic Sea | Ostrołęka (PL) | Stanisławów (PL) | Single circuit line 220kV Ostrołęka-Miłosna will be partly upgraded to double circuit line 400kV (2x1870 MVA, 106km) with development of Ostrołęka 400kV substation + New substation 400kV Stanisławów will be connected by splitting and extending existing line Miłosna-Narew and Miłosna-Siedlce. | Reinforcement of Polish internal grid to make possible power transfer capacity (between PL and LT) of 1000MW. | Improved security of supply and increase of NTC. | design & permitting | 2020
374 | CCE Baltic Sea | Kozienice (PL) | Siedlce Ujrzanów (PL) | Existing single circuit line will be upgraded to 400kV line in the same direction (1870 MVA, 90km). | Reinforcement of Polish internal grid to make possible power transfer capacity (between PL and LT) of 1000MW. | Improved security of supply and increase of NTC. | design & permitting | 2020
375 | CCE Baltic Sea | Płock (PL) | Olsztyn Mątki (PL) | New single circuit line 400kV (1870 MVA, 180km) with development of Olsztyn Mątki 400kV substation. | Reinforcement of Polish internal grid to make possible power transfer capacity (between PL and LT) of 1000MW. | Improved security of supply and increase of NTC. | design & permitting | 2020
376 | CCE Baltic Sea | Alytus (LT) | PL-LT border (PL) | Construction of Back-to-Back convertor station near Alytus 330kV substation. Construction of double circuit 400kV OHL between Alytus and PL-LT border. Construction of 330kV AC line Alytus-Kruonis. Length of line: 46km. | Project: Elk (PL) - Alytus (LT). | Currently there are no connections between LT and PL. Increase of NTC and Improved security of supply. | design & permitting | 2015
377 | Baltic Sea | Klaipeda (LT) | Telsiai (LT) | New single circuit 330kV OHL (943 MVA, 85km). | The new line is required to take advantage of full capacity of HVDC line to Sweden. | Increase of NTC and Improved security of supply. | design & permitting | 2013
378 | Baltic Sea | Panevezys (LT) | Musa (LT) | New single circuit 330kV OHL (1080 MVA, 80km). | The new line is required to take advantage of full capacity of HVDC line to Sweden. | Increase of NTC. | planned | 2016
379 | Baltic Sea | Kruonis (LT) | Alytus (LT) | New double circuit 330kV OHL (2x1080 MVA, 53km). | new line is required to take advantage of full capacity of link to Poland. | Increase of NTC and Improved security of supply. | planned | 2020
380 | Baltic Sea | Visaginas (LT) | Kruonis (LT) | New single circuit 330kV OHL (1080 MVA, 200km). | new line is required to take advantage of full capacity of link to Poland. | Increase of NTC. | planned | 2020
381 | Baltic Sea | Visaginas (LT) | Liksna (LV) | Upgrade single circuit OHL (943 MVA, 50km). | new line is required to take advantage of full capacity of link to Poland. | Increase of NTC. | under consideration | 2020
382 | Baltic Sea | Vilnius (LT) | Neris (LT) | New single circuit 330kV OHL (943 MVA, 50km). | Additional line could be required when new Visaginas NPP will be build. | Improved security of supply. | planned | 2020
382a | Baltic Sea | Bitenai (LT) |  | New 330kV switching station. | Switching station will be build near Kaliningrad district border and will connect existing 330kV OHL Klaipeda-Sovetsk and Jurbarkas-Sovetsk. | Improved security of supply. | under construction | 2011
383 | Baltic Sea | Klaipeda (LT) | Nybro (SE) | (NordBalt) A new 300kV HVDC VSC partly subsea and partly underground cable between Lithuania and Sweden. (440km). | Connection between Lithuania and Sweden. 440km long. | Improved the market integration Nordic Baltic. Currently is no connection between LT and Sweden. | design & permitting | 2015/2016 |  | necessary documentation is under preparation
384 | Baltic Sea | RigaCHP1 (LV) | Imanta (LV) | A new 12.5km AC 330kV cable will be built from RigaCHP1 substation to Imanta substation. Both substations will be reconstructed, according new line connecting. New cable will be underground and one part will be underwater (under Daugava river). Expected capacity: 880MW. | New line will increase transmission capacity in the Riga region. Reliability and security of supply in town Riga and Latvia. | Improved security of supply and increase of NTC. | design & permitting | 2012 | X | Project is the part of the big project of Latvian grid reinforcement (Kurzeme Ring). This project is strong reinforcement of Riga transmission network, security of supply increasing and start connection point to Kurzeme Ring
385 | Baltic Sea | Grobina (LV) | Imanta (LV) | "Kurzeme Ring" is a Latvian grid reinforcement project with new 330kV OHL construction and connection to the Riga node. New 330kV OHL construction mainly instead of the existing 110kV double circuit line route, 110kV line will be renovated at the same time and both will be assembled on the same towers. Upgrade of double circuit 330kV double circuit OHL new 380 330. (Capacity 800MW). | New interconnection lines between Western and Central part of Latvia. New transmission line will increase Security of Supply in Western and Central part of Latvia. Platform for integration of new renewable power generation. | Improved security of supply; RES integration ; Increase of NTC. Mentioned line reinforcement is part of the NordBalt project and planned connection point to Estonian-Latvian third interconnection. | planned | 2016 | X
386 | Baltic Sea | EE (Lihula-Sindi) | LT (Ventspils-Dundaga- TEC2) | Latvian-Estonian third interconnection will consist of OHL Harku-Sindi-Lihula in Estonian part, OHL Imanta-Tume-Dundaga-Ventspils in Latvian part, and sea cable between cross-border DC or AC cable. Final interconnection type and final interconnection and transmission line route will be selected in middle of 2010. At present three alternative route variants researched. Final interconnection length, DC voltage and transmission capacity will be selected in feasibility and technical study in the middle of 2010. The connection would be as a new single circuit line mixed (OHL+subsea cable) up to 500kV. | Need to increase the current transfer capacity between Estonia and Latvia. Need to increase Security of Supply in Latvia, Estonia and all Baltic countries. Platform for integration of new renewable power generation in both countries. | Increase of NTC, improved security of supply and RES integration. Increasing security of supply in Baltic. Capacity congestion and number of hours with market division will be reduced. Risk of shortage of energy will be reduced in the Nordic and Baltic power system. Expected NTC 600-1200MW. | under consideration | 2020 | X
387 | Baltic Sea | Tartu (EE) | Sindi (EE) | A new 162km internal connection will be established on existing route resulting in double circuit line with 2 different voltages (330kV / 110kV). | Depending on market situation the cross-border connection between Latvia and Estonia can be congested. In addition it has positive impact to security of supply in Baltic. | Improved security of supply, RES integration and increase of NTC. New internal connection is for ensuring voltage stability in Western part of Estonia and it is also related to transfer capacity regarding new interconnections between Estonia and Latvia and power exchanges between Nordic and Continental Europe. | design & permitting | 2014
388 | Baltic Sea | Harku (EE) | Sindi (EE) | New single circuit 400 ÷ 220 OHL. (Capacity 1200 MVA, 140-160km). Major part of new internal connection will be established on existing right of way on the Western part of Estonian mainland and the line voltage will be 330kV. | Depending on market situation the cross-border connection between Latvia and Estonia can be congested. In addition it has positive impact to Security of Supply in Baltic. | Increase of NTC ; RES integration ; improved security of supply in Baltic. The new internal connection will ensure transfer capacity between Estonia and Latvia and facilitate power exchanges between Nordic and Continental Europe. | planned | 2018
389 | Baltic Sea | Eesti (EE) | Püssi (EE) | Reinforcement of existing 57km single circuit 330kV OHL. Expected capacity:1200 MVA. | Depending on market situation the cross-border connection between Finland and Estonia can be congested. In addition it has positive impact to security of supply in Baltic. | Increase of NTC, reduction of infrastructure vulnerability and improved security of supply. New internal connection is for ensuring transfer capacity concerning second interconnection between Estonia and Finland. | under construction | 2010
390 | Baltic Sea | Balti (EE) | Püssi (EE) | Reconstruction of 68km single circuit 400-220kV OHL. | Depending on market situation the cross-border connection between Finland and Estonia can be congested. In addition it has positive impact to security of supply in Baltic. | Increase of NTC, reduction of infrastructure vulnerability and improved security of supply. New internal connection is for ensuring transfer capacity concerning second interconnection between Estonia and Finland. | design & permitting | 2011
391 | Baltic Sea | Püssi (EE) | Anttila (FI) | A new HVDC (450kV) connection will be built between Estonia and Finland. On the Finnish side, a 14km DC overhead line will be built to a new substation Anttila where the converter station will be placed. On the Estonian side, a 11km DC cable line will be built to a existing substation Püssi where the converter station will be placed. length of marine cable is 140km. Expected capacity: 650MW. | Depending on market situation the cross-border connection between Finland and Estonia can be congested. In addition it has positive impact to security of supply in Baltic. | Increase of NTC; improved security of supply; RES integration ; 650MW ; Increasing Security of Supply in Baltic. Capacity congestion and number of hours with market division will be reduced. Risk of shortage of energy will be reduced in the Nordic and Baltic power system. | design & permitting | 2013
392 | Baltic Sea | Yllikkälä (FI) | Huutokoski (FI) | New 155km single circuit 400kV OHL and renovation of 400kV substations in Yllikkälä and Huutokoski. Expected capacity: 1850 MVA. | High imports from Russia + high local surplus of power. | Increase of NTC and Improved security of supply. | design & permitting | 2013
393 | Baltic Sea | Seinäjoki Ulvila Ventusneva Keminmaa (FI) | Tuovila Kristinestad Pyhänselkä (FI) | Four new single circuit 400kV OHL are part of project in upgrading Ostrobothnian 220kV system into 400kV, and strengthening the 400 kV grid in Northern Finland. Commissioning of first section in year 2011, second in 2014 third in ca. 2018 and fourth ca 2020. total length of lines: 520 km. Expected capacity: 1850 MVA. | Integration of new generation + replacement of ageing 220kV system + increased transmission capacity demand. | Increase of NTC, RES integration and Improved security of supply. | under construction | 2011/2020
394 | Baltic Sea | Hikiä (FI) | Forssa (FI) | New 80km single circuit 400kV OHL. Expected capacity:1850 MVA. | Changed exchange patterns. | Increase of NTC. | under consideration | 2015
395 | Baltic Sea | Rauma (FI) | Finnböle (SE) | A new 500kV HVDC connection will be built in parallel with the existing one between Finland and Sweden. On the Swedish side, a 70km direct current overhead line will be built to a new substation Finnböle where the converter station will be placed. Total length of line: 300km and capacity: 800MW. | Depending on a hydro situation and market situation the cross-border connection between Finland and Sweden can be congested. In addition there is a large generator under construction in the vicinity of the Finnish side of the border. | Increase of NTC, improved security of supply and annual losses reduction. Congestion and number of hours with market division will be reduced. Redispatching of load flow between 400kV interconnectors at North and Fenno-Skan will reduce power losses. Cost of ancillary services can be decreased. Risk of shortage of energy will be reduced in the Nordic power system. | under construction | 2011
396 | Baltic Sea | Finland Nord (FI) | Sweden North (SE) | Third single circuit 400kV AC OHL between Sweden and Finland. Expected capacity: 1850 MVA. | New wind power generation + larger units + decommissioning of 220kV interconnector. | New wind power generation + larger units + decommissioning of 220kV interconnector. | under consideration | 2018/2020
397 | Baltic Sea North Sea | Varangerbotn (NO) | Pirttikoski or Petäjäskoski (FI) | New single circuit 380 - 400kV OHL (500km). | Enabling RES (wind and small scale hydro power) to connect to the grid (currently limited grid capacity). Enhance the Security of Supply for the Finnmark area, including critical oil and gas installations. | Security of Supply for the Finnmark area. Enabling new demand in critical oil and gas installations. Enabling RES (wind power) in Northern Norway. | under consideration | 2020/2025 |  | The project will be part of a future/potential "Arctic Circle", including reinforcements in Finland, Sweden and Norway.
398 | Baltic Sea North Sea | Under consideration (SE) |  | New series compensation of OHL. | Power flow limited by reactive power issues. | Increased power flow. | under consideration | 2016/2020
399 | Baltic Sea | Vasteras (SE) | Lindbaka (SE) | Upgrade/Replacement of existing single circuit 220kV lines to 400kV. | Increase power flow. | Increase of NTC, improved security of supply and annual losses reduction. | under consideration | 2016/2020
400 | Baltic Sea | Ekhyddan (SE) | Barkeryd (SE) | New single circuit 400kV OHL. | Increased installed nuclear capacity. | Improved security of supply. | under consideration | 2016/2020
401 | Baltic Sea | Västervik (SE) | Gotland (SE) | New AC or DC subsea cable interconnection 400kV (1000 MW). | Integration of new renewable power generation. | RES integration. | under consideration | 2016/2020
402 | Baltic Sea North Sea | Hurva/Hallsberg (SE) | Tveiten (NO) | "South West link" consisting of three main parts: 1) New 400kV line between Hallsberg and Barkeryd 2) New double HVDC VSC underground cable line between Barkeryd and Hurva 3) New HVDC VSC line between Barkeryd and Tveiten/Norway. The project also include new substations and converter stations in the connection points line double circuit new OHL Hallsberg - Barkeryd 170km, underground VSC Barkeryd - Hurva 250km and VSC Barkeryd - Tveiten with 103km on the Norwegian side. Expected capacity: 1200MW. | Market integration. Integration of new renewable power generation. | Increase of NTC, improved security of supply and RES integration. | planned | 2014
403 | Baltic Sea North Sea | Scandinavia North (NO) | Scandinavia South (SE) | A joint Stattnett & Svenska Kraftnat study north - south reinforcement (AC or VSC), expected length: 400 - 500km under study. | Integration of new renewable power generation / limit to renewable export. | RES integration. | under consideration | long term
405 | Baltic Sea North Sea | Kristiansand (NO) | Rød (NO) | Voltage upgrading of an existing single circuit 300kV OHL and a new section of OHL between Rød and Bamle. Total length: 175km. | New interconnection lines between Southern Norway and Europe. Security of supply for the Oslo region. | Increase of NTC and reduction of infrastructure vulnerability. Voltage upgrading required in the AC grid to enable the increase of cross-border capacities in 142, 425, 426. | design & permitting | 2014 |  | Seen as an extension of the new HVDC cables (142, 424, 425, 426).
406 | Baltic Sea North Sea | Kristiansand (NO) | Tonstad - Saurdal (NO) | Voltage upgrading of existing single circuit 300kV OHL Kristiansand-Feda-Tonstad-Lyse-Saurdal Seen as an extension of the new HVDC cables. | New interconnection lines between Southern Norway and Europe. Integration of new renewable power generation. | Increase of NTC, RES integration. Voltage upgrading required in the AC grid to enable the increase cross-border capacities in 142, 425, 426. | design & permitting | 2013/2016 |  | Seen as an extension of the new HVDC cables (142, 424, 425, 426).
407 | Baltic Sea North Sea | Tonstad (NO) | Arendal (NO) | Voltage upgrading of existing single circuit 300kV OHL Tonstad-Solhom-Arendal. | New interconnection lines between Southern Norway and Europe. Integration of new renewable power generation. | Increase of NTC, RES integration. Voltage upgrading required in the AC grid to enable the increase cross-border capacities in 142, 425, 426. | planned | 2016/2018 |  | Seen as an extension of the new HVDC cables (142, 424, 425, 426).
408 | Baltic Sea North Sea | Kristiansand, Feda (NO) |  | Reactive compensation due to HVDC links NorNed and Skagerak 4. Reactive power devices in 400kV substations. | Increased market integration. Reactive compensation due to HVDC links NorNed and Skagerak 4. | Improved security of supply and reduction of infrastructure vulnerability. | planned | 2011/2014 |  | Seen as an extension of the new HVDC cables (142, 424, 425, 426).
409 | Baltic Sea North Sea | Feda, Tonstad (NO) |  | Reactive power devices in 400kV substations. | Increased market integration. Reactive compensation due to HVDC links. | Improved security of supply. | planned | 2017/2018 |  | Seen as an extension of the new HVDC cables (142, 424, 425, 426).
410 | Baltic Sea North Sea | Kristiansand (NO) |  | Spare transformer for the HVDC Skagerak interconnection transformer. | Increased market integration. | Improved security of supply and reduction of infrastructure vulnerability. | under construction | 2010
411 | Baltic Sea North Sea | Rød (NO) | Sylling (NO) | Voltage upgrading of existing single circuit 300kV OHL Rød-Tveiten-Flesaker-Sylling in connection with the new HVDC line to Sweden, the Syd Vest link. | Increased market integration. | Increase of NTC and improved security of supply. | under consideration | 2012/2016
412 | Baltic Sea North Sea | Rød (NO) - Sylling (NO) - Flesaker (NO) - | Hasle (NO) Tegneby (NO) Tegneby (NO) | Reinvestment and capacity increase Oslofjord 400kV subsea cables. Three cables: Filtvedt - Brenntangen, Solberg - Brenntangen, and Teigen - Evje. | Enhance the Security of Supply for the Oslo area, increase cross-border capacity. | Improved security of supply and increase of NTC. | design & permitting | 2011/2013
413 | Baltic Sea North Sea | Ørskog (NO) | Fardal (NO) | New 300km single circuit 400kV OHL. | Critical situation with security of supply in the Mid-Norway area. | Improved security of supply, RES integration and increase of NTC. | design & permitting | 2013/2014
413a | Baltic Sea North Sea | Sima (NO) | Samnanger (NO) | New 420kV line Sima-Samnanger to ensure security of supply in the region of Hordaland/ Bergen, and to integrate new hydro power. | Enhance the Security of Supply for the Hordaland area. Enabling RES small scale hydro power in Western Norway to connect to the grid (currently limited grid capacity). | Improved security of supply; RES integration. | design & permitting | 2013/2014
414 | Baltic Sea North Sea | Fardal (NO) | Aurland (NO) | Voltage upgrading of existing single circuit 300kV OHL Fardal-Aurland Extension of 413 - Ørskog - Fardal. | RES integration. | Improved security of supply, RES integration and increase of NTC. | planned | 2015/2017
415 | Baltic Sea North Sea | Namsos (NO) | Klæbu (NO) | Voltage upgrading of existing single circuit 300kV OHL Namsos-Klæbu. | Enabling RES (wind and small scale hydro power) to connect to the grid (currently limited grid capacity). | RES integration. | planned | 2013
416 | Baltic Sea North Sea | Klæbu (NO) | Aura/ Viklandet (NO) | Voltage upgrading of existing single circuit 300kV OHL Klæbu-Aura. | Enabling RES (wind and small scale hydro power) to connect to the grid (currently limited grid capacity). | RES integration. | planned | 2016
417 | Baltic Sea North Sea | Aura/Viklandet (NO) | Fåberg (NO) | Voltage upgrading of existing single circuit 300kV OHL Aura/Viklandet-Fåberg. | Enabling RES (wind and small scale hydro power) to connect to the grid (currently limited grid capacity). | RES integration. | under consideration | 2016/2020
418 | Baltic Sea North Sea | Nedre Røssåga (NO) | Namsos (NO) | Voltage uprating of existing single circuit 300kV Nedre Røssåga-Tunnsjødal-Namsos OHL to 400kV. | Enabling RES (wind and small scale hydro power) to connect to the grid (currently limited grid capacity). | RES integration. | planned | 2015
419 | Baltic Sea North Sea | Namsos (NO) | Storheia (NO) | New 119km 800MVA single circuit Namsos-Roan-Storheia OHL to connect new wind power generation at Fosen. | Enabling RES (wind and small scale hydro power) to connect to the grid (currently limited grid capacity). | RES integration. | design & permitting | 2013
420 | Baltic Sea North Sea | Storheia (NO) | Orkdal / Trollheim (NO) | New Storheia-Snillfjord-Orkdal/Trollheim single circuit 400kV line to connect new wind power generation in the Snillfjord area; part of the line will be a subsea cable. | Enabling RES (wind and small scale hydro power) to connect to the grid (currently limited grid capacity). | RES integration. | design & permitting | 2015
421 | Baltic Sea North Sea | Ofoten (NO) | Balsfjord (NO) | New 150km single circuit 400kV OHL. | Enabling RES (wind in Northern Norway) to connect to the grid (currently limited grid capacity). Enhance the Security of Supply of the Finnmark area, including critical oil and gas installations. | Improved security of supply; RES integration. | design & permitting | 2014/2015 |  | The project will be part of a future/potential "Arctic Circle", including reinforcements in Finland, Sweden and Norway.
422 | Baltic Sea North Sea | Balsfjord (NO) | Hammerfest (NO) | New 355km single circuit 400kV OHL. | Enabling RES (wind in Northern Norway) to connect to the grid (currently limited grid capacity). Enhance the Security of Supply for the Finnmark area, including critical oil and gas installations. | Improved security of supply; RES integration. | design & permitting | 2016 |  | The project will be part of a future/potential "Arctic Circle", including reinforcements in Finland, Sweden and Norway.
423 | Baltic Sea North Sea | Skaidi (NO) | Varangerbotn (NO) | New single circuit 400kV OHL. | Enabling RES (wind in Northern Norway) to connect to the grid (currently limited grid capacity). Enhance the Security of Supply for the Finnmark area, including critical oil and gas installations. | Improved security of supply; RES integration. | planned | 2020/2025 |  | The project will be part of a future/potential "Arctic Circle", including reinforcements in Finland, Sweden and Norway.
424 | Baltic Sea North Sea | kVilldal (NO) | UK (substation to be determined) | A new 1400MW HVDC bipolar installation connecting Western Norway and the UK via 800km subsea cable; DC voltage is to be determined. | Currently there is no connection between UK and Norway. | 1400MW increase of NTC; RES integration; diversity of supply: connection between a hydro and a thermal power system. | under consideration | 2017/2020
424b | North Sea | Triton Knoll (UK) |  | Establish new 400kV double busbar collector substation. | Provision for additional wind capacity from the North Sea. | RES integration. | under consideration | 2018
424c | North Sea | Triton Knoll (UK) | Bicker Fenn (UK) | New 400kV double circuit. | Limit to renewable export. | Reduce congestion. | under consideration | 2018
424d | North Sea | Near Triton Knoll (UK) |  | Establish new 400kV double busbar collector substation. | Provision for additional wind capacity from the North Sea. | RES integration. | under consideration | 2018
424e | North Sea | Triton Knoll (UK) | Walpole (UK) | New 400kV double circuit. | Limit to renewable export. | Reduce congestion. | under consideration | 2018
424f | North Sea | Triton Knoll (UK) | Grimsby West (UK) | New 400kV double circuit. | Limit to renewable export. | RES integration. | under consultation | 2019
424g | North Sea | Bicker Fenn (UK) | Near Bainton (UK) | New 400kV double circuit. | Limit to renewable export. | RES integration. | under consideration | 2018
424h | North Sea | Near Bainton (UK) |  | Establish new 400kV double busbar substation. | Limit to renewable export. | RES integration. | under consideration | 2018
424i | North Sea | Killinghome South (UK) |  | Establish new 400kV double busbar substation and construct new 400kV double circuit to Grimsby West. | Limit to renewable export. | RES integration. | under consideration | 2020
424j | North Sea | Bramford (UK) | Twinstead(UK) | New 400kV double circuit. | Limit to renewable and nuclear export. | Reduce congestion. | under consideration | 2017
425 | Baltic Sea North Sea | Feda (NO) | to be determined (NL) | NorNed 2: a 2nd HVDC connection between Norway and The Netherlands via 570km 450kV DC subsea cable with 700 - 1400MW capacity. | Need to increase the current transfer capacity between both countries. | 700-1400MW increase of NTC; RES integration; diversity of supply: connection between a hydro and a thermal power system. | under consideration | 2015/2017
426 | Baltic Sea North Sea | Kristiansand (DK) | Tjele (NO) | Skagerak 4: 4th HVDC connection between Southern Norway and Western Denmark, built in parallel with the existing 3 HVDC cables; new 700MW including 230km 500kV DC subsea cable. | Need to increase the current transfer capacity between both countries. | 700 MW increase of NTC ; Diversity of supply: connection between a hydro and a thermal power system. Enabling increased RES integration. | design & permitting | 2014 | X | http://www.energinet.dk/en/menu/Transmission/New+projects/New+electricity+transmission+installations/Skagerrak+4/
427 | Baltic Sea North Sea | Endrup (DK) | Eemshaven (NL) | COBRA: New single circuit HVDC connection between Jutland and the Netherlands via 350km subsea cable; the DC voltage will be up to 450kVand the capacity 600-700MW. | Need to increase the current transfer capacity between both countries. | Increase of NTC ; improved security of supply; RES integration ; 600-700MW ; The purpose of the link is to allow for the exchange and integration of wind energy and increase the value of renewable energy into the Dutch and Danish power systems and to increase security of supply. | design & permitting | 2016 |  | http://www.energinet.dk/en/menu/Transmission/New+projects/New+electricity+transmission+installations/Cobra+cable/
428 | Baltic Sea North Sea | Kassø (DK) | Tjele (DK) | Rebuilding of a 400kV OHL of 173km from a single-circuit to a double-circuit . This increases the transfer capacity with approx 1000 MW. | Need for increased capacity Norway-Jutland-Germany. | 1000MW increase of NTC; RES integration. | design & permitting | 2012/2014 |  | http://www.energinet.dk/en/menu/Transmission/New+projects/New+electricity+transmission+installations/Kassø-Tjele/
429 | Baltic Sea North Sea | Ferslev (DK) | Vester Hassing (DK) | New 20km single circuit 400kV line via a cable with a capacity of approx 800 MW. | Need for improving the ability to transport Læsø off-shore wind power in N-1 security conditions. | RES integration ; improved security of supply. | Planned | 2018 |  | http://www.energinet.dk/en/menu/Transmission/New+projects/New+electricity+transmission+installations/Cable+action+plan/Cable+action+plan.htm
430 | Baltic Sea North Sea | Revsing (DK) | Landerupgård (DK) | New 18km single circuit 400kV line via cable with capacity of approx. 1200 MW. | Need for transporting wind power from the West Coast to the consumption centre on the East Coast. | RES integration; improved security of supply. | Planned | 2017 |  | http://www.energinet.dk/en/menu/Transmission/New+projects/New+electricity+transmission+installations/Cable+action+plan/Cable+action+plan.htm
431 | Baltic Sea North Sea | Tjele (DK) | Trige (DK) | New 46km single circuit 400kV line via cable with capacity of approx. 1200 MW. | Need for transporting wind power from the West Coast to the consumption centre on the East Coast. | RES integration; improved security of supply. | Planned | 2017 |  | http://www.energinet.dk/en/menu/Transmission/New+projects/New+electricity+transmission+installations/Cable+action+plan/Cable+action+plan.htm
432 | Baltic Sea North Sea | Asvæsværket ((DK) | Kyndbyværket (DK) | New 60km single circuit 400kV line via cable with capacity of approx. 1200 MW. | Need for reinforcing and meshing the 400kV grid on Zealand. | Improved security of supply. | Planned | 2014 |  | http://www.energinet.dk/en/menu/Transmission/New+projects/New+electricity+transmission+installations/Cable+action+plan/Cable+action+plan.htm
433 | Baltic Sea North Sea | Glentegård (DK) | Amagerværket & H.C. Ørstedværket (DK) | New 22km single circuit 400kV line via cable with capacity of approx. 1200MW. | Creating a 400kV ring around Copenhagen. | Improved security of supply. | Planned | 2016 |  | http://www.energinet.dk/en/menu/Transmission/New+projects/New+electricity+transmission+installations/Cable+action+plan/Cable+action+plan.htm
434 | Baltic Sea North Sea | Fraugde (DK) | Herslev(DK) | New single circuit HVDC-LCC installation including a 56km 450kV DC subsea cable with 600MW capacity. | Need for interconnection between Eastern and Western Denmark to exchange wind power & regulation power. | Improved security of supply; RES integration. | under construction | 2010 |  | http://www.energinet.dk/en/menu/Transmission/New+projects/New+electricity+transmission+installations/Great+Belt/
435 | Baltic Sea North Sea | Endrup (DK) | Revsing(DK) | Upgrade of 50km double-circuit 400kV OHL to reach a capacity of approx. 2000MW. | Need to connect COBRA line; improve n-1 security; need to increase transport capacity between West coast to East coast. | RES integration; improved security of supply. | Planned | 2017 |  | http://www.energinet.dk/en/menu/Transmission/New+projects/New+electricity+transmission+installations/Cable+action+plan/Cable+action+plan.htm
436 | Baltic Sea North Sea | Idomlund (DK) | Tjele (DK) | New 74km single circuit 400kV line via cable with capacity of approx. 1200MW. | Need for a second 400kV connection to Idomlund for security of supply and to evacuate wind power from Western Jutland. | RES integration; improved security of supply. | under consideration | 2018/2020 |  | http://www.energinet.dk/en/menu/Transmission/New+projects/New+electricity+transmission+installations/Cable+action+plan/Cable+action+plan.htm
437 | North Sea | Grain (UK) | Maasvlakte (NL) | New 1290MW HVDC bipolar installation including 260km of 450kV DC subsea cable. | Currently there is no connection between UK and Netherlands. | Project results in 1000MW NTC between both countries; enhanced diversity and security of supply for both markets open access for all market parties by explicit auction and market coupling increase of interconnection capacity and market transparency. | under construction | 2010 | X | commissioned in 2010 but commercial operation as from 2011
438 | North Sea | Eemshaven (NL) | Diemen (NL) | New 175-200km AC overhead line with capacity of 2x2650 MVA of 380kV. | need for connection from the generation locations in the vicinity of Eemshaven to the Dutch 380kV central ring. | Conventional generation integration; RES integration. | design & permitting | 2016
439 | North Sea | Borssele (NL) | Geertruidenberg (NL) | New 100-130km double-circuit 380kV OHL with 2x2650 MVA capacity. | Need for connection from the generation locations in the vicinity of Borssele to the Dutch 380kV central ring. | Conventional generation integration; RES integration. | design & permitting | 2014
440 | North Sea | Maasvlakte (NL) | Beverwijk (NL) | New 380 kV double-circuit mixed project (OHL+ underground cable) including approximately 20km of underground cable for 2650 MVA. The cable sections are a pilot project. The total length of cable at 380kV is frozen until more experience is gained. | Need for connection from the generation locations in the vicinity of Rotterdam and Amsterdam to the Dutch 380kV central ring. | Conventional generation integration; feed of load increase; RES integration. | under construction | 2013
441 | North Sea | Zwolle (NL) | Hengelo (NL) | Upgrade of the capacity of the existing 60km double circuit 380kV OHL to reach a capacity of 2x2650 MVA. | Need to increase the capacity of the existing line to avoid overloads due to different flow patterns in the grid. | Improved security of supply; conventional generation integration; RES integration. | under consideration | tbd
442 | North Sea | Krimpen aan de Ijssel (NL) | Maasbracht (NL) | Upgrade of the capacity of the existing 150km double circuit 380kV OHL to reach a capacity of 2x2650 MVA. | Need to increase the capacity of the existing line to avoid overloads due to different flow patterns in the grid. | Improved security of supply; conventional generation integration; RES integration. | under consideration | tbd
443 | North Sea | Richborough (UK) | Zeebrugge (BE) | Nemo project: new DC sea link including 135km of 250kV DC subsea cable with 1000MW capacity. | Currently there is no connection between BE and UK. | Increase of NTC by 1000MW. | planned | 2016
444 | North Sea | Zomergem (BE) | Zeebrugge (BE) | New approx 50km double-circuit 380kV 5000MVA OHL line between Zomergem and Zeebrugge to evacuate the locally (offshore) produced power line. | Required to further realise the renewable offshore resources available to Belgium. | RES integration; Increase of NTC. | design & permitting | 2014
445 | North Sea | Zandvliet (BE) | Lillo (BE) | Doubling of the axis Zandvliet-Mercator via Lillo by erecting a new 35km 380kV double circuit OHL with 1500 MVA capacity. | Needed to avoid overloading of the line during certain contingencies as a result of new generation and increasing demand. | Conventional generation integration; improved security of supply; Increase of NTC. | design & permitting | 2014
445a | North Sea | Gramme (BE) | Van Eyck (BE) | Doubling of 380kV the axis Gramme-Van Eyck. | Increase of NTC and connection of new generation units. | Market integration and power plants connection. | planned | 2014
446 | North Sea | Bascharage (LU) | Aubange (BE) | New interconnection between Creos grid in LU and ELIA grid in BE via a 16km double circuit 225kV underground cable with a capacity of 1000 MVA. | Grid studies promote a new interconnection in the south of the grid line for improving security of supply. | Improved security of supply; Increase of NTC; Diversity of supply; new capacity between LU and BE. | design & permitting | 2013
447 | North Sea | Heisdorf (LU) | Berchem (LU) | New 20km double-circuit mixed (underground cable+OHL) 225kV project with 1000 MVA capacity including substations for infeed in lower voltage levels. | Need for increased infeed to lower voltage levels, the project will also close a mesh in the south of the grid. | Improved security of supply; Increase of NTC. | design & permitting | 2012/2020
448 | North Sea | Thames estuary (UK) |  | Double-circuit 400kV line upgrade around the Thames estuary. | Low cross border capacity. | Increase of NTC (investment needed to accommodate additional interconnectors and integrate offshore RES. | under construction | 2011
449 | North Sea | Richborough (UK) | Canterbury (UK) | New double-circuit 400kV OHL and new 400kV substation in Richborough. | Low cross border capacity. | Increase of NTC (investment needed to accommodate additional interconnectors). | planned | 2019
449a | North Sea | Gravir (UK) | Beauly (UK) | Western Isles link. New 450MW HVDC link, +/- 150kV. Route length 156km (80km subsea, 76km onshore underground cable). | Limit to renewable export. | RES integration & reduced reliance on diesel generation. | design & permitting | 2013
450 | North Sea | Sellindge (UK) | Dungeness (UK) | Reconductoring existing double-circuit 400kV OHL. | Low cross border capacity. | Increase of NTC (investment needed to accommodate additional interconnectors). | planned | 2019
450a | North Sea | Kergord and Caithness (UK) | Blackhillock (UK) | The Moray Firth HVDC development - Shetland and Caithness links with offshore HVDC hub. Three ended HVDC link, 2 x 600MW legs and common 1200MW leg. Total route length 395km. | Limit to renewable export. | RES integration. | design & permitting | 2014 |  | EC grant of €74m awarded to SHETL under the European Energy Programme for Recovery. Grant relates to the offshore hub element and rating increase to 1200MW.
451 | North Sea | Rowdown (UK) |  | New 400kV quadboosters. | Low cross border capacity. | Increase of NTC (investment needed to accommodate additional interconnectors). | planned | 2019
451a | North Sea | Dounreay (UK) | Beauly (UK) | String a second 275kV OHL circuit on existing towers. | Limit to renewable export. | RES integration. | design & permitting | 2012
452 | North Sea | Deeside (UK) | Hunterston (UK) | New 2000MW HVDC link via 360km 500kV DC subsea cable on the West coast of the UK and new 400kV substation in Deeside - CSC Technology. | Limit to renewable export. | RES integration. | planned | 2015
452a | North Sea | Beauly (UK) | Kintore (UK) | Reconductor existing 275kV overhead line route. | Limit to renewable export. | RES integration. | design & permitting | 2014
453 | North Sea | Peterhead (UK) | Hawthorn Pit (UK) | New 1800MW HVDC link via 365km 500kV DC subsea cable on the East coast of the UK and new 400kV substation in Hawthorn Pit - CSC Technology. | Limit to renewable export. | RES integration. | planned | 2018
453a | North Sea | Blackhillock (UK) | Kincardine (UK) | Reinsulate existing 275kV route for 400kV operation and establish three new 400kV substations en-route. | Limit to renewable export. | RES integration. | design & permitting | 2015
454 | North Sea | Hawthorn Pit (UK) | Norton (UK) | Upgrade of double circuit OHL from 275 to 400kV. | Limit to renewable export. | RES integration. | planned | 2018
455 | North Sea | Beauly (UK) | Denny (UK) | New double circuit 400kV OHL (220km) with new terminal substations and substation extensions en route. | Limit to renewable export. | RES integration. | under construction | 2014
456 | North Sea | Harker (UK) | Hutton (UK) | Upgrade to double-circuit Harker - Hutton 400kV OHL. | Limit to renewable export. | RES integration. | planned | 2013
456b | North Sea | Harker(UK) | Quernmore(UK) | New 400kV double circuit. | Limit to renewable and nuclear export . | Reduce congestion. | under consideration | 2020
456c | North Sea | Quernmore(UK) | Padiham(UK) | New 400kV double circuit. | Limit to renewable and nuclear export. | Reduce congestion. | under consideration | 2020
457 | North Sea | Harker (UK) | Stella (UK) | New 400kV series compensation at a number of locations across the Anglo-Scottish border. | Limit to renewable export. | RES integration. | planned | 2014
458 | North Sea | Hinkley (UK) | Seabank (UK) | New 60km double-circuit 400kV overhead line for renewables off the South West peninsula, replanting of Hinkley Point nuclear power station and further CCGT at Seabank. | Integration of nuclear plant and limit to renewable export. | RES and conventional integration. | design & permitting | 2016
459 | North Sea | New substation (UK) | Ironbridge (UK) | New 400kV substation and 85km line to connect the TAN-08 wind farms in mid Wales. | Limit to renewable export. | RES integration. | design & permitting | 2016
459b | North Sea | Wlyfa (UK) | Central Wales (UK) | New HVDC (VSC) bipolar interconnection. | Limit to renewable export. | RES integration. | under consideration | >2020
460 | North Sea | Pentir (UK) | Trawsfynydd (UK) | Upgrade of existing 48km single circuit 400kV line to double circuit to accommodate new wind generation off Anglesey and nuclear replanting at Wylfa. | Integration of nuclear plant and limit to renewable export. | RES and conventional integration. | under consideration | 2015
460b | North Sea | Wylfa(UK) | Pentir(UK) | New 400kV double circuit to connect offshore wind. | Limit to renewable export. | RES integration. | under consideration | 2017
461 | North Sea | Woodland (IE) | Deeside (UK) | A new 260km HVDC (380kV DC) underground and subsea connection between Ireland and Britain with 500MW capacity. On the Irish side, a 45km direct current underground cable will be built to the Woodland substation where the VSC converter station will be placed. The link will consist of two identical circuits. | Future generation import and export to and from Ireland respectively. | RES integration; improved security of supply; diversity of supply. The project will enhance market opportunities and benefit competition. | under construction | 2011 | X
462 | North Sea | Moyhill (IE) | Turleenan (UK) | A new 80km single circuit 400kV 1500MVA OHL from a new Moyhill 400/220kV substation in Ireland to a new Turleenan 400/275kV substation in Northern Ireland. This project is an integral part of the new interconnection project Moyhill- Wooodland between Ireland and Northern Ireland. | Low cross border capacity. | Increase of NTC up to 1000MW NTC from IE to NI (today <450MW); improved security of supply; improved access for renewable generation. | design & permitting | 2012 | X
463 | North Sea | IE (substation to be determined) | UK (substation to be determined) | Strengthening of EHV networks (partial uprate and new) into Donegal and West of Northern Ireland and enhanced links between the two systems. | This project needs to be completed to facilitate the development of renewable energy in the North-West and Border Regions. | RES integration; improved security of supply; Annual losses reduction. | under consideration | >2015
464 | North Sea | Moyhill (IE) | Woodland (IE) | A new 60km single circuit 400kV 1500MVA OHL from Woodland station north of Dublin up to a new Moyhill 400/220kV station in Co. Meath. This project together with Moyhill-Turlenaan constitute the new interconnection project between Ireland and Northern Ireland. | Low cross border capacity. | Increase of NTC up to 1000 MW NTC from IE to NI (today <450MW); improved security of supply; improve access for renewable generation. | design & permitting | 2012 | X
465 | North Sea | Loughteeog (IE) |  | A new 500 MVA 400/110kV substation connected into the Moneypoint-Dunstown 400kV line and the Athy-Portlaoise 110kV line, and with two 400/110kV 250 MVA transformers. This project also comprises a new 110kV line from Loughteeog to Ballyragget 38kV station and upgrading of Ballyragget station and the Ballyragget-Kilkenny 38kV line from 38kV to 110kV substation. | Demand growth at Kilkenny city and surrounding region. | Improved security of supply for counties Kilkenny, Carlow and Laois; reduce losses. | design & permitting | 2014
466 | North Sea | Flagford (IE) | Srananagh (IE) | The construction of a new 55km single circuit 220kV line connecting the existing Flagford 220/100kV station to a new Srananagh 220/110kV station. | This development is needed to reinforce the network in the North-West area by supporting the voltage and reducing the risk of loss of supply during the winter peaks and the summer maintenance outages. This project will help alleviate constraints on the network in the South-West Region. | Improved security of supply; RES integration; reduce Losses. | under construction | 2011 |  | The 110kV works associated with this project have been completed
467 | North Sea | Moneypoint (IE) | Tarbert or Kilpaddoge (IE) | A new 10km single circuit 220kV 500MVA (underground+subsea) cable constructed across the River Shannon Estuary from Moneypoint in Co. Clare to Tarbert or a new Kilpaddoge station in Co. Kerry. A new 400/220kV transformer at Moneypoint station is included in this project. | This project will provide an alternative route to import to or export power from the south West. | Improved security of supply; RES integration; Reduce Losses. | planned | 2012
468 | North Sea | South-West Substation tbd (IE) | Mid-West Substation tbd (IE) | Increased capacity between the South-West and the Mid-West regions. | This new circuit is required to facilitate the evacuation of generation from the South-West region. This project will help alleviate constraints on the network in the South-West Region. | RES integration; improved security of supply; Reduce Losses. | under consideration | tbd
469 | North Sea | South-West Substation tbd (IE) | Mid-East Substation tbd (IE) | Increased capacity between the South-West and the Mid-East regions. | This new development is required to facilitate the evacuation of generation from the south-West region. This project will help alleviate constraints on the network in the South-West Region. | RES integration; improved security of supply; Reduce Losses. | under consideration | tbd
470 | North Sea | Mayo Substation tbd (IE) | Mid-East Substation tbd (IE) | The construction of new EHV transmission circuit(s) from north West Mayo to the EHV system. | This circuit(s) will facilitate the evacuation of generation from the North-West Region towards the main load centre in the East. | RES integration; improved security of supply; Reduce Losses. | under consideration | tbd
471 | North Sea | Dunstown (IE) | Woodland (IE) | Uprate of the 62-km single circuit 400-kV line between the Dunstown and Woodland stations for increasing the capacity | Following the construction of this circuit, large quantities of generation can be transferred through the Mid-East Region without having to pass through the Dublin city system. | Improve security of supply; Conventional generation integration; RES integration; | under consideration | tbd